## Sheet1
ID | File tag | Provider | Date 1 | Time 2 | Latitude 3 | Longitude 3 | Address of incident 4 | ID of nearest asset 5 | ID of nearest polyphase line 6 | Voltage of line in which fire start occurred 7 | Network categorisation 8 | Type of primary asset involved in fire start 9 | Phase(s) of line or transformer 10 | Kind of fire start as per Clause 5 of F-factor Order-In-Council 11 | Location area 12 | Location multiplier | Fire danger rating 13 | Danger multiplier | Product of multipliers | DNSP record number 14 | OSIRIS (ESV) reference number 15 | Fault description 16 | Overhead conductors
1 | United 19/20 | United | 2019-07-01 | 0.48681 | -38.2188 | 145.1724 | 1003 FRANKSTON-FLINDERS ROAD, SOMERVILLE VIC 3912 | 8822258 | HGS22 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1308097 | 20190705UTD_01 | Council Tree branch (undeclared area so UE) brought down HV in Ftn Flinders Rd on tee cond & caused sparking which caused approx 1m sq grass fire on O/H between LIS# PO-8822258. Fire report # 6565 | - overhead conductor (bare; aluminium core steel reinforced)
2 | United 19/21 | United | 2019-07-11 | 0.39793 | -38.0089 | 145.2068 | 221-231 HAMMOND ROAD, DANDENONG SOUTH VIC 3175 | 8830311 | DSH23 | 22kV AC | Urban | - capacity balancing units | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1311704 | 20190813UTD_01 | CAP HAMMOND N221 RHUR reported as arcing / sparking/fire coming from vacuum switch (es). | - overhead conductor (bare; all aluminium conductor)
3 | United 19/22 | United | 2019-07-17 | 0.26896 | -37.8511 | 145.1233 | 326-328 BURWOOD HIGHWAY, BURWOOD VIC 3125 | 7002221 | EB11 | Low voltage AC (<1kV) | Urban | - services pit | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1313896 | 20190725UTD_01 | Pit is at tram pole # 88. On sth side of Tram track 50 mtrs east of Renow st Burwood. Fire in the pit and wires are fire damaged. Fire start but no damage to anything other than our wiring in the pit. Closest LIS 7002221 | - overhead conductor (bare; steel)
4 | United 19/23 | United | 2019-07-29 | 0.81667 | -38.314 | 145.1388 | 96 COOLART ROAD, TUERONG VIC 3915 | 1110660 | HGS22 | 22kV AC | Rural Short | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1318437 | 20190808UTD_02 | ABICARE N90 COOLART single phase S/Stn: Crew replaced 5 amp EDO on south side phase. Cause: HV fuse was candling and finally failed. Note: S/Stn pole has animal proofing installed. | - overhead conductor (ABC)
5 | United 19/24 | United | 2019-08-07 | 0.30513 | -37.908 | 145.098 | 102 HAUGHTON ROAD, OAKLEIGH VIC 3166 | 8804026 | OE04 | Low voltage AC (<1kV) | Urban | - lamps (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1321009 | 20191004UTD_01 | isolated SL pole. SL head burnt out, head req replacement. LIS# 8804026. | - overhead conductor (covered uninsulated)
6 | United 19/25 | United | 2019-08-08 | 0.092361 | -38.2749 | 145.1597 | LOT 16 GERARDS WAY, TYABB VIC 3913 | 1112692 | HGS22 | 22kV AC | Rural Short | - transformer (pole mounted) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1321638 | 20190821UTD_02 | 5kVA single phase Tx requires replacement ASAP on 8/8/19, Birds nest on Bushings has caught fire, at some stage and burnt bushings/2 x LV bushings cracked and broken. Fire report 6828. HV/LV isolated and burnt birds next removed. | - overhead conductor (insulated)
7 | United 19/26 | United | 2019-08-09 | 0.37222 | -38.3692 | 144.7773 | 22 HARLEIAN STREET, BLAIRGOWRIE VIC 3942 | 1304484 | STO14 | 22kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1322158 | 20190821UTD_03 | Pole fire at HV inter LV strain normal open point pole down lis 1304484. possible HVI HV fuse at RB0578 Open. | Service lines
8 | United 19/27 | United | 2019-08-09 | 0.47448 | -38.2149 | 145.1164 | 280 ERAMOSA ROAD W, MOOROODUC VIC 3933 | 1103528 | MTN22 | 22kV AC | Rural Short | - overhead conductor (ABC) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1322299 | 20190903UTD_01 | Severe storm high winds at time of outage . Large tree thru HV ABC 257 Eramosa Rd. cHV ABC & LV ABC damaged between MT7286 ERAMOSA RD & MT7287 ERAMOSA RD.(5 Bays) and a small fire start on ground | - overhead service conductor (residential)
9 | United 19/28 | United | 2019-08-25 | 0.99295 | -38.1402 | 145.1271 | 15 FLETCHER ROAD, FRANKSTON VIC 3199 | 8819028 | FTN11 | Low voltage AC (<1kV) | Urban | - lamps (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1327197 | 20190828UTD_03 | isolated at base of pole, new 250w HPS required, traffic control required to replace, refer #1327197 | - overhead service conductor (commercial / industrial)
10 | United 19/29 | United | 2019-09-10 | 0.23271 | -37.8801 | 145.1406 | 289 LAWRENCE ROAD, MOUNT WAVERLEY VIC 3149 | 602198 | EB12 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1331551 | 20190923UTD_01 | Part of EB12 feeder fault to#1331552, crossarm fire due to insulator failure | - overhead service conductor (subdivision / construction)
11 | United 19/30 | United | 2019-09-21 | 0.21806 | -37.7579 | 145.1131 | 420 THOMPSONS ROAD, TEMPLESTOWE LOWER VIC 3107 | 7068425 | BU14 | 11kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1335344 | 20191001UTD_01 | During strong winds a council tree branch and fell into HV conductors which caused a HV injection. The resulting surge cause a flashover at kiosk S/Stn THOMSON-FOOTE which ignited a small grass fire. Closest LIS = 7068425 | - overhead service conductor (other)
12 | United 19/31 | United | 2019-10-06 | 0.89237 | -38.0427 | 145.1114 | 255 STATION STREET, EDITHVALE VIC 3196 | 3303709 | CRM35 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1340098 | 20191106UTD_01 | Broken Hv Xarm LIS#3303709 Short interruption to replace | - underground service cable (residential)
13 | United 19/32 | United | 2019-10-28 | 0.66245 | -37.8847 | 145.2067 | QUARRY, 191 GEORGE STREET, WANTIRNA SOUTH VIC 3152 | 619559 | GW7 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 1346112 | 20191106UTD_02 | Originally recorded as abird/Animal it was subsequently determined after investigation a vehicle has contacted the conductors and laft a scorch mark on the ground <1m | - underground service cable (commercial / industrial)
14 | United 19/33 | United | 2019-10-30 | 0.60738 | -37.9762 | 145.0215 | 533 BALCOMBE ROAD, BLACK ROCK VIC 3193 | 1820222 | BR4 | 11kV AC | Urban | - underground cable | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1346876 | 20191127UTD_04 | Refer also to T/E#1346872. CrCrew also reports hole blown in HV UGC at CHP #1812587 c/t BALCOMBE EBDEN S/S, this was likely the primary fault. Faulty HV cable disconnected, isolated and earthed and A/P issued to UGC crew from ZNX. Customers ex BALC | - underground service cable (subdivision / construction)
15 | United 19/34 | United | 2019-11-04 | 0.96045 | -37.8467 | 145.1042 | 45 PARER STREET, BURWOOD VIC 3125 | 7048034 | BW22 | 11kV AC | Urban | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1348043 | 20191203UTD_02 | Gas switch bh7267 needs replacement. the leads and bushing are b/out. LIS # 7048034 Crew have isolated supply and issued permits and crew are replacing gas switch. Refer TE 1348055 A smaill amount of debris caused a 100X 100mm ground fire | - underground cable
16 | United 19/35 | United | 2019-11-18 | 0.0041667 | -37.9275 | 145.0677 | 3 GREENDALE ROAD, BENTLEIGH EAST VIC 3165 | 1801649 | CDA24 | Low voltage AC (<1kV) | Urban | - connection box | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1351867 | 20191203UTD_03 | MFB reported Pole Fire but was out when crew arrived replaced burntout J/Box on pole. | - underground communications cable
17 | United 19/36 | United | 2019-11-21 | 0.64097 | -37.9202 | 145.0854 | 18 DELIA STREET, OAKLEIGH SOUTH VIC 3167 | 2328854 | OR33 | Low voltage AC (<1kV) | Urban | - pole (wood) | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1353529 | 20200110UTD_01 | PART OF south circuit isolated, pole to be repalced as struck by lightning . Fire Report # 02526. lv t-off pole replaced. LIS#2328854. PM not#1000735445 | Poles
18 | United 19/37 | United | 2019-11-21 | 0.70375 | -38.4128 | 145.014 | 389 TUCKS ROAD, SHOREHAM VIC 3916 | 1313635 | DMA23 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | Very High | 1 | 1 | 1353670 | 20191122UTD_01 | DMA23 tripped and reclosed DMA #2 22kV BUEL stage 2 operated. Fault traced to tree over HV at lis 1313635 Tucks Rd. Small fire started ESV advised ref#12847040 TUCKS LYNCROFT is isolated LV. | - pole (concrete)
19 | United 19/38 | United | 2019-11-26 | 0.22608 | -37.8079 | 145.1211 | 140 NELSON ROAD, BOX HILL NORTH VIC 3129 | 7035489 | DC12 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1355201 | 20191204UTD_02 | South cct of SAXTON-SHANNON S/S 22Kv X-Arm broken at Isolator pole BH0405, HV conductors down in Nelson St North of Tyne St. LIS#7035489. | - pole (steel)
20 | United 19/39 | United | 2019-11-26 | 0.25764 | -37.9176 | 145.1493 | 226-236 WELLINGTON ROAD, CLAYTON VIC 3168 | 622882 | SVTS-EB | 66kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1355208 | 20191203UTD_04 | 66KV termination xarm burnt through at insulator. lis #0622882, P/M #1000725805 | - pole (wood)
21 | United 19/40 | United | 2019-11-26 | 0.35694 | -37.9286 | 144.9995 | 99 SOUTH ROAD, BRIGHTON VIC 3186 | 1805014 | MR13 | 11kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1355246 | 20200110UTD_02 | No fire when crews arrived, fire report done #4455 - HV strain arm and 3x 11kv HV isolator req replacing PM#1000735918 - lis 1805014 CH0769 switch pole - works completed | Crossarms
22 | United 19/41 | United | 2019-11-26 | 0.45314 | -38.3239 | 144.7322 | 3572-3574 POINT NEPEAN ROAD, PORTSEA VIC 3944 | 1302728 | STO22 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1355337 | 20191204UTD_01 | CFA reported tree branch on fire but was out when crew arrived. Crew found tree branch resting on HV conductors. Private tree from 3568 Point Nep Rd. | - crossarm (wood)
23 | United 19/42 | United | 2019-11-27 | 0.18874 | -37.9103 | 144.9863 | 218B ESPLANADE, BRIGHTON VIC 3186 | 1806095 | NB33 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1355658 | 20200114UTD_01 | FiRef #1357042 replcd red phase fuse base & 100a service fuse at the pole lis# 1806095 fire report: 1569 caused very small fire at base of pole supply left on - email sent from analytics @ 02:00 on 1/12/19 | - crossarm (steel)
24 | United 19/43 | United | 2019-11-30 | 0.50278 | -38 | 145.1072 | 19 MALCOLM ROAD, BRAESIDE VIC 3195 | 616892 | MC4 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1356774 | 20191210UTD_02 | End of x/arm had burnt through at MALCOLM N13 BOUNDARY S/stn LIS#0616892, HV conductor resting in tree small fire in canopy. installed on same x/arm. X/Arm to be replaced at a later date. Notification 1000736622 - Fire Report number 03074. | - crossarm (other)
25 | United 19/44 | United | 2019-12-04 | 0.33315 | -38.2758 | 145.0134 | 46 GLENISLA DRIVE, MOUNT MARTHA VIC 3934 | 1103211 | DMA24 | 22kV AC | Rural Short | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1358310 | 20191213UTD_01 | Found White Phase HV EDO with black marks on tube. Suspect fuse hung up and possibly candled. Fire report No 7023 completed. No cause found. LBRA area - no fire present - LIS 1103211 | - capacity balancing units
26 | United 19/45 | United | 2019-12-08 | 0.4702 | -38.0164 | 145.1188 | 54 SUTHERLAND AVENUE, ASPENDALE GARDENS VIC 3195 | 3305055 | KBH-M-MC | 66kV AC | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1359403 | 20191213UTD_04 | KBH to M to MC 66kV line, AL to CU amapac failure. as Lis# 3305055 is on bike track at rear of # 54 - confirmed fire start, 2m2 grass fire 66kv sub t pole - steel xarm, concrete pole - large tower required to change ampacs - fire report #04454 | - connector / termination
27 | United 19/46 | United | 2019-12-09 | 0.85226 | -37.8884 | 144.9958 | BENT AVE BRIGHTON 3186 [Cnr New St] | 2308461 | EW14 | 11kV AC | Urban | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1359943 | 20191213UTD_02 | Cause: Large pine tree in Elsternwick golf course dropped branch onto HV CHP LIS# 2308461 in Bent Ave, Tree branch was sparking / burning at time of fault. No fire at ground level. Crew will submit fire report #1099... | - dropper / bridge
28 | United 19/47 | United | 2019-12-10 | 0.28681 | -37.9301 | 145.1018 | 18 THE PARADE, CLARINDA VIC 3169 | 2333349 | CDA-SVTS | 66kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1359994 | 20200211UTD_01 | End of Xarm burnt off... post type 11 shed grey porcelain.... No fire on arrival...Switched out line to replace Xarm.Pole # 2333349 - Wayne Highmore in attendance - O/S 18 The Parade Clarinda | - insulator tie wires / connections
29 | United 19/48 | United | 2019-12-10 | 0.28889 | -37.8978 | 145.1234 | 5 BELLERIVE AVENUE, MOUNT WAVERLEY VIC 3149 | 2300779 | NO7 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1359995 | 20200128UTD_01 | Broken xarm HV inter needs replacement 1 nth Bellvue. Const adv. LIS # 2300779 Hv x-arm broke, Swung into LV. | - insulators
30 | United 19/49 | United | 2019-12-10 | 0.31209 | -37.954 | 145.0765 | 371-373 WARRIGAL ROAD, CHELTENHAM VIC 3192 | 1825384 | HT11 | 22kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1360013 | 20191218UTD_01 | HV Pole burnt fire report 5243 .Pole # 1825384 -o/s 371 Warrigal Rd | - tower
31 | United 19/50 | United | 2019-12-10 | 0.50347 | -37.9563 | 145.0077 | 153-155 BEACH ROAD, SANDRINGHAM VIC 3191 | 1817434 | SR11 | 11kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1360185 | 20191217UTD_02 | construction crew required, crew returning to depot get, new HV anchor arm. X-arm is boken and conductor hanging low but not dangerous. | - traction lines
32 | United 19/51 | United | 2019-12-14 | 0.42755 | -37.9255 | 145.1562 | 821 SPRINGVALE ROAD, MULGRAVE VIC 3170 | 619973 | SVW53 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1361411 | 20200114UTD_03 | HV x-arm fire & snapped PM#1000738403, DN1225 LIS#0619973.. Wood pole & arm, Brown pin type insulators. Small flame visible adjacent to kingbolt in xarm.. Xarm replaced.. fire report no. 02527. photos attached to file as per crew. | - services pit
33 | United 19/52 | United | 2019-12-17 | 0.54792 | -38.1589 | 145.1541 | 42 LIPTON DRIVE, FRANKSTON VIC 3199 | 8819961 | FSH22 | Low voltage AC (<1kV) | Urban | - underground service cable (residential) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1362369 | 20200114UTD_02 | Pillar o/s 42 Lipton is blown up and requires repair. parralelling pillar on the n/strip. supply. Fire report number is 03823. Small fire in the garden bed approx 1 meter x 1 meter . Closest LIS 8819961 | - transformer (pole mounted)
34 | United 19/53 | United | 2019-12-20 | 0.72083 | -38.1595 | 145.1091 | 38 BRUARONG CRESCENT, FRANKSTON SOUTH VIC 3199 | 3315975 | FSH13 | Low voltage AC (<1kV) | Urban | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 1363600 | 20200117UTD_01 | replaced white phase LV krone box isolator and blade which was arcing and sparking , this caused a grass fire @ pole lis # 3315975 approx 1m x 1m - fire report # 08002notification # 1000739449 Reported to ESV - (Cody) @ 20:10 hrs 20/1/219 ESV Ref # 13036024 . | - transformer (ground outdoor mounted)
35 | United 19/54 | United | 2019-12-20 | 0.73889 | -38.1864 | 145.0901 | 129 MOUNT ELIZA WAY, MOUNT ELIZA VIC 3930 | 3313700 | FSH12 | Low voltage AC (<1kV) | Rural Short | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 1363609 | 20200218UTD_01 | Replaced red phase burnt out IPC Connection @ the transformer -There is a report in regards to a object falling onto a car o/s 129 MT Eliza Way Mt Eliza there is no car on arrival but sebesequent claim confirmed a fire start | - measurement transformer (current transformer)
36 | United 19/55 | United | 2019-12-21 | 0.49306 | -38.3875 | 144.7894 | 11 DOROTHY STREET, RYE VIC 3941 | 1305665 | STO21 | Low voltage AC (<1kV) | Rural Short | - connector / termination | single phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 1364062 | 20200114UTD_04 | Blue ph ampact connection to OH line at sub pole melted (LIS#1305665 - o/s 11 Dorothy St, Rye). Small fire evident at base of pole. approx 0.5m2. fire report 6829. fire started from molten metal dropping to ground. supply restored 1330. | - transformer (indoor chamber mounted)
37 | United 19/56 | United | 2019-12-21 | 0.99976 | -38.1373 | 145.1239 | 377 NEPEAN HIGHWAY, FRANKSTON VIC 3199 | 3308817 | FTN22 | Low voltage AC (<1kV) | Urban | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1364161 | 20200114UTD_05 | TX LV Krone Box has melted (red phase contact failed, however it shorted to white phase.). Outage to substation to replace krone box. Fire Report #6830 - smal fire started nature strip area 1/2 metre square, crew have sent photos to dispatch. LIS 3308817 | - transformer (any other type)
38 | United 19/57 | United | 2019-12-24 | 0.42287 | -37.9588 | 145.1226 | 550-570 HEATHERTON ROAD, CLAYTON SOUTH VIC 3169 | 610198 | SS21 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1364424 | 20200114UTD_06 | Replaced x-arm burnt at one end Heatherton Rd. Lis 0610198. Fire report No 1100. No fire on ground. | - measurement transformer (voltage transformer)
39 | United 19/58 | United | 2019-12-27 | 0.78207 | -38.3951 | 144.8178 | 347 BROWNS ROAD, RYE VIC 3941 | 1315973 | STO21 | 22kV AC | Rural Short | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 1364824 | 20200114UTD_07 | Pole lis 1315973 is ok.. no damage, just blackening from fire..Fire report 7041, unable to determine if fire was caused by our asset but as reclose and feeder and call to CFA was 4 minutes apart it appears likely cause is a bird | - measurement transformer (capacitive voltage transformer)
40 | United 19/59 | United | 2019-12-30 | 0.53189 | -37.8219 | 145.1113 | 427 MONT ALBERT ROAD, BOX HILL VIC 3128 | 7023862 | BH23 | 22kV AC | Urban | - connector / termination | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Extreme | 3.5 | 0.7 | 1365109 | 20200211UTD_04 | Also Refer to TE# 1365107. ACR BH7390 was initial tripping device. Tree on O/H tee to BLACK MONT ALBERT and also white phase ampac failed to the east of this location LIS#7023862. Small ground fire indicated by Linesman | Fuses and switchgear
41 | United 19/60 | United | 2019-12-30 | 0.60684 | -37.8243 | 145.1228 | 500 STATION STREET, BOX HILL VIC 3128 | 7027380 | BH23 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Extreme | 3.5 | 0.7 | 1365273 | 20200114UTD_09 | P/M #1000739715 to replace x/arm and insulator. Feeder BH23 lis 7027380. Fire on x.arm only, fire report #9401. replaced burnt out hv angle type 1 intermediate cross arm | - fuse (boric acid)
42 | United 19/61 | United | 2019-12-30 | 0.77569 | -37.7927 | 145.1862 | 60-62 MCGOWANS ROAD, DONVALE VIC 3111 | 7067313 | NW13 | Low voltage AC (<1kV) | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Extreme | 3.5 | 0.7 | 1365271 | 20200114UTD_08 | possibly cause of reclose on TBL#1365241, large council tree thru lv, started grassfire aprox 4 mtrs x 2 mtrs. caused by lv hitting ground. Fire report to come from Rod Parker hv fuse needs to be replaced | - fuse (EDO fuse)
43 | United 19/62 | United | 2019-12-31 | 0.20182 | -37.7636 | 145.1193 | 317 HIGH STREET, TEMPLESTOWE LOWER VIC 3107 | 7058574 | BU1 | 11kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1365627 | 20200211UTD_03 | Confirmed fire start cause of broken HV inter x arm at lis 7058574. Notification 1000739729. ESV Ref 13086092 Intermediate x arm in High St at Tee to Linton LIS#7058574. end of X arm burnt off. Iss and can A/P , X arm replaced | - fuse (powder filled)
44 | United 19/63 | United | 2019-12-31 | 0.22965 | -37.8406 | 145.1114 | 2 NEVILLE STREET, BOX HILL SOUTH VIC 3128 | 7029573 | BH31 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1365634 | 20200114UTD_10 | Broken x-arm reported by MFB, Road side Rph HV resting in Rph LV. Possible HVI - Fire Ignition report #8081 filled out by D Glen, Confirmed HVI HVI#BWD1915, Polynumeric insulator tracked and burnt x-arm. PM Notification 1000739728. ESV ref 13086073. | - circuit breaker
45 | United 19/64 | United | 2019-12-31 | 0.35278 | -37.9094 | 145.0199 | 111 UNION STREET, BRIGHTON EAST VIC 3187 | 2333173 | BT-NB | 66kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1365679 | 20200211UTD_02 | Confirmed fire star NB-BT 66kv line. ESV Ref 13086105 Poss broken x arm per mfb TE#1365697. N No apparent cause between 11kv and 66 KV Iss and can A/P . LIS = 2333173 | - switch (disconnector/isolator)
46 | United 19/65 | United | 2020-01-01 | 0.47652 | -38.3374 | 144.9705 | 79 PIER STREET, DROMANA VIC 3936 | 1311099 | DMA21 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1365879 | 20200122UTD_01 | At lis 1317021.cut away la's at 2 x tx pier nepean, gibson beach and council pier. insert lv parralels for council pier as bearer burnt as a result of helium ballons into 22+66 fire report 7042 started a 1ms ground fire | - switch (earth)
47 | United 19/66 | United | 2020-01-03 | 0.67406 | -37.9193 | 145.0216 | 759 NEPEAN HIGHWAY, BRIGHTON EAST VIC 3187 | 1805698 | MR31 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1366293 | 20200122UTD_02 | LIS= 1805698, HV Inter arm. ESV ref 13107094. Crew replaced xarm LL method. Fire ignition report #: 01543. | - switch (FuseSaver)
48 | United 19/67 | United | 2020-01-05 | 0.3647 | -37.8522 | 145.1329 | 10 BURWOOD HIGHWAY, BURWOOD VIC 3125 | 7037580 | EB11 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1366531 | 20200122UTD_04 | X-arm broken at switch pole BH7256 Burwood Rd LIS#7037580. HV has hit the neutral wire, LV OK. No HV injection, Chemist shop OK and power on, all other shops are closed. ASR AT 13:24HRS - ESV 13116347 | SCADA, network control and protection systems
49 | United 19/68 | United | 2020-01-05 | 0.39792 | -37.868 | 145.0282 | 33 ARTHUR STREET, CAULFIELD NORTH VIC 3161 | 9490012 | MTS-EL-EM | 66kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1366542 | 20200122UTD_05 | MTS-EL/EM 66Kv line X-Arm broken in Arthur St 1pole West of Carnavan Rd LIS#9490012. Fire report # 8082 - ESV 13116340 | - automatic circuit recloser (ACR)
50 | United 19/69 | United | 2020-01-05 | 0.42866 | -38.3301 | 144.7136 | 26 ELIZABETH ROAD, PORTSEA VIC 3944 | 1307150 | STO13 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1366547 | 20200122UTD_06 | ELIZABETH AVE, LIS:1307150 HV LV Inter, 9 Shed insulators. Xarm requires replacement broken at strap bolt. fire report #7043 -ESV #13140653 | - communications linear assets
51 | United 19/70 | United | 2020-01-05 | 0.46163 | -38.1203 | 145.1485 | 4 WINDOO STREET, FRANKSTON NORTH VIC 3200 | 3316011 | FTN13 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1366559 | 20200122UTD_07 | Xarm fire in Windoo, Lis# 93316011, Grey fogs... SNumber 7 Windoo Frankston North hv interxarm to be replaced. ire report# 04457 - ESV 13116335 | - communications network assets
52 | United 19/71 | United | 2020-01-05 | 0.46847 | -38.01 | 145.2128 | 22 STEPHEN ROAD, KEYSBOROUGH VIC 3173 | 635167 | DSH23 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1366564 | 20200122UTD_08 | peFire report 01544 - ESV 13116331 - Xarm fire at switch pole DN0295 CORRIGAN RD, xarm fell onto switch breaking switch insulator. Xarm and switch replaced, supply restored. lis = 0635167 | - communications site infrastructure
53 | United 19/72 | United | 2020-01-05 | 0.48936 | -37.9883 | 145.1005 | 29 DE HAVILLAND ROAD, MORDIALLOC VIC 3195 | 1806826 | MC9 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1366571 | 20200122UTD_09 | Xarm burnt off at G/T S/S, Glass discs & Grey fog dressing down... LIS#1806826... fire report# 04456... hv termination xarm on the sub pole being replaced... - ESV 13116343 | - field devices
54 | United 19/73 | United | 2020-01-05 | 0.62013 | -37.939 | 145.0665 | 16 NELLBERN ROAD, MOORABBIN VIC 3189 | 1816585 | HT8 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1366606 | 20200122UTD_10 | X/Arm / Pole burnt in Nellbern, LIS#1816585...Grey Fogs.. - ESV 13116345 - Fire report 01545 | - local network wiring assets
55 | United 19/74 | United | 2020-01-05 | 0.65214 | -37.8097 | 145.1453 | 32 SPRINGFIELD ROAD, BLACKBURN VIC 3130 | 639430 | BH12 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1366612 | 20200203UTD_01 | Customer rang to say pole 0639430 had a burning piece of wood on the ground. Looks like part of cross arm. Was still smoldering. Wires still up.Tee-off cross-arm in Springfield Rd corner of Beverley, broken LIS#0639430 Fire report 3030 | - master station assets
56 | United 19/75 | United | 2020-01-09 | 0.18384 | -37.9473 | 145.0744 | 5 POWLETT STREET, MOORABBIN VIC 3189 | 1816317 | HT13 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1367602 | 20200203UTD_02 | Patrol found burnt off X arm at Powlett-Simpson S/S. Switched out for Emg A/P to make repairs Fire report ESV#13142340 lis=1816317 | - neutral earthing resistor
57 | United 19/76 | United | 2020-01-10 | 0.6728 | -38.1196 | 145.1541 | 18 LINDSAY STREET, FRANKSTON NORTH VIC 3200 | 3309505 | FTN13 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1368166 | 20200204UTD_01 | Per MFB Lis# 3309505. Broken HV inter x-arm, LINDSAY cnr MORETON. LIS 3309505. Dropped onto HV t-off x-arm. (x-arm burnt through). O/S 18 LINDSAY ST FRANKSTON NORTH Po ESV advised (ref #13151279) - pole fire. \ | - oil-filled circuit recloser (OCR)
58 | United 19/77 | United | 2020-01-10 | 0.69042 | -37.9276 | 145.1491 | 2215-2221 DANDENONG ROAD, MULGRAVE VIC 3170 | 620496 | SVW53 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1368194 | 20200304UTD_03 | X-arm fire at Tx at LAWFORDS KALIMNA. Fire report # Fi's at DN2903 KALIMNA STREET did not operate - (Notification 1000740495 for FI's) - crew replaced (hv term arm @ lis: 0636681 - Notification 1000740496) ESV advised ref#13151298 | - rapid earth fault current limiter (REFCL)
59 | United 19/78 | United | 2020-01-11 | 0.775 | -37.7786 | 145.112 | 6 ROSINE COURT, DONCASTER VIC 3108 | 7069742 | WD34 | Low voltage AC (<1kV) | Urban | - overhead service conductor (residential) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1368574 | 20200402UTD_01 | A LV service wore through on a xarm strap and caused fire damage to the top aof a pole that needed replacement, Fire report #9606, no fire on ground only on pole. LIS 7069742 | Public lighting
60 | United 19/79 | United | 2020-01-11 | 0.80017 | -37.881 | 144.9856 | 2 SHELLEY STREET, ELWOOD VIC 3184 | 2306140 | EW12 | 11kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1368580 | 20200304UTD_01 | broken hv anchor x-arm being replaced today . x arm failed due to fire damage. suspect from yesterday. damage looked old. lis 2306140. fire report2528 | - lamps (major road)
61 | United 19/80 | United | 2020-01-15 | 0.96816 | -38.2081 | 145.101 | 38 EUMERALLA GROVE, MOUNT ELIZA VIC 3930 | 3313495 | MTN22 | 22kV AC | Rural Short | - switch (disconnector/isolator) | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1370130 | 20200204UTD_02 | FS0857 EUMERALLA ROAD has failed.MFB on site due to smoke coming from switch. Suspect damaged by earlier lightning strike at Eumaralla Banool s/s. Fire report # 6767. PM 1000741380. Switch replaced. Lis=3313495 | - lamps (minor road)
62 | United 19/81 | United | 2020-01-17 | 0.83918 | -37.9581 | 145.207 | 211 GLADSTONE ROAD, DANDENONG NORTH VIC 3175 | 619701 | LD4 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1370827 | 20200304UTD_02 | Tree from school into HV. Bought down conductors. Suspect HVI. Confirmed HVI, #KEY2003, Whispir & 1st email sent/DAO, Emer Mgr & Cust Rel adv LIS#0619701 | - luminaires (minor road)
63 | United 19/82 | United | 2020-01-19 | 0.77926 | -37.8201 | 145.1856 | UNIT 1 24 ROOKS ROAD, NUNAWADING VIC 3131 | 7033741 | NW22 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1371239 | 20200204UTD_06 | BPh FI' up at BH1964 HV CABINET 444 WHORSE Both xarms burnt off t/pole LIS#7033741 PM # 1000742130... S | - poles / columns (major road)
64 | United 19/83 | United | 2020-01-20 | 0.23358 | -38.0276 | 145.2235 | 47 HEALEY ROAD, DANDENONG SOUTH VIC 3175 | 623699 | DVY32 | 22kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1371335 | 20200205UTD_01 | CFA attended and extinguished pole fire between HV+LV xarms. D Glen states "pole is stable, requires closer inspection and either insulators or pole + insulators replaced" Fire report #2706. | - poles / columns (minor road)
65 | United 19/84 | United | 2020-01-20 | 0.33723 | -38.0017 | 145.1104 | 61-65 JARRAH DRIVE, BRAESIDE VIC 3195 | 624869 | MC10 | Low voltage AC (<1kV) | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1371549 | 20200205UTD_02 | - REPLACED BURNT OUT IPC CONNECTION ON WHITE PHASE.- REPLACED BURNING OUT CU - AL D CONNECTION TO TX LEAD.- REPAIRED BURNT OUT CONDUCTOR WITH SLEEVE. no fire on arrival - fire report done #08023 | - connection box
66 | United 19/85 | United | 2020-01-20 | 0.91166 | -38.1995 | 145.1042 | 13 BELLBIRD ROAD, MOUNT ELIZA VIC 3930 | 3311834 | FSH12 | 22kV AC | Rural Short | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1371880 | 20200205UTD_04 | crew replaced HV/LV strain arms, . Lower LV x-arm and lowered/ replaced HV x-arm. New #5 HV Stay. Cut burnt pole top off. No ground fire damage observed. LIS=3311834 | - earth / earthing
67 | United 19/86 | United | 2020-01-21 | 0.2622 | -37.8898 | 145.0623 | 364 NEERIM ROAD, CARNEGIE VIC 3163 | 2327323 | EM10 | 11kV AC | Urban | - fuse (powder filled) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1371932 | 20200205UTD_05 | Found to be a candling fuse 206v on blue, at sub bus 192v at sub 216 on blue. R & W 243 & 245…LIS 2327323
68 | United 19/87 | United | 2020-01-23 | 0.28412 | -38.3987 | 144.9395 | 33A BROWNS ROAD, MAIN RIDGE VIC 3928 | 8831401 | RBD12 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very High | 1 | 1 | 1372960 | 20200124UTD_01 | replaced 3 phase fmb on service pole, caught fire, fire report no 01981. box supplying no 35. nst passed and left on ncia. ESV REF# 13241384 - lis 8831401
69 | United 19/88 | United | 2020-01-27 | 0.39885 | -37.9413 | 145.1024 | 101 ELDER STREET S, CLARINDA VIC 3169 | 2331012 | CDA22 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1373908 | 20200205UTD_03 | Broken hv strain x-arm as above at LIS#2331012...... Crew replaced x-arm today - After the event, determined to be x-arm fire (time unknown) Appears to be old x-arm fire caused by tracking grey fog insulator on red phase. Arm replaced on day under A/P. | Extra low voltage AC (<50V)
70 | United 19/89 | United | 2020-01-31 | 0.99583 | -38.3769 | 145.1488 | 307 SANDY POINT ROAD, SOMERS VIC 3927 | 1108966 | HGS23 | 22kV AC | Rural Short | - fuse (boric acid) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Severe | 2 | 2 | 1375847 | 20200204UTD_04 | MT7722 opened auto reclosed and held, cause was the Blue phase BA fuse unit at MT512 which failed and burnt the bottom contact off; which started a 1m2 ground fire. Fire report 9607. | Low voltage AC (<1kV)
71 | United 19/90 | United | 2020-02-07 | 0.035417 | -37.8584 | 145.0659 | 6 KERFERD ROAD, GLEN IRIS VIC 3146 | 2310294 | K13 | Low voltage AC (<1kV) | Urban | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1377883 | 20200218UTD_02 | West cct krone box b/out & tx lv isols damaged -O/S 6 Kerferd st. Crew repl a 3 ph fmb at pole end feeding a pit. LV transformer krone switch 1000a blades is melted and a small grass fire occurred. Fire ignition report # 02943. LIS=2310294 | 6kV AC
72 | United 19/91 | United | 2020-02-13 | 0.37186 | -38.3523 | 144.9178 | 769 POINT NEPEAN ROAD, ROSEBUD VIC 3939 | 1309797 | DMA21 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1379761 | 20200218UTD_04 | Tree private in #769 Point Nepean Rd, UE responsible, LIS#1309797 and LIS#1309796. Wph and Bph conductor damage - wrap-ons fitted, FIRE Report #1982 completed by onsite crew. Clashing on 22Kv from Pole LIS#13017011 2 bays to pole LIS#13017013. | 11kV AC
73 | United 19/92 | United | 2020-02-13 | 0.59167 | -37.7983 | 145.1843 | 1 WARROCK AVENUE, DONVALE VIC 3111 | 7067545 | NW13 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1379971 | 20200218UTD_03 | Large tree branch broke and fell on HV. No damage. 2x65A BA fuses blown at DT1434. Tree branch fell clear before it could be manualy removed. Fire report #03013 - LIS = 7067545 | 12.7kV AC
74 | United 19/93 | United | 2020-02-14 | 0.75997 | -37.9274 | 145.2507 | 1090 WELLINGTON ROAD, ROWVILLE VIC 3178 | 3413682 | FGY21 | Low voltage AC (<1kV) | Urban | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1380454 | 20200226UTD_01 | Customers reported fire when crew arrived fire was out but they had to replace a burnt out white ph 1000a krone box on LIS# 3413682….likely flames present at some point | 22kV AC
75 | United 19/94 | United | 2020-02-18 | 0.36204 | -38.0175 | 145.2214 | 13 LANYON STREET, DANDENONG SOUTH VIC 3175 | 600027 | DSH31 | Low voltage AC (<1kV) | Urban | - connector / termination | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1381166 | 20200331UTD_01 | Customer stated a small fire had begun at his POA - Fire out on arrival but replaced the white ph active connection on service, burnt out - LIS 0600027 | 66kV AC
76 | United 19/95 | United | 2020-02-18 | 0.79377 | -38.0143 | 145.2629 | 11-13 WESTPOOL DRIVE, HALLAM VIC 3803 | 639074 | DN08 | 22kV AC | Urban | - switch (disconnector/isolator) | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1381450 | 20200331UTD_02 | Customer adved switch opposite hit by lightning and exploded. Was on fire for short time. Now out. Switch replaced lis 0639074 | 330kV AC
77 | United 19/96 | United | 2020-02-19 | 0.30756 | -37.8871 | 145.0463 | 172A NEERIM ROAD, CARNEGIE VIC 3163 | 2328360 | CFD26 | 11kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1381586 | 20200304UTD_05 | refer to t/o #: 1381651 (part of larger fault) unable to group. pole fire due to glass disc insulator failure at pole lis#2328360. CFD26 was shortened, interupted, insulator replaced. fire report # 09421. ESV#13435748, LIS 2328360 | 500kV AC
78 | United 19/97 | United | 2020-02-20 | 0.42387 | -38.4842 | 145.0304 | 92 THE ESPLANADE, FLINDERS VIC 3929 | 9864733 | RBD21 | 22kV AC | Rural Short | - connector / termination | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 1382078 | 20200324UTD_01 | Crew replaced 31.5A PFF Rph including top and bottom connection rings which were damaged due to fuse not being latched correctly. No a HV "fuse"sue - a HV connection issue | Extra low voltage DC (<120V ripple free)
79 | United 19/98 | United | 2020-02-27 | 0.38389 | -37.9399 | 145.04 | 1037 NEPEAN HIGHWAY, MOORABBIN VIC 3189 | 1815697 | MR24 | 11kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1383685 | 20200304UTD_06 | Crossarm Fire LIS 1815697 - 2nd call completed xarm replacement, did not provide any details of poss firestart | Low voltage DC (<1.5kV)
80 | United 19/99 | United | 2020-03-02 | 0.23898 | -38.3674 | 144.8093 | 2549 POINT NEPEAN ROAD, RYE VIC 3941 | 1303874 | STO23 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1384438 | 20200310UTD_01 | xarm fire at tee pole Pt Nepean rd tee to TAROOK WHITECLIFFS. Zinfra crew changed pole. Fire Ignition Report #7061. - lis 1303874 | 600V DC
81 | United 19/100 | United | 2020-03-02 | 0.50065 | -37.9939 | 145.235 | 15 MATIPO STREET, DOVETON VIC 3177 | 623092 | DN11 | Low voltage AC (<1kV) | Urban | - overhead service conductor (residential) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1384525 | 20200306UTD_01 | replaced service, burning at simpy crimp. sign of fire on service, melting and burn marks. fire report#05245. fire was out when crew arrived. WISPIR sent. ESV #: 13517982. | 1500V DC
82 | United 19/101 | United | 2020-03-04 | 0.077836 | -37.9831 | 145.08 | 46 LOWER DANDENONG RD MENTONE VIC 3194, | 1822639 | M33 | 11kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1384996 | 20200409UTD_03 | Tree branch from #46 Lower Dandenong Rd fell over HV conductors. Secondary damage to Bph HV isol at CH6334. MFB reported branch was on fire - LIS 1822639 | Earthing cable
83 | United 19/102 | United | 2020-03-11 | 0.19933 | -37.7908 | 145.174 | 5 MITCHAM ROAD, DONVALE VIC 3111 | 7066918 | NW13 | Low voltage AC (<1kV) | Urban | - lamps (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1387113 | 20200325UTD_01 | Street light fire Disconected light and made safe Light head requires replacement LIS 7066918
84 | United 19/103 | United | 2020-03-17 | 0.10278 | -37.9748 | 145.2488 | 8 NICHOLSON CLOSE, ENDEAVOUR HILLS VIC 3802 | 638159 | LD2 | Low voltage AC (<1kV) | Urban | - underground cable | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1388956 | 20200327UTD_02 | A // pillar blew up and u/g crew are repairing after an LVIBS was issued. see also TO # 1388955 - crew have repaired // switch in pillar Clsest LIS 0638159
85 | United 19/104 | United | 2020-03-17 | 0.51045 | -38.3746 | 145.0514 | 101 STANLEYS ROAD, RED HILL SOUTH VIC 3937 | 1318468 | DMA13 | 22kV AC | Urban | - fuse (boric acid) | two phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 1389174 | 20200409UTD_02 | RPh BA at RB0510 was found broken in 1/2 with obvious signs of candling... Replaced barrell... LIS#1318468... 1Ph supply. | single wire earth return (SWER)
86 | United 19/105 | United | 2020-03-20 | 0.98113 | -38.0088 | 145.0983 | 51A GOVERNOR ROAD, MORDIALLOC VIC 3195 | 1807866 | MC3 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1390226 | 20200327UTD_01 | Pole fire at LIS#1807866. Awaiting daylight assessment of damage and replacement parts required. Fire report number #03748. ESV fire report to be made within 48hrs | single phase
87 | United 19/106 | United | 2020-04-03 | 0.49741 | -37.8925 | 145.232 | 8 BARRY COURT, SCORESBY VIC 3179 | 619620 | BRA21 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1394037 | 20200427UTD_03 | Customer reported fronds from Palm tree were intermittently sparking/burning when touching wires…….Tree trimmed. LIS 0619620 | two phase
88 | United 19/107 | United | 2020-04-04 | 0.21824 | -37.9984 | 145.0742 | 141 BEACH ROAD, PARKDALE VIC 3195 | 1808847 | M25 | Low voltage AC (<1kV) | Urban | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1394207 | 20200406UTD_01 | MFB reported a pole fire outside premises, on arrival a Krone box had caught fire. Fire report # 03749, UE Emergency ESV notified ESV Ref #13753960 Crew re attended next day and repl krone box LIS 1808847 | three phase
89 | United 19/108 | United | 2020-04-09 | 0.5033 | -37.8797 | 145.0444 | 94 QUEENS AVENUE, CAULFIELD EAST VIC 3145 | 2327650 | CFD24 | 11kV AC | Urban | - capacity balancing units | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1395899 | 20200427UTD_06 | Customer reported box on pole on fire. Structure was "Queen Derby" Cap Bank. There was no fire on ground - fire report #08024. LIS 2327650
90 | United 19/109 | United | 2020-04-15 | 0.76944 | -38.2114 | 145.0506 | 6-8 KALIMNA DRIVE, MORNINGTON VIC 3931 | 1100802 | MTN35 | Low voltage AC (<1kV) | Rural Short | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1397340 | 20200427UTD_05 | CFA advise approx halfway down pole was on fire, but now out. LV Isolator krone box melted suspect due to corrosion & loose connection. 1/2 sqm fire at base of pole fire report #6831 LIS 1100802
91 | United 19/110 | United | 2020-04-17 | 0.76667 | -38.152 | 145.1333 | 7 MCMAHONS ROAD, FRANKSTON VIC 3199 | 3306626 | FTS-FTN | 66kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1398177 | 20200427UTD_01 | ESV report #13834428 Fire report #6965 - Confirmed fire start, Fire is on pole, about 3M down from top of pole. Suspected cause maybe 66kV tracking as brown insulator appeared broken. LIS 3306626 | Negligible: no ground fire
92 | United 19/111 | United | 2020-04-22 | 0.40069 | -38.2002 | 145.1162 | 58-62 ALLISON ROAD, MOUNT ELIZA VIC 3930 | 3315364 | FSH12 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 1399254 | 20200427UTD_02 | Customer tree branch at 62 Alison Rd fell through HV and was resting on LV when crew arrived. Branch removed under shutdown. No damage to HV/LV conductors. 20CFA had reported sparking and flames. LIS 3315364 | Localised: less than 10 sq.m
93 | United 19/112 | United | 2020-05-05 | 0.76597 | -37.8353 | 145.1759 | 422 CANTERBURY ROAD, FOREST HILL VIC 3131 | 7020345 | NW33 | Low voltage AC (<1kV) | Urban | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1402844 | 20200512UTD_01 | LV red phase fuse isolator Debris from the melting pieces of the isolator this caused a small area fire on ground in some plants- as per customer on site MFB had already attended - too dark to take photos Fire report created- LIS 7020345 | Small: 10 - 1000 aq.m
94 | United 19/113 | United | 2020-05-06 | 0.79236 | -37.8821 | 144.9784 | UNIT 1 1 ORMOND ESPLANADE, ELWOOD VIC 3184 | 2308954 | EW12 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1403253 | 20200512UTD_02 | Replaced 3 phase FMB @ pole end that was on fire o/s 1 Ormond Esplanade Elwood- Fire Report #9615 - LIS 2308954 | Medium: 1000 sq.m - 10 ha
95 | United 19/114 | United | 2020-05-09 | 0.76551 | -37.8714 | 144.9962 | 19 THE AVENUE, BALACLAVA VIC 3183 | 2304444 | BC11 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1404071 | 20200514UTD_01 | MFB reported a minor fire at the POA. Crew arrived and replaced the UE owned porcelain box which was believes to have ignited the small fire as well as the neutral service with black 2/c service. LIS 2304444 | Large: more than 10 ha
96 | United 19/115 | United | 2020-05-13 | 0.65863 | -38.4724 | 144.8947 | 164 CAPE SCHANCK ROAD, CAPE SCHANCK VIC 3939 | 1312552 | RBD21 | 22kV AC | Rural Short | - fuse (EDO fuse) | two phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1405093 | 20200518UTD_01 | Crew replaced 10A EDO fuse at CAPE SCHANCK -ISO S/S B phase. Fuse had candled. SWER ACR RB7329 was opened by NCC to enable fuse change on the 22kV side of ACR. - fire report #6832, no ground fire. - ESV ref 13971860. LIS 1312552
97 | United 19/116 | United | 2020-05-14 | 0.5716 | -38.3092 | 145.0698 | 166 FOXEYS ROAD, TUERONG VIC 3915 | 1105620 | MTN32 | 22kV AC | Rural Short | - fuse (boric acid) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1405386 | 20200518UTD_02 | A HV fuse at "Ellerina P5-Junction" s/stn has candled.S/S is fully animal proofed. Fire report #6841 - no ground fire start - ESV ref 13971883 - LIS 11056203 Crew replaced a 6 Amp BA on White phase.
98 | United 19/117 | United | 2020-05-14 | 0.74167 | -37.8822 | 145.0111 | 54 ALLISON ROAD, ELSTERNWICK VIC 3185 | 2303150 | EL13 | Low voltage AC (<1kV) | Urban | - switch (disconnector/isolator) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1405473 | 20200518UTD_03 | MFB was on site at "Morton-Leslie" S/Stn when crew arrived and reported fire on assets but had gone out on its own - Source of fire at red phase isol (equip too melted to determine). ESV advised ref # 13978228 - LIS 2303150 | Started in or originated from a distribution system
99 | United 19/118 | United | 2020-05-20 | 0.42194 | -38.4232 | 144.8761 | 112 MAXWELL ROAD, FINGAL VIC 3939 | 1318609 | STO14 | 22kV AC | Urban | - fuse (boric acid) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1406965 | 20200521UTD_01 | Punshon Maxwell S/S 2 HV fuses candled, R and W phase , single phase S/S ,P/P ,conc pole, 6K BA fuses, fire report and ESV to be notified. ESV Ref 14001255 - LIS = 1318609 | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system
100 | United 19/119 | United | 2020-05-21 | 0.46736 | -37.8831 | 144.9901 | 128 GLEN HUNTLY ROAD, ELWOOD VIC 3184 | 2311320 | EW02 | Low voltage AC (<1kV) | Urban | - overhead service conductor (residential) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1407345 | 20200525UTD_01 | Service line rubbing up against tree at pole end & had sparks & flames from it, Council has cut back tree form service line to units replaced 25 metres of 35mm 4c service....Fire evident on adjacent council vegetation ...Fire report 3846, LIS = 2311320 | Started by any person, bird, reptile or other animal coming into contact with a distribution system
101 | United 19/120 | United | 2020-06-06 | 0.46736 | -38.3657 | 144.7593 | 42 CENTRAL AVENUE, BLAIRGOWRIE VIC 3942 | 1304267 | STO21 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1412201 | 20200611UTD_01 | A resident at number 45 Central Ave Blairgowrie advised she saw something on the pole on fire. On arrival the crew identified a fire damaged FOLCB outside # 42 Central Ave which they replaced - LIS 1304267 | Started by lightning striking a distribution system or a part of a distribution system
102 | United 19/121 | United | 2020-06-08 | 0.28634 | -37.8581 | 145.1509 | 390 BLACKBURN ROAD, BURWOOD EAST VIC 3151 | 7025054 | EB33 | Low voltage AC (<1kV) | Urban | - lamps (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1412367 | 20200629UTD_02 | MFB reported a street light on fire.....crew attended and isolated a 250W HPS. To be replaced by street light crew. LIS 7025054 | Started by any other thing forming part of or coming into contact with a distribution system
103 | United 19/122 | United | 2020-06-09 | 0.77708 | -37.9053 | 144.9881 | 301 ST KILDA STREET, BRIGHTON VIC 3186 | 1806162 | NB33 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1413040 | 20200611UTD_02 | A report came in to UE of a FMB sparking at 310 St Kilda St, Brighton. On arrival the crew identified a fire damaged FOLCB on pole LIS 1806162. The likely cause was determined by EIO to be a earth defect within the customers installation at 301 St Kilda St | Otherwise started by a distribution system
104 | United 19/123 | United | 2020-06-11 | 0.36162 | -38.0002 | 145.0762 | 155 BEACH ROAD, PARKDALE VIC 3195 | 1807524 | M25 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1413538 | 20200629UTD_01 | Customer reported a fire on the pole. Crew attended and and reported the fire was actually a FOLCB feeding underground services on LIS 1807524.
105 | United 19/124 | United | 2020-06-11 | 0.98125 | -37.9593 | 145.0601 | 64A WILSON STREET, CHELTENHAM VIC 3192 | 1815005 | HT11 | Low voltage AC (<1kV) | Urban | - dropper / bridge | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1413845 | 20200629UTD_08 | Customer advised pole in front of property was sparking and arcing. Turned into flames but went out quickly. Black scorch marks near the powerlines and x-arm. Crew arrived and replaced a blackened LV IPC, LIS=1815005
106 | United 19/125 | United | 2020-06-15 | 0.074525 | -38.173 | 145.1872 | 240 WARRANDYTE ROAD, LANGWARRIN VIC 3910 | 8816167 | FSH21 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1414449 | 20200629UTD_07 | CFA reported a branch failed and was resting on the HV conductors -and requested tree require to be cut prior to fire brigade extinguishing fire. Crew arrived and cut tree branch clear, small branch was smoldering on ground - no fire start on the ground. | 1
107 | United 19/126 | United | 2020-06-17 | 0.011412 | -38.2003 | 145.2428 | 65 EVANS STREET, PEARCEDALE VIC 3912 | 3321507 | LWN21 | 22kV AC | Rural Short | - dropper / bridge | single phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1415152 | 20200629UTD_03 | Customer at no.65 Evans St said he saw flames on transformer. When the crew arrived they found a melted HV bushing cover caused by loose connection. They carried out repairs and replaced 6 k BA , Red phase. | 2
108 | United 19/127 | United | 2020-06-22 | 0.70647 | -38.2588 | 145.1818 | 4 CANNERY COURT, TYABB VIC 3913 | 9923466 | HGS33 | Low voltage AC (<1kV) | Rural Short | - underground cable | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1416801 | 20200629UTD_04 | LV pillar box caught fire after 160amp cct breakers failed, replacement of pillar box and breakers R & W 250 amp LV fuses blew at dist cabinet that feeds 5 Cannery ct Tyabb . ESV notified # 14201906 Small amount <0.5m of grass burnt. | 3
109 | United 19/128 | United | 2020-06-23 | 0.90069 | -38.3291 | 144.7169 | 55 FRIMMELL WAY, PORTSEA VIC 3944 | 1307407 | STO22 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1417207 | 20200629UTD_06 | 3PH fmjb to UG supply (53 & 55 Frimmell Way) caught fire due to corrosion, caused 2 x 250amp din LV fuses to FRANKLIN PARKVILLE s/s on white/blue phase. Damaged 2 wire service to 60 Frimmell Way repl. Repaired 2 wire service to 58 Frimmell Way. Services height compliant, premises tested ok & left, no damage to pole, only to fmjb that burnt out/caught fire. Fire ignition report 04460. Details emailed to RC (TS) and Eric C, whispir required, NCC Mgt to send. | 4
110 | United 19/129 | United | 2020-06-27 | 0.79236 | -38.176 | 145.1902 | 262 WARRANDYTE ROAD, LANGWARRIN VIC 3910 | 3301774 | FSH21 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1418250 | 20200629UTD_05 | Customer reported that the Service fuse box on pole in front of property (enter off Anthoney's Lane) has caught fire. Crew arrived (no fire on arrival) and replaced a melted transformer FMB at "WARRANDYTE T44 NTH 2" substation. | 5
111 | PowerCor 19/20 | PowerCor | 2019-04-07 | 0.45278 | -37.5467 | 143.9119 | 20 SPRINGS ROAD, BROWN HILL VIC 3350 | 32000612 | BAN015 | 22kV AC | Rural Short | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0007472 | 20190715PWA_08 | A customer reported transformer and wire on fire at the incident location. The attended crew found that an insulated HV dropper on the substation pole ignited. There was no ground fire. The crew made the place safe and repairs arranged.
112 | PowerCor 19/21 | PowerCor | 2019-10-07 | 0.90417 | -38.0765 | 144.3692 | 292 -296 Princes Highway Corio 3214 | 30268929 | FNS021 | 22kV AC | Rural Short | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | INC-0007772 | 20190809PWA_01 | Pole fire reported at incident location. There was no ground fire, no reported injuries or third party property damage.
113 | PowerCor 19/22 | PowerCor | 2019-11-07 | 0.54167 | -36.272 | 143.1372 | 1983 Borung Hwy, Jeffcott VIC 3480 | 31002530 | CTN006 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | INC-0007775 | 20190809PWA_02 | During pole inspection pole fire damage to crossarm found. There was no ground fire, no reported injuries or third party damage.
114 | PowerCor 19/23 | PowerCor | 16/07/2019 | 0.64167 | -35.262 | 143.0506 | 2375 Springfield Rd Chillingollah 3585 | 32155903 | SHL001 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | INC-0007569 | 20190724PWA_02 | A customer reported a wire hanging low in the mid air and smoke coming from the pole at the incident location. The attended crew found that the angle cross arm burnt through on the pole. The crew made the place safe and repairs completed.
115 | PowerCor 19/24 | PowerCor | 16/07/2019 | 0.48472 | -38.3592 | 142.5391 | 310 HORNE ROAD, WARRNAMBOOL VIC 3280 | 30241936 | WBL005 | 12.7kV AC (SWER) | Rural Short | - pole (wood) | single wire earth return (SWER) | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | INC-0007623 | 20190729PWA_01 | A customer reported a smoking pole at the incident location. The attended crew found that the pole had been burnt through some time ago and at this time it was smoking. The place made safe and repairs done. There was no ground fire or injuries. This insulator had been identified as P2 maintenance to replace it. However this pole fire which causes to damage the pole occurred in between the asset inspection date (P2 report) and this incident date. It believes the pole fire self-extinguished and no protection operations. It was not reported. This incident was informed to the asset investigation team. This conductor was replaced and armour rod was fitted recently. These upgrades should have been done together with replacement of insulator per the asset investigation team. The team will conduct a line patrol to check if there are more this type insulators on the line.
116 | PowerCor 19/25 | PowerCor | 19/07/2019 | 0.5 | -34.2134 | 142.1484 | 1 SPRINGFIELD DRIVE MILDURA 3500 | 30333970 | MDA034 | 22kV AC | Urban | - overhead conductor (bare; steel) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0007537 | 20190722PWA_01 | Call received from Vic Fire of pole fire at incident location. On arrival crew found a small burnt area of nature reserve adjacent to a concrete pole. CFA had extinguished the fire. There were no reported injuries or third party property damage.
117 | PowerCor 19/26 | PowerCor | 19/07/2019 | 0.74167 | -38.2594 | 144.5349 | 3 Lowe Street, Ocean Grove | 33043236 | DDL011 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0007540 | 20190722PWA_02 | A customer saw sparks coming from pole with streetlight on it, first pole in Lowe St. Power went off momentarily. A crew was dispatched to investigate. On arrival the crew identified a live HV conductor laying on the ground between P1 (LIS-7141) and P2 (LIS-787357), causing burns to the green grass. The crew found a deceased bird believed to be the likely cause. It was suspected that the bird had bridged over two HV phases, causing 1 phase helical termination to fail and conductor to fall to ground. There were no reported injuries or third party property damage. The fire brigade and police had the road blocked to keep the public away from the danger.
118 | PowerCor 19/27 | PowerCor | 24/07/2019 | 0.47917 | -35.2317 | 143.451 | White Road 284 meters west of N S Rd Worrien North, 3585. | 32161264 | SHL004 | 22kV AC | Rural Short | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0007571 | 20190724PWA_03 | Vic Fire reported wires down and pole on fire reported at Intersection of White Rd and Nth Sth Rd Beverford. On arrival found that pole top had burnt thru and toppled over all insulators and phases still connected. There was no ground fire, no reported injuries or third party property damage. Crew isolated the pole and all supply restored. One property will be off until pole replaced.
119 | PowerCor 19/28 | PowerCor | 26/07/2019 | 0.8 | -36.4036 | 144.9614 | 43 Cowie Road, Girgarre VIC 3624 | 32189817 | SHP011 | 22kV AC | Rural Short | - transformer (pole mounted) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0007728 | 20190809PWA_06 | Customer reported pole fire at the incident location, customer also advised that a large Crow's nest was built on the structure in question & believe that to be the source of the fire. Upon arrival crew found that a birds nest was built on the termination substation structure, material within the nest was believed to be conductive & when a rain event commenced a flashover occurred that commenced combustion of the nesting materials. The fire soon self extinguished with the precipitation. No ground fire occurred, no damage to 3rd party.
120 | PowerCor 19/29 | PowerCor | 31/07/2019 | 0.75 | -37.9688 | 144.6851 | Opposite 668 Diggers Rd Werribee South 3030 (Melways 199 Ref E9) | 32171115 | WBE034 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0007679 | 20190801PWA_03 | MFB and local resident reported pole fire in Diggers Rd. that had now extinguished. Attending Powercor fault crew noted a burnt FOLCB. There were no shocks, injuries or ground fire.
121 | PowerCor 19/30 | PowerCor | 2019-08-08 | 0.32847 | -38.602 | 143.0009 | 2549 C164, Port Campbell VIC 3269, Australia | 32056249 | TRG003 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | INC-0007832 | 20190814PWA_02 | A passer-by reported a pole on fire at the incident location. Upon arrival a Powercor crew found a melted fuse box on the pole. There was no ground fire, no reported injuries or third party property damage.
122 | PowerCor 19/31 | PowerCor | 2019-11-08 | 0.17917 | -34.3065 | 142.1642 | 6 Nealie St, Cardross VIC 3496, Australia | 32145619 | RCT023 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0007850 | 20190815PWA_03 | Pole fire reported by Vic Fire at incident location. On arrival crew found pole had burnt from below HV crossarm to stay position. There was no ground fire, no reported injuries or third party property damage.
123 | PowerCor 19/32 | PowerCor | 2019-11-08 | 0.33333 | -34.2219 | 142.1677 | 640 Sandilong Ave, Irymple VIC 3498, Australia | 30095461 | MDA023 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0007852 | 20190815PWA_04 | Report received of a pole fire at the incident location. On arrival crew found a crossarm had burnt in half. There was no HVI. There was no ground fire, no reported injuries or third party property damage.
124 | PowerCor 19/33 | PowerCor | 13/08/2019 | 0.85347 | -36.3533 | 145.4314 | 133 GRAHAMVALE ROAD, GRAHAMVALE VIC 3631 | 30128968 | SHN024 | Low voltage AC (<1kV) | Rural Short | - fuse (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0007875 | 20190816PWA_03 | Report received of a house fire at incident location. On arrival crew found fire extinguished and observed that the meter board had sustained fire damage. Crew was advised that customers gas heating had failed and they were running 4 x electric heaters in the house. There was no ground fire, no reported injuries.
125 | PowerCor 19/34 | PowerCor | 20/08/2019 | 0.99306 | -37.7369 | 144.8095 | UNIT1,11 LESLIE STREET, ST ALBANS, VIC 3021 | 30247361 | SA012 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0007914 | 20190821PWA_02 | Emergency Services reported fire at POA at the incident location. On arrival the crew found that the FOLCB at the POA was completely melted, dropping hot debris to the ground, which started a small grass fire in the front of the property of less than 0.5 meter square. There were no reported injuries.
126 | PowerCor 19/35 | PowerCor | 27/08/2019 | 0.39306 | -36.6091 | 143.9497 | 5 Cementry Rd, Bridgewater on Loddon | 30028602 | BET001 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | INC-0007980 | 20190828PWA_03 | A pole fire was reported by a customer. On arrival, A Powercor crew found that the LV fuse box on the pole caught fire. There was fallen debris but no ground fire. There was no ground fire, no reported injuries or third party property damage.
127 | PowerCor 19/36 | PowerCor | 31/08/2019 | 0.0076389 | -36.0553 | 145.6977 | Bourke Rd, Katamatite VIC 3649, Australia | 32185775 | NKA001 | 22kV AC | Rural Long | - fuse (boric acid) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0008062 | 20190903PWA_03 | Passer by reported sparking and hot debris being emitted from pole top at incident location. Upon arrival crew found that a Boric Acid fuse tube had candled and burnt through. No resultant ground fire.
128 | PowerCor 19/37 | PowerCor | 2019-03-09 | 0.29444 | -35.3426 | 143.5592 | 257 Beveridge st Swan Hill vic 3585 | 33070207 | SHL007 | 22kV AC | Urban | - pole (concrete) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0008611 | 20191101PWA_01 | Bird flashed over on pole top and caught fire. There was no ground fire or reported injuries.
129 | PowerCor 19/38 | PowerCor | 2019-04-09 | 0.41042 | -36.77 | 144.2777 | 10 Russell St Quarry Hill 3550 | 31008832 | BGO022 | Low voltage AC (<1kV) | Urban | - connector / termination | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0008074 | 20190905PWA_01 | Customers reported supply issues at the incident location. Street light fire due to neutral fault.
130 | PowerCor 19/39 | PowerCor | 2019-05-09 | 0.27222 | -35.8856 | 144.2399 | Leitchville-Kerang Rd, Horfield VIC 3567, Australia | 33021753 | CHA005 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0008095 | 20190906PWA_02 | Customer reported wires down and fire at incident location. Upon arrival the fault crew found that a swan had hit conductors nearest pole 17 of the Leitchville line, bringing 2 of the 3 conductors down. A ground fire was initiated due to downed conductors, approximately 3M x 10M of road verge was burnt. There was no injuries or third party property damage.
131 | PowerCor 19/40 | PowerCor | 2019-07-09 | 0.62639 | -35.9039 | 141.1475 | Unnamed Road, Telopea Downs VIC 3420 | 30087080 | NHL031 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | INC-0008612 | 20191101PWA_02 | Pole replaced due to pole fire. No ground fire reported.
132 | PowerCor 19/41 | PowerCor | 13/09/2019 | 0.925 | -38.5489 | 143.9797 | 22 Francis Street, Lorne | 30261511 | CLC005 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | INC-0008278 | 20190920PWA_01 | Vicfire reported a pole fire at the incident location, on arrival the crew found a single phase FOLCB on the pole in front of the incident location address had overheated and caught fire. There was damage to wiring both up and down the pole, however there was no ground fire reported. There were no injuries or third party damage reported.
133 | PowerCor 19/42 | PowerCor | 14/09/2019 | 0.25486 | -38.2828 | 144.4012 | 291 BREAMLEA ROAD, CONNEWARRE VIC 3227 | 33045904 | WPD024 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | INC-0008193 | 20190916PWA_01 | A swan contacted the HV conductors at the incident location, causing one of the HV conductors to fall to the ground alive via back-feed. This situation resulted in several small grassfires, totaling less than 1m2 in total. The CFA attended, however the grassfires self extinguished once the supply was isolated. There were no reported injuries or third party damage.
134 | PowerCor 19/43 | PowerCor | 16/09/2019 | 0.60694 | -34.2384 | 142.1967 | 206 Ginquam Ave, Irymple VIC 3498, Australia | 30097798 | RCT021 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0008221 | 20190918PWA_01 | Report received from Vic Fire of a crossarm fire at incident location. There was no damage to the pole, the crossarm was burnt in half and HV conductors have fallen into LV below. There was suspected HVI effecting possibly 12 premises. There was no ground fire, no reported injuries.
135 | PowerCor 19/44 | PowerCor | 16/09/2019 | 0.54167 | -34.228 | 142.1005 | 3158 WALNUT AVENUE,MILDURA,VIC,3500 In front of this property. | 31020923 | MBN032 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0008224 | 20190918PWA_02 | Vic Fire reported pole fire at incident location. On arrival crew found crossarm on fire, part of crossarm burnt off and conductor hanging low. There was no ground fire, no reported injuries or third party property damage.
136 | PowerCor 19/45 | PowerCor | 21/09/2019 | 0.09375 | -36.1312 | 145.5592 | 503 Drumanure Rd Invergordon | 32184425 | NKA001 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0008318 | 20190923PWA_02 | Customer called reporting wire down at back of his property which has caused a fire. On Arrival, crew found a tree had fallen across a slack span of conductor, breaking the wires mid span and bringing them to ground. A small burn section was found under the conductors approx. the size of a "dinner plate". No injury or third party damage.
137 | PowerCor 19/46 | PowerCor | 23/09/2019 | 0.61736 | -37.7111 | 144.7325 | 58 Olsen Retreat, Caroline Springs VIC 3023, Australia | 30322459 | SA011 | Low voltage AC (<1kV) | Urban | - underground service cable (other) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0008393 | 20191002PWA_06 | Constable Alistair- Caroline Springs Police reports copper has been stolen out of pit on hume drive- between Infinity Dr and Lancefield Dr (thinks roughly at the back of 57 olsen retreat), pit lid is missing, wires pulled out of pit and exposed and burnt grass around the pit. Unsure of any other details of who has done this. On arrival PAL crew have advised that the LV cables were laying on the ground adjacent to the affected pit and were found to be ALIVE. They further advised that a pair of secatier cutters were found at the scene and the were burn marks around the service pit. No injuries have been reported to PAL.
138 | PowerCor 19/47 | PowerCor | 25/09/2019 | 0.54653 | -36.3646 | 145.4735 | 540 New Dookie Rd, Shepparton East 3631 | 33093102 | SHN024 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0008365 | 20190926PWA_01 | A Lend Lease G&B Crew contracted to Powercor were attending a P1 fault on P71 Saleyards Spur (LIS-6304), where there was damage to an insulator and the aluminum conductor, believed to have been caused by a previous lightning strike. Whilst the crew were in the process of repairing the conductor, the conductor broke and fell to the ground. On contact with the ground, the conductor started a small grassfire of approx. 3m2. There were no injuries or third party damage.
139 | PowerCor 19/48 | PowerCor | 2019-01-10 | 0.73264 | -36.7824 | 144.2305 | 105 NORELLE CRESCENT,KANGAROO FLAT,VIC,3555 | 33011824 | BET006 | 22kV AC | Rural Short | - pole (concrete) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0008389 | 20191002PWA_03 | A customer reported hearing loud bang, went outside and pole was sparking and cause fire in grass under pole. Supply not affected now but power did go off for a moment, fire is out now. Crew found a bird caused flashover on center phase HV bridge at pole 63 Norelle Cresent. There was a ground fire, no reported injuries or third party property damage.
140 | PowerCor 19/49 | PowerCor | 2019-02-10 | 0.085417 | -35.5003 | 143.6792 | 320 Ridge Rd, Tresco VIC 3583 | 33068355 | KGT004 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0008390 | 20191002PWA_04 | Report received of fallen conductor resulting in 100 x 200 square metres of stubble being burnt. On arrival crew found that HV conductor had parted about one metre from the pole. Protection operated. There was a ground fire, no reported injuries.
141 | PowerCor 19/50 | PowerCor | 2019-03-10 | 0.45 | -34.7386 | 142.6536 | Staley Rd, Wemen | 32143201 | WMN013 | Low voltage AC (<1kV) | Rural Short | - switch (disconnector/isolator) | single phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0008421 | 20191007PWA_02 | A Customer reported that a few days ago when he started his pump, the nearby pole dropped a few large sparks that started a small grass fire. On arrival the crew found that a Low Voltage Isolator had overheated and caused hot debris to fall to the ground starting a small grassfire. The Customer told the crew that the initial grassfire was less than 1m2 in size, and the customer stamped it out with his feet. The customer subsequently burnt a larger area himself to create a fire break. There were no reported injuries or third party damage.
142 | PowerCor 19/51 | PowerCor | 2019-04-10 | 0.38889 | -38.5378 | 143.9752 | 46B Mountjoy Parade, Lorne VIC 3232, Australia | 30273992 | CLC005 | Low voltage AC (<1kV) | Rural Short | - luminaires (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0008550 | 20191023PWA_05 | A customer called to report that on the previous night, the street light opposite No 50, was on fire, and that the lens fell on a truck, they also claim that they called 000 at the time, but no call was received by Powercor. On arrival the crew found the streetlight had overheated and was badly damaged and melted, the remains of the lens was on the ground. There was no ground fire, and no reported third party damage.
143 | PowerCor 19/52 | PowerCor | 13/10/2019 | 0.79583 | -37.5295 | 143.8652 | 10 Harrier Dr, Invermay Park VIC 3350, Australia | 32011052 | BAN011 | 22kV AC | Rural Long | - pole (wood) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0008470 | 20191014PWA_01 | Vic fire reported a small ground fire ( 5 x 1 mts) at the base of a pole at the incident location. On arrival the crew noticed that one HV crossarm strap had become loose, but was not in contact with conductors. The fire start has been attributed to a bird contact although a bird was not found at the site. There was no injuries or third party property damage.
144 | PowerCor 19/53 | PowerCor | 25/10/2019 | 0.29167 | -35.4255 | 142.461 | 2446 Sunraysia Hwy Turriff 3488 | 32159041 | OYN005 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very high | 1 | 1 | INC-0008566 | 20191028PWA_01 | Customer reported loss of supply. On arrival crew found a deteriorated crossarm and one conductor had fallen to ground causing a small grass fire (30m x 20m). The fire self extinguished. There was no injuries.
145 | PowerCor 19/54 | PowerCor | 28/10/2019 | 0.35556 | -35.973 | 144.3967 | 77 Lavender rd Gunbower 3566 | 32032440 | CHA005 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0010478 | 20200501PWA_01 | Following a report of an outage at the incident location crew attended site. On arrival crew found an EDO fuse burnt in half. There was no ground fire, no reported injuries or thrid party property damage.
146 | PowerCor 19/55 | PowerCor | 31/10/2019 | 0.63472 | -38.0375 | 144.3562 | 520 BACCHUS MARSH ROAD, LARA VIC 3212 | 33044700 | FNS011 | 22kV AC | Rural Short | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very high | 1 | 1 | INC-0010479 | 20200501PWA_02 | Following on from supply outage crew found hung up burnt edo fuse. There was no ground fire, no reported injuries or third party property damage.
147 | PowerCor 19/56 | PowerCor | 2019-01-11 | 0.71389 | -37.9263 | 144.6471 | 215 Farm Road, Cocoroc, VIC, 3030 | 30304230 | WBE033 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0008621 | 20191104PWA_02 | MMBW report grass fire possibly due to conductor clash between lis 799280 and 799276. PCA Faults Crew attended site and at first could not find any evidence of any grass fire within the span from Pole 2 LIS-799276 south west to Pole 3 LIS-799280. After further investigations the crew advised that they discovered a grass fire of approx. 30m x 30m, some 20m south of the conductors.
148 | PowerCor 19/57 | PowerCor | 2019-01-11 | 0.50417 | -36.5331 | 145.0586 | 5 Waranga Drive Waranga Shores 3612 | 33089098 | SHP014 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | Very high | 1 | 1 | INC-0008623 | 20191104PWA_04 | Customer reported wire down hanging from pole and down onto grass, has caused fire, Fire brigade has just arrived to put fire out, at incident location. Crew found a customers tree had damaged an O/H HV conductor, starting a 800m2 ground fire, no property damage, no injuries, Vegetation Crew working nearby assisted with clean-up.
149 | PowerCor 19/58 | PowerCor | 2019-01-11 | 0.086111 | -37.8586 | 144.7149 | 91 Grevillea Crescent, Hoppers Crossing, VIC, 3029 | 33073674 | LV009 | Low voltage AC (<1kV) | Urban | - overhead service conductor (residential) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0008626 | 20191104PWA_05 | VIC Fire reported Service wire sparking and melted, started grass fire. Upon arrival the PCA Faults Crew have found that the POA/FOLCB at House No.91 Grevillea Crescent, Hoppers Crossing, VIC, 3029 has overheated, failed and melted and burnt away. The resultant hot melted plastic from the POA above has fallen onto the ground below causing a small grass fire of approximately 3m x4m, within the front yard of No.91 Grevillea Crescent, Hoppers Crossing, VIC, 3029. The MFB attended site and the grass fire was extinguished.
150 | PowerCor 19/59 | PowerCor | 2019-01-11 | 0.58472 | -36.3267 | 143.4685 | Calder Hwy, Woosang 3518 (near Edwards Rd) (13km South of Charlton) | 30229277 | BETS-CTN | 66kV AC | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Severe | 2 | 9.2 | INC-0008627 | 20191104PWA_06 | Crew were investigating an outage on BETS-CTN 66kV line and found a broken conductor and ground fire.
151 | PowerCor 19/60 | PowerCor | 2019-02-11 | 0.63958 | -36.5831 | 145.0136 | 5 McDonald Street Rushworth 3612 | 30127619 | SHP014 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0008628 | 20191104PWA_07 | Customer reported a pole fire out front of school on McDonald Street, wooden pole. Crew found that FSD had been consumed and required replacement.
152 | PowerCor 19/61 | PowerCor | 2019-02-11 | 0.097917 | -34.2008 | 142.1538 | 276 San Mateo Avenue Mildura 3500 | 32147322 | MDA022 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0008629 | 20191104PWA_08 | Vic Fire reported a Pole fire at intersection of Burrows Street and San Mateo Avenue, fire on HV cross arm. Crew found small fire on pole had started at king bolt.
153 | PowerCor 19/62 | PowerCor | 2019-02-11 | 0.47153 | -37.8701 | 144.705 | 32 Macedon Street, Hoppers Crossing, VIC, 3029 | 32174345 | LV009 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0008638 | 20191106PWA_03 | Customer advised that mains wire has come off insulator and is resting on the cross arm, making a sizzling sound. On arrival the PCA Faults Crew have advised that the HV cross arm has burnt.
154 | PowerCor 19/63 | PowerCor | 2019-03-11 | 0.24097 | -35.9967 | 144.4742 | 159 Patho Cemetery Road Patho 3564 | 33022125 | CHA005 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0008630 | 20191104PWA_09 | Customer reports of supply failure. Crew found wires down during line patrol due to pole fire, pole top assembly replaced.
155 | PowerCor 19/64 | PowerCor | 2019-04-11 | 0.7375 | -36.6133 | 145.3034 | 5475 GOULBURN VALLEY FREEWAY, MOORILIM, VIC, 3610 | 31027823 | MNA034 | 12.7kV AC (SWER) | Rural Long | - fuse (EDO fuse) | single wire earth return (SWER) | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0010508 | 20200515PWA_01 | Customer called can see fuse down hanging down on substation. On arrival crew found fuse had candled and burnt in half. There was no ground fire, no reported injuries or third party property damage.
156 | PowerCor 19/65 | PowerCor | 2019-05-11 | 0.87778 | -37.2972 | 144.4411 | 455 CENTRAL ROAD, KYNETON SOUTH VIC 3444 | 33029664 | WND024 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | within electric line construction area | 19.8 | Low-moderate | 0.2 | 3.96 | INC-0010510 | 20200515PWA_02 | Customer reports fuse arcing and sparking, sparks nor reaching the ground. On arrival crew found burnt hung up edo fuse. There was no ground fire, no reported injuries.
157 | PowerCor 19/66 | PowerCor | 2019-08-11 | 0.94653 | -38.4111 | 144.1832 | 31 MURRAY STREET, ANGLESEA VIC 3230 | 32072743 | WPD021 | 22kV AC | Rural Short | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0010513 | 20200515PWA_04 | Calls received of supply failure at incident location. On arrival crew found EDO fuse burnt. There was no ground fire, no reported injuries or third party property damage.
158 | PowerCor 19/67 | PowerCor | 2019-11-11 | 0.58333 | -36.3527 | 145.4333 | 130 Grahamvale Rd Grahamvale 3631 | 33096475 | SHN024 | 22kV AC | Rural Short | - fuse (boric acid) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0008675 | 20191113PWA_03 | A customer reported a loud bang and ground fire at the incident location. Upon arrival, a Powercor fault crew found that a bird flash over resulted in a small ground fire.
159 | PowerCor 19/68 | PowerCor | 2019-12-11 | 0.30347 | -36.3715 | 141.8602 | 5651 WESTERN HIGHWAY, GERANG GERUNG VIC 3418 (near Angle Road) Gerang Gerung 3418 | 30546090 | NHL015 | 22kV AC | Rural Long | - automatic circuit recloser (ACR) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0008674 | 20191113PWA_02 | Emergency services reported a crow on transformer causing sparks and small grass fire. Crew removed bird off ACR P205 Gerang.
160 | PowerCor 19/69 | PowerCor | 13/11/2019 | 0.85625 | -34.1699 | 142.0421 | 30 YELTA RD MERBEIN (ACROSS THE ROAD). | 33066091 | MBN031 | 22kV AC | Rural Short | - fuse (boric acid) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0008684 | 20191115PWA_01 | CFA reported a grassfire . Upon crew arrival found an extinguished grassfire near the base of the pole. A magpie had caused a flash over on HV fuse.
161 | PowerCor 19/70 | PowerCor | 13/11/2019 | 0.33194 | -38.4967 | 143.2404 | 276 TOMAHAWK CREEK ROAD, SIMPSON VIC 3266 | 33035709 | CDN001 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0010516 | 20200515PWA_05 | Person advised fuse box half way up pole has caught on fire, fuse box may need replacing, pole is near the dairy, cust and dairy, access ok. On arrival crew found leads fuse box had burn damaging leads. There was no ground fire, no reported injuries or third party property damage.
162 | PowerCor 19/71 | PowerCor | 21/11/2019 | 0.55903 | -36.2636 | 143.4952 | 379 Barrakee-Buckrabanyule Rd, Buckrabanyule VIC 3525 | 32027791 | CTN001 | Low voltage AC (<1kV) | Rural Long | - dropper / bridge | single wire earth return (SWER) | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Code Red | 5 | 23 | INC-0008745 | 20191122PWA_01 | A crew attended a fault on a SWER ACR BORUNG P81, no cause for the outage was located. The crew departed to site , but a short time later a grass fire was observed emanating from near the incident location. CFA extinguished fire, police attended. There was a ground fire of around 16.5 hectares. There was no injuries and potentially fencing and pasture burnt (unconfirmed).
163 | PowerCor 19/72 | PowerCor | 21/11/2019 | 0.49792 | -37.6923 | 143.0087 | 525 Glenelg Hwy, Streatham, 3351 | 30083878 | ART033 | 22kV AC | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very high | 1 | 4.6 | INC-0008747 | 20191122PWA_02 | Vic fire reported wires down causing grass fire. On arrival crew found a broken strand of HV conductor had been intermittently brushing across phases. The sparks from this started a grass fire, observed and extinguished by CFA personnel. There was a small fire, no reported injuries or third party property damage.
164 | PowerCor 19/73 | PowerCor | 21/11/2019 | 0.60417 | -37.4066 | 143.8938 | 8 Geddes Rd, Creswick VIC 3363, Australia | 33007412 | BAN009 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very high | 1 | 4.6 | INC-0008749 | 20191122PWA_03 | Crew reports that a branch has broken of a gum tree and contacted the overhead line between P1 and P2 Flem spur line. The branch caught fire and started a ground fire when it came to rest on the ground under the 22kV overhead line. There was a small ground fire, no reported injuries or third party property damage.
165 | PowerCor 19/74 | PowerCor | 21/11/2019 | 0.65556 | -37.8765 | 144.6952 | 18 Mossfiel drive. Hoppers crossing 3029 | 32169859 | WBE013 | Low voltage AC (<1kV) | Urban | - dropper / bridge | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0008758 | 20191125PWA_02 | A Customer reported a Small Fire at base of Pole LIS-971870. CFA attended, Fire extinguished. Supply Off. On arrival the crew found that the LV conductor line bridges had burnt at a substation LV bus fuse termination mounted on pole (LIS-208939). There was a small area of burnt grass at the base of the pole (LIS-208939) caused by fallen hot debris. There was no reported injuries nor third party property damage.
166 | PowerCor 19/75 | PowerCor | 21/11/2019 | 0.60764 | -37.874 | 144.7894 | 293 QUEEN STREET,ALTONA MEADOWS,VIC,3028 | 30118601 | LVN022 | Low voltage AC (<1kV) | Urban | - overhead conductor (bare; steel) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0008760 | 20191125PWA_04 | City West Water, reported pole to pole wire is broken, wire down, crossing over driveway and road. Fire is out and police is on site. On arrival the crew found that the LV O/H service conductor between poles LIS-214017 and LIS-214018 was broken and lying on the ground over the driveway and on the grass. There was a small area of burnt grass. There was no reported injuries nor third party property damage.
167 | PowerCor 19/76 | PowerCor | 25/11/2019 | 0.79583 | -36.7862 | 144.2909 | 11 ELIZABETH STREET -SPRING GULLY | 32054109 | BET007 | Low voltage AC (<1kV) | Rural Short | - overhead service conductor (residential) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | INC-0008768 | 20191126PWA_01 | Report received from customer of service wire on ground and small patch of burnt grass in front yard. Service is still attached at pole end and draped across roadway. There was no injuries or third party property damage.
168 | PowerCor 19/77 | PowerCor | 25/11/2019 | 0.74444 | -36.4302 | 145.1138 | 515 Springvale Rd, Girgarre East VIC 3616, Australia | 33097486 | SHP014 | 22kV AC | Rural Long | - automatic circuit recloser (ACR) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | INC-0008769 | 20191126PWA_02 | Vicfire called in event at the incident location advising that there had been a fire possibly causing damage to a PCA asset. On arrival the crew found a small branch entangled in the ACR structure. The ACR had tripped, but the branch was on the supply side and still buzzing There was a small fire started. There was no injuries and minor damage to fence posts.
169 | PowerCor 19/78 | PowerCor | 25/11/2019 | 0.7 | -36.6477 | 141.2623 | 75 Barry Bulls Road, Minimay | 30086961 | HSM004 | 12.7kV AC (SWER) | Rural Long | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0008779 | 20191127PWA_01 | Vic Fire reported that powerlines that started a grass fire at the incident location. On arrival the fault crew found that approx. 40cm had burned off the top of a SWER pole, allowing the conductor to drop into the scrub in the span below, igniting a fire in that scrub. The burned area was contained within the scrubland reserve on the southern fringe of the Little Desert National Park, and was estimated by CFA to be in the order of 1.6 hectares. There was no injuries.
170 | PowerCor 19/79 | PowerCor | 26/11/2019 | 0.32569 | -36.428 | 145.1137 | Springvale Rd, Cooma VIC 3616, Australia ( cnr midland hwy and springvale rd) | 30566780 | SHP014 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0010519 | 20200515PWA_06 | Customer advised Pole on Fire corner of Midland Highway and Springvale rd, Shepparton. Wires across the road. Emergency services have been called. On arrival crew found the top had been burnt off the pole. There was no ground fire, no reported injuries or third party property damage.
171 | PowerCor 19/80 | PowerCor | 30/11/2019 | 0.36597 | -35.9054 | 144.3014 | 28 King Albert Ave, Leitchville VIC 3567 | 30029109 | CHA005 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0008890 | 20191202PWA_02 | Customer called reporting pole caught fire and smoldering. When crew arrived, they found that cross arm had burnt and outer phase (red phase) had dropped onto the LV cross arm. Crew called an LEI who attended and advised a HVI had occurred. No ground fire, no injuries that we have been made aware of.
172 | PowerCor 19/81 | PowerCor | 30/11/2019 | 0.14514 | -34.2728 | 142.199 | 151 Campbell Ave Irymple (Cnr Twenty Second St) | 32151419 | RCT021 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0008891 | 20191202PWA_03 | CFA called to advise pole fire and wire down at the incident location. Crew arrived and found HV cross arm was burning and part of cross arm had burnt out, dropping HV insulator and line to the ground. CFA and Police in attendance. Cable was still sparking due to backfeed. There was a small ground fire (1 mtr), no reported injuries or third party property damage.
173 | PowerCor 19/82 | PowerCor | 30/11/2019 | 0.50694 | -36.3475 | 145.4117 | 5 Shorthorn Ct (Ford Rd), Shepparton VIC 3630 | 33095210 | SHTSHN1 | 66kV AC | Unknown | - insulators | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0008893 | 20191202PWA_04 | CFA reported pole fire that caused grass fire at the incident location. When crew arrived they found an area of burnt grass approx. 4m x 18m in road reserve. Crew inspected pole and found evidence of a flash over from burn marks on east side of HV insulator but couldn't find any evidence of what had caused it or when. There was no protection operations in the area.
174 | PowerCor 19/83 | PowerCor | 30/11/2019 | 0.41389 | -35.2834 | 143.5654 | 68 Woodgate Rd, Murraydale VIC 3586 | 32157209 | SHL004 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0008901 | 20191203PWA_03 | Customer reported pole outside property was burnt at top of pole and wires were low. On arrival crew found broken cross-arm that had snapped in two and burn damage around the king bolt. CFA on site. No ground fire, no injuries no third party damage.
175 | PowerCor 19/84 | PowerCor | 30/11/2019 | 0.37014 | -34.2909 | 142.1792 | 62 Moonah St, Red Cliffs VIC 3496 | 32153101 | RCT023 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0008907 | 20191204PWA_01 | CFA reported pole fire at above address. When crew arrived, they found a cross arm that had burnt and conductors that had fallen onto LV. Closer inspection showed damage to LV and HV insulators. LEI could find no evidence of property damage. There was no ground fire, no injuries or property damage.
176 | PowerCor 19/85 | PowerCor | 30/11/2019 | 0.74236 | -35.3191 | 141.3634 | 410 Perkins Rd, Cowangie VIC 3506 | 32150598 | OYN001 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very high | 1 | 1 | INC-0008908 | 20191204PWA_02 | Report from LSA Barry Gregg of pole fire at above address. Crew arrived and found pole that appeared to have been burning all day. There was a lot of burnt debris from the pole but no ground fire had occurred and commented that site was very sandy. No third party damage or injuries.
177 | PowerCor 19/86 | PowerCor | 30/11/2019 | 0.125 | -35.3845 | 142.1877 | 88 CUMMINGS ROAD, PATCHEWOLLOCK VIC 3491 | 32151395 | OYN005 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very high | 1 | 1 | INC-0010521 | 20200515PWA_07 | Report Received of cross-arm fire at incident location. On arrival crew found strain cross-arm had been burnt.
178 | PowerCor 19/87 | PowerCor | 2019-01-12 | 0.49583 | -35.2252 | 143.4541 | North South Rd, Beverford VIC 3590 | 32160282 | SHL004 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0008898 | 20191203PWA_01 | CFA reported lines down with small fire. When crew arrived they found that the HV cross arm had burnt on one side and the conductor had dropped but was still in the air. No injuries or third party damage. No ground fire.
179 | PowerCor 19/88 | PowerCor | 2019-01-12 | 0.49514 | -35.2483 | 143.524 | 195 Tyntynder Central Rd, Tyntynder VIC 3586 | 32157266 | SHL004 | 22kV AC | Rural Short | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0008899 | 20191203PWA_02 | CFA called advising pole fire at above address. When crew arrived, they found that the top of the pole had burnt and cross arm had broken. Conductors were still on cross arm which was hanging on top of pole. No injuries, no ground fire, no third party damage.
180 | PowerCor 19/89 | PowerCor | 2019-01-12 | 0.53958 | -35.1811 | 142.9225 | Chinkapook-Mittyack rd Chinapook vic 3546 | 30304554 | OYN003 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0010509 | 20200515PWA_09 | Crew reports burnt wooden HV crossarm on pole 238 - small ground fire
181 | PowerCor 19/90 | PowerCor | 2019-01-12 | 0.75417 | -35.2818 | 143.4548 | 507 LAKE ROAD, WOORINEN VIC 3589 | 50033988 | SHL004 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0010529 | 20200515PWA_08 | Pole fire at incident location
182 | PowerCor 19/91 | PowerCor | 2019-02-12 | 0.59792 | -34.3807 | 141.6552 | 4 Millewa Road, Werrimull Vic 3496 | 30567057 | RCT023 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very high | 1 | 1 | INC-0010532 | 20200515PWA_10 | Powercor received a report of a Pole fire at LIS 215, Just off Millewa Rd.
183 | PowerCor 19/92 | PowerCor | 2019-03-12 | 0.20833 | -38.2725 | 143.1516 | 259 Count Boundary Rd East, Camperdown | 30149131 | CDN002 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0008967 | 20191209PWA_02 | Pole fire reported by Vicfire at incident location. Crew confirmed pole fire. Burn marks around crossarm straps only. There was no ground fire, no reported injuries or third party property damage.
184 | PowerCor 19/93 | PowerCor | 2019-04-12 | 0.60278 | -35.9416 | 144.3771 | Cnr of Hipwell Rd and Gunbower Island Rd Gunbower | 33018378 | CHA005 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0008952 | 20191206PWA_01 | CFA reported a fire under a pole last night at the incident location and CFA extinguished the fire. Crew replaced HV fuse and believed small grass fire was from some time ago (no CFA on site). On 5/12 following CFA advise crew re attended site and confirmed the fire area of 5*60m Sqm. The crew also did not find the cause of fire or the fuse operation.
185 | PowerCor 19/94 | PowerCor | 2019-06-12 | 0.80625 | -37.7456 | 144.6055 | 11 Strathtulloh Circuit, Strathtulloh 3338 | 33105868 | MLN011 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0008966 | 20191209PWA_01 | Report received of grass fire at incident location. On arrival crew found that a FOLCB had overheated and resultant sparks caused a small grass fire (5 x 30m). There was no injuries or third party property damage.
186 | PowerCor 19/95 | PowerCor | 2019-07-12 | 0.58264 | -35.9809 | 141.842 | 1981 Rainbow-Nhill Rd, Rainbow 3424 | 32120528 | NHL015 | 12.7kV AC (SWER) | Rural Long | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0008970 | 20191209PWA_04 | A call was received from the CFA stating that a wire had come down at the above address and had caused a fire. Powercor crew arrived onsite they found that the HV SWER conductor between Pole 33 and 34 Lake Hindmarsh had broken mid span and caused a grass fire. At the point that the conductor broke, a extremely large cactus was growing and it appears that the cactus had made contact with the HV conductor causing the fire and conductor failure. The fire burnt approx. 15 acres of grass, bush and cactus plantation. CFA attended and extinguished the fire. THere was no reported injuries.
187 | PowerCor 19/96 | PowerCor | 2019-08-12 | 0.053472 | -37.6272 | 144.5176 | 431 DIGGERS REST-COIMADAI ROAD, COIMADAI VIC 3340 | 32168128 | MLN022 | 22kV AC | Rural Short | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0010535 | 20200515PWA_11 | Crew attending a fault found that the end had burnt off edo fuse tube. No ground fire.
188 | PowerCor 19/97 | PowerCor | 2019-09-12 | 0.35833 | -35.8997 | 144.2864 | Leitchville-Kerang Rd, Leitchville VIC 3567, Australia | 33021956 | CHA005 | 22kV AC | Rural Long | - insulators | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Extreme | 3.5 | 0.7 | INC-0008968 | 20191209PWA_03 | CFA reported a ground fire at the incident location. On arrival, a Powercor crew found a 200 Sqm ground fire. They also observed a bird flashover on the pole top but no damage to pole top assets. There was no reported injuries or third party property damage.
189 | PowerCor 19/98 | PowerCor | 2019-09-12 | 0.026389 | -37.0721 | 144.207 | Corner Johnstone Street and Elizabeth Street Castlemaine 3450 | 32045518 | BETS-CMN | 66kV AC | Unknown | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0009023 | 20191212PWA_01 | Vic fire reported explosion and fire and incident location. On arrival crew found that a bat had caused a flashover on 66kv conductor resulting in 66kv conductors coming in contact with 22kv circuit below. There was a small grass fire (30m x 30m) , no reported injuries or third party property damage.
190 | PowerCor 19/99 | PowerCor | 2019-09-12 | 0.56597 | -36.3509 | 144.713 | 25 SULLIVAN ROAD, ROCHESTER VIC 3561 | 33083749 | KYM001 | Low voltage AC (<1kV) | Rural Long | - overhead service conductor (residential) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | INC-0010536 | 20200515PWA_12 | Branch fell breaking service line and causing a small fire.
191 | PowerCor 19/100 | PowerCor | 2019-10-12 | 0.46736 | -37.346 | 144.7028 | 1686 Romsey Road Romsey 3434 | 32042999 | WND012 | 22kV AC | Rural Long | - earth / earthing | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0009030 | 20191212PWA_03 | During a fault patrol a crew found a small ground fire (2 x 2 mtrs) at the incident location. The fault and fire was caused by a dislodged earth wire contacting an EDO fuse unit. There was no injuries or third party property damage. Fire was extinguished by fault crew.
192 | PowerCor 19/101 | PowerCor | 2019-11-12 | 0.71181 | -37.0675 | 142.7941 | Cnr Centenary Crt and Jubilee Rd, Stawell (opposite 12 Jubilee Rd, Stawell) | 33053400 | STL007 | 22kV AC | Rural Long | - transformer (pole mounted) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0009028 | 20191212PWA_02 | VicFire reported a fire at the incident location. On arrival the crew found that a bird had caused a flashover on a substation pole. The resultant fault current caused the feeder CB to reclose and the bird to fall to the ground, resulting in a ground fire (approx. 8m x 2m) on road reserve and a 2m section of a customer front yard at 12 Centenary Crt. There were no reported injuries or third party damage.
193 | PowerCor 19/102 | PowerCor | 18/12/2019 | 0.49444 | -37.5341 | 143.8854 | 15 KIEWA STREET, NERRINA VIC 3350 | 30003432 | BAN011 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very high | 1 | 4.6 | INC-0010537 | 20200518PWA_01 | Inspector reports burnt HV crossarm near HV fuse mount at incident location. No ground fire.
194 | PowerCor 19/103 | PowerCor | 19/12/2019 | 0.73403 | -35.4364 | 143.6211 | O/S SHAE STUD, 189 Lake Baker Rd, Lake Boga VIC 3584, Australia | 32159504 | SHL005 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0009219 | 20191224PWA_01 | Vicfire reported grassfire involving Powercor assets. Upon arrival crew found that a small grassfire had occurred approximately 50m X 15m in area which had been extinguished by the CFA. The LV fuse box on the cross-arm had burnt out as was the LV cross-arm on the sub pole. There was also minor damage to the pole. There was no reported injuries.
195 | PowerCor 19/104 | PowerCor | 20/12/2019 | 0.67569 | -37.7741 | 143.0617 | 565 Trawalla East Rd, Nerrin Nerrin 3351 | 32057787 | CDN006 | 12.7kV AC (SWER) | Rural Long | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Extreme | 3.5 | 16.1 | INC-0009208 | 20191223PWA_01 | SWER ACR Trawalla P10A tripped to Lock out at 16:13hrs. Shortly afterwards a report of a "fire in the area - pole fire" was recieved. Crews patrolled the line and found an extinguished paddock fire at the incident address together with 3 bays of SWER conductor down on the ground. Evidence of a tree branch on the ground near Trawalla P22. On arrival crew found the fire had been extinguished by persons unknown. There was no reported injuries.
196 | PowerCor 19/105 | PowerCor | 20/12/2019 | 0.90069 | -36.8172 | 144.3434 | 20 Red Tank Road Strathfieldsaye 3551 | 33034128 | BGO013 | 22kV AC | Rural Short | - automatic circuit recloser (ACR) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Severe | 2 | 9.2 | INC-0009209 | 20191223PWA_02 | CFA reported a ground fire has burnt pole, check for damage. Crew found a Magpie had caused a flash over, starting a 20m x 10m grass fire. There was no reported injuries , no property damage.
197 | PowerCor 19/106 | PowerCor | 20/12/2019 | 0.56667 | -38.3814 | 142.2281 | 31 Villiers St, Port Fairy 3284 | 31028939 | KRT022 | Low voltage AC (<1kV) | Rural Short | - overhead service conductor (residential) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Extreme | 3.5 | 0.7 | INC-0009210 | 20191223PWA_03 | Vic Fire reported wire down and sparking at incident address. When crews arrived they found a neutral screen Service wire had failed due to contact with a cust resp tree. A small ground (lawn) fire 2m x 2m in size had started on the front lawn area and was extinguished by Vic Fire. No injuries or property damage reported.
198 | PowerCor 19/107 | PowerCor | 20/12/2019 | 0.65833 | -36.9894 | 144.0647 | 84 HIGH STREET MALDON 3463 | 32050537 | CMN004 | Low voltage AC (<1kV) | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | INC-0009211 | 20191223PWA_04 | Customer reported broken branch laying across mains wires at incident location, not reachable from ground, smallish branch. Crew found tree branch caused conductors to clash starting small 300mm x 300mm ground fire. There was no reported injuries or third party property damage.
199 | PowerCor 19/108 | PowerCor | 20/12/2019 | 0.85972 | -38.1818 | 144.4379 | 105 Whitehorse Rd, Moolap 3224 | 30064947 | GLE024 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | Severe | 2 | 2 | INC-0009212 | 20191223PWA_05 | Fire brigade reported pole fire and grass fire and incident address. When crews arrived confirmed a LV UG service cable on Transformer pole had failed at the connection box. There was a small 4 square spot fire at the base of the pole. There was no reported injuries or property damage.
200 | PowerCor 19/109 | PowerCor | 20/12/2019 | 0.84097 | -38.1551 | 144.3111 | 230 Scenic Rd, Highton 3216 | 32086978 | GL021 | Low voltage AC (<1kV) | Urban | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | INC-0009213 | 20191223PWA_06 | Fire Brigade reported pole fire at incident address. When crews arrived they found a small grass fire 4m2, had started due to a loose connection on a LV fused bus isol. No injury or property damage was reported.
201 | PowerCor 19/110 | PowerCor | 20/12/2019 | 0.60278 | -37.8753 | 144.7953 | QUEEN STREET, ALTONA VIC 3018 | 32178028 | LVN022 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | INC-0010538 | 20200518PWA_03 | Report of pole fire at incident location. No ground fire.
202 | PowerCor 19/111 | PowerCor | 20/12/2019 | 0.64375 | -37.5776 | 143.8396 | 804 TALBOT STREET S, REDAN VIC 3350 | 31001148 | BAS012 | Low voltage AC (<1kV) | Urban | - overhead service conductor (residential) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | INC-0010539 | 20200518PWA_02 | Service on the ground neutral screen service had burnt to the ground leaving some burns on some customer grass.
203 | PowerCor 19/112 | PowerCor | 21/12/2019 | 0.077083 | -37.0697 | 142.7925 | Lot 2 39 London Rd Stawell 3380 | 32095103 | STL007 | 22kV AC | Rural Long | - insulators | three phase | Started by lightning striking a distribution system or a part of a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very high | 1 | 4.6 | INC-0009216 | 20191223PWA_09 | Lightning has Struck the pole at incident location. There was damage to two Disc Insulators, there was a ground fire approx. 2 x 4m. There was no injuries reported or third party property damage.
204 | PowerCor 19/113 | PowerCor | 22/12/2019 | 0.95694 | -35.4719 | 143.826 | Murrabit W Rd, Benjeroop VIC 3579, Australia | 30255066 | KGT003 | 22kV AC | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0009220 | 20191224PWA_02 | Vicfire called to advise that PCA assets could have been the possible cause of a grassfire. On arrival crew found a conductor had fallen and was on the ground at the incident location. CfA extinquished a small grass fire (100m x 5m) on roadside. There was no reported injuries.
205 | PowerCor 19/114 | PowerCor | 22/12/2019 | 0.52569 | -38.1439 | 142.9853 | 120 CRUICKSHANKS ROAD, GLENORMISTON NORTH VIC 3265 | 30042218 | TRG001 | 22kV AC | Rural Short | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0010540 | 20200518PWA_07 | Crew attending outage found burnt off edo fuse at incident location.
206 | PowerCor 19/115 | PowerCor | 23/12/2019 | 0.30903 | -38.0115 | 143.9728 | 19 Tolson st, Shelford vic 3329 | 31034200 | GL012 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0010549 | 20200518PWA_08 | Crew attending outage found burnt off edo fuse at incident location.
207 | PowerCor 19/116 | PowerCor | 24/12/2019 | 0.54444 | -37.444 | 143.9805 | Ballarat-Daylesford Rd, Newlyn VIC 3364, Australia | 33005282 | BAN008 | Low voltage AC (<1kV) | Rural Long | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0009223 | 20191230PWA_01 | Vic fire reported a ground fire at the incident location. Upon arrival, a Powercor crew found an overheated isolator connection had burnt out dropping molten particles on the the grass below. This resulted in a 120 sq section of roadside being burnt. There was no reported injuries or third party property damage.
208 | PowerCor 19/117 | PowerCor | 24/12/2019 | 0.68194 | -37.7197 | 141.9629 | 204 Balkins Rd, Hamilton VIC 3300, Australia | 30090118 | HTN006 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0009224 | 20191230PWA_02 | Customer reported burnt out mains box. When crews arrived they found a failed FOLCB on Substation pole. There was small spots of burning amongst the long grass at the base of the pole. There was no reported injuries or third party property damage.
209 | PowerCor 19/118 | PowerCor | 25/12/2019 | 0.99583 | -38.1867 | 143.1862 | 460 Chocolyn Rd, Camperdown 3260 | 30047237 | CDN004 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0009226 | 20191230PWA_04 | Vic Fire reported a pole fire at the incident address. When crews arrived they found a FOLCB on substation pole had failed resulting in a equip fire and small (9x2m) grd fire. CFA crews extinguished the fire. No injuries or property damage was reported.
210 | PowerCor 19/119 | PowerCor | 25/12/2019 | 0.61875 | -36.7225 | 144.2654 | 23 Bright St, California Gully VIC 3556, Australia | 32032597 | EHK023 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0009228 | 20191230PWA_06 | Vic fire reported an umbrella has blown onto HV line and wire down which started small grass fire. Crew found that an outdoor table umbrella had been caught by a gust of wind and had been thrown into the HV. The centre phase of the three phase line has as a result burnt to the ground and started a grassfire in road reserve and creek reserve. There were no reported electrical injuries (Ambulance onsite were treating a resident for smoke inhalation.)
211 | PowerCor 19/120 | PowerCor | 27/12/2019 | 0.22569 | -38.3159 | 144.0311 | 155 WORMBETE STATION ROAD, WURDIBOLUC VIC 3241 | 33040998 | WIN022 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | within electric line construction area | 19.8 | High | 0.5 | 9.9 | INC-0010552 | 20200518PWA_09 | Following supply failure crew found an edo fuse had hung up and burnt in half.
212 | PowerCor 19/121 | PowerCor | 28/12/2019 | 0.79167 | -38.4604 | 144.1054 | 12 Beach Rd, Aireys Inlet, 3231 | 31039147 | WPD014 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009229 | 20191230PWA_07 | Customer reported service down the side of pole on fire. On arrival the crew found a single phase fuse box had burnt and caused a small fire that was quickly extinguished by locals and CFA who were on site. There was no reported injuries or third party property damage.
213 | PowerCor 19/122 | PowerCor | 29/12/2019 | 0.77083 | -37.0648 | 142.7932 | 20 Oregan Street Stawell | 31016235 | STL005 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very high | 1 | 4.6 | INC-0009230 | 20191230PWA_08 | Vic Fire reported a wire down and small fire at the incident location. On arrival the fault crew found that a branch had broken from a tree standing on the opposite side of the road from this property and had fallen onto the overhead distribution wires, bringing 3 bays of HV & LV conductors to the ground, and causing the small fire in the front yard of this residence. The fault crew also found evidence of High Voltage Injection damage to the electrical wiring and the switchboard at this residence. There was no reported injuries.
214 | PowerCor 19/123 | PowerCor | 29/12/2019 | 0.74514 | -35.0254 | 142.7935 | Intersection of O'Toole Road and Sleep Road, Manangatang | 32140525 | OYN003 | 12.7kV AC (SWER) | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | single wire earth return (SWER) | Started by lightning striking a distribution system or a part of a distribution system | HBRA only | 1 | Severe | 2 | 2 | INC-0009231 | 20191230PWA_09 | Lightning Strike Pole # 6 & Pole #5 Winnambool Spur OYN003 30-40 Hectares burnt. Fault tamer fuse destroyed, fire ignited at pole 6. There was no reported injuries.
215 | PowerCor 19/124 | PowerCor | 30/12/2019 | 0.45833 | -38.3859 | 142.6078 | 14 Grauers Rd, Allansford VIC 3277. | 32198150 | WBL002 | 22kV AC | Rural Short | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Extreme | 3.5 | 0.7 | INC-0009232 | 20191231PWA_01 | Vicfire reported branch landed on conductors causing sparking and grass fire. On arrival crew reported small grass fire under line (1m*1m) started by customer's tree branch contacting 22kV overhead conductors outside the incident address. Fire is out and branch has been pruned away form the line.
216 | PowerCor 19/125 | PowerCor | 30/12/2019 | 0.55208 | -37.8286 | 144.8078 | 38 Dohertys Road, Laverton North, 3026. (Substation Dohertys 34-Cherry SStn) | PA0121380 | LVN032 | 22kV AC | Urban | - dropper / bridge | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Extreme | 3.5 | 0.7 | INC-0009233 | 20191231PWA_02 | Vic fire requested attendance required at factory fire. Some tin roof has blown onto HV conductors and caused a grassfire. Crew advise that a tin roofing sheet has come loose in strong winds and has been blown of the warehouse at 38 Dohertys Road onto its substation known as Dohertys 34-Cherry. Resulting in substation fire and a large grass fire in a vacant paddock to its east. Grass fire approximately 50m*300m. Grass fire has been extinguished by the CFA & MFB who were on site. There were no reported injuries.
217 | PowerCor 19/126 | PowerCor | 30/12/2019 | 0.81319 | -37.5668 | 142.8977 | 1485 Delacombe Way, Mininera | 30084285 | ART033 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Extreme | 3.5 | 16.1 | INC-0009234 | 20191231PWA_03 | Vic Fire reported a wire had come down from a pole and had started a grass fire at the incident location. On arrival the fault crew found that a tree had fallen from the other side of the road (outside clearance space) and had fallen across the overhead distribution wires, breaking a HV crossarm, and causing a grass fire below. There was no reported injuries.
218 | PowerCor 19/127 | PowerCor | 30/12/2019 | 0.56597 | -38.4231 | 144.1769 | 2A SIXTH AVENUE,ANGLESEA,VIC,3230 | 33041664 | WPD021 | Low voltage AC (<1kV) | Rural Short | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Extreme | 3.5 | 0.7 | INC-0009235 | 20191231PWA_04 | Vicfire reported Transformer explosion - powerdown at this address. Crew attended to find ground fire under substation 5m*10m. The grass fire was extinguished by customer and CFA also attended. There was no reported injuries.
219 | PowerCor 19/128 | PowerCor | 30/12/2019 | 0.58333 | -37.6778 | 144.571 | 50 Quail Crescent, Melton,3337. | 30300618 | MLN032 | Low voltage AC (<1kV) | Rural Short | - connector / termination | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Extreme | 3.5 | 0.7 | INC-0009236 | 20191231PWA_05 | Following reports of outage crew found a burnt out copper to aluminium connection on north side transformer bus. Molten particles had caused a number of small spot fires in the grass below. There was no reported injuries or property damage.
220 | PowerCor 19/129 | PowerCor | 30/12/2019 | 0.95208 | -36.3162 | 141.3004 | 1004 Broughton Rd, Kaniva VIC 3419, Australia | 32100682 | NHL031 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Extreme | 3.5 | 3.5 | INC-0009237 | 20191231PWA_06 | Vic Fire reported a pole fire at the incident location. On arrival the fault crew found a HV crossarm had burned through at the kingbolt and had broken. There was no ground fire, no reported injuries or third party property damage.
221 | PowerCor 19/130 | PowerCor | 30/12/2019 | 0.96111 | -36.7335 | 142.2084 | 2 Apricot Street, Horsham 3400 | 32116250 | HOTS-HSM2 | 66kV AC | Unknown | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Extreme | 3.5 | 0.7 | INC-0009239 | 20191231PWA_09 | Vic Fire reported a pole fire at the incident location. On arrival the fault crew found that a HV crossarm had been burning at a bridging insulator, but the fire had been extinguished before the crossarm burned through. CFA attended and extinguished the crossarm fire. There was no ground fire.
222 | PowerCor 19/131 | PowerCor | 30/12/2019 | 0.86111 | -36.7395 | 141.0518 | 8576 Natimuk Frances Road, Neuarpurr 3413 | 32090113 | HSM004 | 22kV AC | Rural Long | - surge diverter | three phase | Started by lightning striking a distribution system or a part of a distribution system | HBRA only | 1 | Extreme | 3.5 | 3.5 | INC-0009243 | 20200102PWA_01 | Vic Fire reported a grass fire at the incident location. On arrival the fault crew found that a surge diverter connected to the substation pole at the incident location had flashed over causing a small grass fire at the base of the pole. There was no reported injuries or third party property damage.
223 | PowerCor 19/132 | PowerCor | 31/12/2019 | 0.20278 | -37.7954 | 144.8049 | 12 Corella Rd, Sunshine West VIC 3020 | 32166103 | SU035 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009247 | 20200102PWA_03 | Report received of Low conductors in Corella rd Sunshine West. Crew advise pole fire roadside phase strain cross-arm has burnt through. Roadside phase with insulators attached is hanging in midair. Possible high voltage injection, LEI on site Miles Tobias. No ground fire no person injured.
224 | PowerCor 19/133 | PowerCor | 31/12/2019 | 0.20139 | -37.723 | 144.8274 | 42 Greengully Road, Keilor, 3036. | 30114080 | SA002 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009248 | 20200102PWA_04 | Crew advise pole fire intermediate arm has burnt through at kingbolt. No ground fire or reported injury.
225 | PowerCor 19/134 | PowerCor | 31/12/2019 | 0.27847 | -37.7424 | 144.8092 | 36 Vincent Ave, St Albans, 3020. | 32163794 | SA007 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009249 | 20200102PWA_05 | Customer reports sparking and buzzing noise coming from pole in front of his home, believes it is coming from the conductors at the top of the pole. still on supply at site, sparks not reaching the ground. Crew advise pole fire. Cross-arm on roadside of pole has burnt through at strap bolt cross-arm is broken, insulator has shattered and fallen onto nature strip below. There was no ground fire, no reported injuries or third party property damage.
226 | PowerCor 19/135 | PowerCor | 31/12/2019 | 0.0069444 | -36.7043 | 142.2153 | 1 Pryors Road, Horsham 3400 | 30078377 | HSM009 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009250 | 20200102PWA_06 | Vic Fire reported a pole fire at the incident location. On arrival the fault crew found a HV crossarm had burned through, dropping the outside conductor. There was no ground fire.
227 | PowerCor 19/136 | PowerCor | 31/12/2019 | 0.27847 | -37.7241 | 144.8366 | 2 Skyline Dr, Keilor VIC 3036 | 30108788 | SA002 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009251 | 20200102PWA_07 | Vic fire reported crossarm on fire at incident location. Crew advise pole fire originating at pin of bridging insulator. Cross arm has lost integrity and insulators have broken away causing fault on feeder and ACR to trip. No ground fire and no reported injury.
228 | PowerCor 19/137 | PowerCor | 31/12/2019 | 0.29167 | -37.8198 | 144.8078 | 13 Raymond Road, Laverton North 3026. | 30115647 | LVN032 | 22kV AC | Urban | - pole (wood) | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009252 | 20200102PWA_08 | Customer reported lightning has struck the pole and its been smoking and there has been sparks coming out as well, also adv its burnt out black at some parts. Crew attended to find HV tee-off arm broken, conductors hanging with insulators attached. MFB attended to extinguish pole fire. Large chunks of the wooden cross-arm on the ground. No ground fire, no reported injuries.
229 | PowerCor 19/138 | PowerCor | 31/12/2019 | 0.22917 | -37.7644 | 144.8154 | 229 St Albans Rd, St Albans VIC 3021. | 30112999 | SSE011 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009254 | 20200102PWA_10 | Crew advise cross-arm burnt through on Red phase roadside HV isolator and fell into low voltage below, HV injection occurred. There was no ground fire or reported injuries.
230 | PowerCor 19/139 | PowerCor | 31/12/2019 | 0.3 | -37.7645 | 144.8397 | 68 Berkshire Road, Sunshine North VIC 3020 | 30102782 | SSE032 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009255 | 20200103PWA_01 | Report received of pole fire at incident location. Crew advised a HV tee off crossarm has broken due to a pole fire. The conductors have come to rest across parked trucks at the premises. There was no ground fire or reported injuries.
231 | PowerCor 19/140 | PowerCor | 31/12/2019 | 0.17847 | -37.8006 | 144.8109 | 69 Cawood Dr, Sunshine West VIC 3020 | 31023754 | SSE033 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009257 | 20200103PWA_03 | Crew reported pole fire at incident location. A high voltage isolator has broken off due to a crossarm fire and is now resting on the LV conductors below. There is reports of HVI. There was no ground fire or reported injuries.
232 | PowerCor 19/141 | PowerCor | 31/12/2019 | 0.46111 | -37.6102 | 144.5114 | 47 ANTIMONY MINE ROAD,COIMADAI,VIC,3340 | 30107875 | MLN022 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0009258 | 20200103PWA_04 | Crew reported a hv crossarm fire at the incident location. CFA on site to extinguish the fire. There was no ground fire, no reported injuries or third party property damage.
233 | PowerCor 19/142 | PowerCor | 31/12/2019 | 0.097222 | -36.7043 | 142.2153 | 3 Pryors Rd, Horsham VIC 3400 | 30078377 | HSM009 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009259 | 20200103PWA_05 | Report received of a pole fire at the incident location. Crew advise cross-arm burnt on LIS 433, Pryors Lane P1. LEI confirmed no high voltage injection. There was no ground fire, no reported injuries or third party property damage.
234 | PowerCor 19/143 | PowerCor | 2020-01-01 | 0.46736 | -37.7839 | 144.8139 | 94 Forrest Street, Ardeer, 3022 | 31034122 | SSE033 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009260 | 20200103PWA_06 | Customer reported HV lines on ground and has started a small fire at incident location. Crew attended site and found the incident was caused by balloons released by unknown persons coming in contact with the over head conductors. The resultant contact caused sparks to fall onto the nature strip and adjacent reserve causing a small grass fire (10x20mtrs). The incident cause the 22kv conductor to rupture and fall to ground. The fault current also caused the connections at Pole 19 lis 25672 ( in Forest st 600mts from original fault) to fail allowing the conductor to fall onto the roadway. There was suspected HVI. There was no reported injuries.
235 | PowerCor 19/144 | PowerCor | 2020-02-01 | 0.74514 | -36.3632 | 145.3261 | 130 CORNISH ROAD, ARDMONA, VIC, 3629 | 33092737 | MNA014 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0009269 | 20200107PWA_03 | CFA reported grass fire around our assets in road reserve. On arrival crew found a fire approx. 80m x 15m along road reserve. Crew identified possible bird flashover and a bridge burnt through. Crew found bird at base of pole. There was a small grass fire, no reported injuries, minor damage to a fence.
236 | PowerCor 19/145 | PowerCor | 2020-02-01 | 0.80139 | -35.3466 | 143.5472 | 80 GRAY STREET, SWAN HILL, VIC, 3585 | 33070600 | SHL007 | Low voltage AC (<1kV) | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009270 | 20200107PWA_04 | Vic Fire reported ground fire at base of pole at above address. When crew arrived, they found that a cable between pole transformer and isolator had melted. Molten material had ignited the grass below. There was no injuries or third party property damage.
237 | PowerCor 19/146 | PowerCor | 2020-02-01 | 0.87083 | -37.4294 | 144.5482 | 67 ELLANDEE CRESCENT, MACEDON, VIC, 3440 | 32050356 | GSB014 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0009271 | 20200107PWA_05 | Crew reported possible HVI from burnt cross-arm. Cross arm had burnt through on one side and HV conductor had landed on red phase of LV. There was no ground fire or reported injuries.
238 | PowerCor 19/147 | PowerCor | 2020-04-01 | 0.66944 | -36.6485 | 144.3195 | 1 OLD MURRAY RD HUNTLY | 32035322 | EHK031 | 12.7kV AC (SWER) | Rural Short | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Severe | 2 | 9.2 | INC-0009263 | 20200106PWA_01 | Call received from Vic Fire reporting wires down and requesting urgent isolation of power. Crew were escorted by CFA to area where a SWER wire was down between Wallenjoe Pole 2 and Wallenjoe Pole 3 and found a tree had fallen on a SWER line. Damage to rural fencing , no injuries reported.
239 | PowerCor 19/148 | PowerCor | 2020-04-01 | 0.76111 | -36.6953 | 144.3306 | 112 STRICKLAND STREET, ASCOT, VIC, 3551 | 33021191 | EHK033 | Low voltage AC (<1kV) | Urban | - overhead service conductor (other) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | INC-0009274 | 20200107PWA_07 | Customer reported tree branch had come down & brought down service wire and a grass fire had occurred nearby. On arrival, crew found that a grey twisted wire road crossing had a tree branch on it and had been pulled at the junction box on the substation pole that it was coming from. There a patch of grass ignited (3x3mtr) around 10 metres from the pole. There was no injuries, no third party property damage.
240 | PowerCor 19/149 | PowerCor | 2020-04-01 | 0.59167 | -38.3074 | 142.3482 | 14 O'Gradys Lane, Koriot | 33099459 | KRT013 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0009280 | 20200108PWA_05 | CFA reported a ground fire at the above location. Powercor crew attended and found the ground fire had been started by faulted FOLCB. There was no reported injuries.
241 | PowerCor 19/150 | PowerCor | 2020-05-01 | 0.7125 | -35.4448 | 143.7947 | 614 WEARNE ROAD, PENTAL ISLAND, VIC, 3586 | 30102272 | KGT003 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0009281 | 20200108PWA_06 | Customer reports broken cross-arm, low wire and grass fire at incident location. When crew arrived, they found that cross-arm had burnt at the road side HV insulator and the wire had dropped to approx. 1m height. Crew found that the fire had been extinguished by the person reporting the incident. There was no reported injuries.
242 | PowerCor 19/151 | PowerCor | 2020-05-01 | 0.67986 | -35.0751 | 142.3181 | 11 RAILWAY TERRACE, OUYEN, VIC, 3490 | 32150815 | OYN007 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009282 | 20200108PWA_07 | Report from Vic Fire that pole on fire at above address. When crew arrived they found that the cross arm had burnt through from the cross arm strap bolt. The outer phase of the HV had fallen onto the LV cross-arm. Crew confirmed no HVI had occurred. There was no ground fire, no injury, no third party damage.
243 | PowerCor 19/152 | PowerCor | 2020-05-01 | 0.74722 | -36.3306 | 145.1036 | 365 DUNBAR ROAD, LANCASTER, VIC, 3620 | 30130749 | SHTS-KYM1 | 66kV AC | Unknown | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009286 | 20200109PWA_01 | Passer by reported broken cross arm and low wires at incident location. On arrival crew found that the cross arm had burn marks on it and had broken at the cross arm strap bolt. 66kV conductor had fallen and was hanging low. No ground fire, no third party damage, no injuries.
244 | PowerCor 19/153 | PowerCor | 2020-05-01 | 0.32847 | -36.3628 | 144.7942 | 58 LETCHER ROAD, NANNEELLA, VIC, 3561 | 30120913 | KYM001 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009287 | 20200109PWA_02 | Reports from customer of cross arm on fire. Crew attended site and found that the wooden cross arm had burnt around the area of one of the EDO fuse arms and the fuse unit had fallen from the cross-arm. No ground fire at site. No injuries no third party damage.
245 | PowerCor 19/154 | PowerCor | 2020-05-01 | 0.65208 | -36.456 | 142.0508 | 66 Horsham Rd, Dimboola VIC 3414, Australia | 32121199 | HSM006 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0009288 | 20200109PWA_03 | Report received report of pole fire at incident location. On arrival crew found a pole top burnt off and crossarm burnt. There was a small grass fire of 10 sq m, no injuries.
246 | PowerCor 19/155 | PowerCor | 2020-05-01 | 0.52361 | -36.7349 | 141.1416 | 61 Hawkins Rd Minimay 3413 | 30139567 | HSM004 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0009289 | 20200109PWA_04 | Vic fire reported Pole fire and grass fire. On arrival crew found a SWER pole burnt in half and a grass fire. There was no reported injuries.
247 | PowerCor 19/156 | PowerCor | 2020-05-01 | 0.38125 | -37.5359 | 143.8193 | 25 Learmonth Rd Wendouree 3355 | 32014213 | BAN004 | 22kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0009290 | 20200109PWA_05 | Report received of pole on fire at incident location. On arrival crew found pole alight at king bolt position. There was no ground fire, no reported injuries or third party property damage.
248 | PowerCor 19/157 | PowerCor | 2020-05-01 | 0.76042 | -36.3029 | 144.6166 | 647 PRAIRIE-ROCHESTER RD BAMAWM | 30120470 | SHP012 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009292 | 20200109PWA_06 | Reports from customers of dim lights and broken cross arm with wire down. On arrival, crews found cross arm had burnt and broken at EDO holder and dropped to ground and a HV conductor was hanging over LV conductor. Crew identified possible HVI and inspector called to investigate. There was no ground fire, no reported injuries or third party property damage.
249 | PowerCor 19/158 | PowerCor | 2020-05-01 | 0.74514 | -35.4625 | 143.6324 | 2 Lalbert Rd, Lake Boga VIC 3584 | 30101817 | KGT004 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009293 | 20200109PWA_07 | CFA reported pole fire in Lalbert Rd near Station Street. When crew arrived they found that cross arm had burnt through at the cross arm strap. No ground fire confirmed by crew. No injuries or third party damage. CFA extinguished fire.
250 | PowerCor 19/159 | PowerCor | 2020-05-01 | 0.74097 | -36.0553 | 144.1144 | 20 VICTORIA STREET, PYRAMID HILL, VIC, 3575 | 30567286 | CHA006 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009294 | 20200109PWA_08 | Vic Fire reported pole fire and wire low at above address and crossing railway line. Concerned that train could hit line. On arrival crew found that cross-arm was burning from the King Bolt on both HV cross arms. No injury or third party damage. No ground fire.
251 | PowerCor 19/160 | PowerCor | 2020-05-01 | 0.68333 | -36.1815 | 144.0319 | 201 Yarrawalla S Rd, Yarrawalla VIC 3575 | 32032629 | CHA006 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0009296 | 20200110PWA_01 | Vic Fire reported ground fire started by our assets at incident location. When crew arrived, they found that the crossarm had burnt through at the roadside pin insulator and burnt grass underneath our assets in road reserve. There was no HVI. No injuries or third party damage.
252 | PowerCor 19/161 | PowerCor | 2020-05-01 | 0.4 | -36.3236 | 141.8772 | 575 Gerang-Glenlee Rd Gerang Gerung 3418 | 31015798 | NHL015 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0009297 | 20200110PWA_02 | Report received of pole and ground fire at incident location. On arrival crew found Buck x arm fire and grass fire. There was no reported injuries or third party property damage.
253 | PowerCor 19/162 | PowerCor | 2020-05-01 | 0.85417 | -36.4036 | 145.398 | 6 Murray St, Shepparton VIC 3630 | 32189142 | MNA024 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009298 | 20200110PWA_03 | Vic Fire reported cross-arm burning through. On arrival, crew found cross arm burning at fuse holder bolt on HV cross-arm. Assets were still secure to cross arm. No injuries, no ground fire, no third party damage.
254 | PowerCor 19/163 | PowerCor | 2020-05-01 | 0.96736 | -34.6369 | 142.7444 | 289 Happy Valley Rd, Robinvale Irrigation District Section C VIC 3549 | 32145857 | RVL001 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0009299 | 20200110PWA_04 | Report from Vic FIre of pole fire at 201 Shaggy Ridge Rd Robinvale. Crew attended and found cross arm had burnt and broke at the cross-arm strap bolt and the outer phase was being held up by the stays off the strain. No ground fire, no injury, no third party damage.
255 | PowerCor 19/164 | PowerCor | 2020-05-01 | 0.88958 | -35.1991 | 143.3826 | 50 DICKINSON ROAD, VINIFERA, VIC, 3591 | 32159107 | SHL002 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009300 | 20200110PWA_05 | Vic Fire reported pole fire at above address. On arrival, crew found cross arm hanging from top of pole and still alight. Burning appears to have occurred at Kingbolt. No HVI suspected. No ground fire, no injuries, no third party damage.
256 | PowerCor 19/165 | PowerCor | 2020-05-01 | 0.81597 | -34.2848 | 142.2101 | 63 Johns Rd, Red Cliffs VIC 3496, Australia | 32153003 | RCT023 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009301 | 20200110PWA_06 | Reported as all supply fail, crew attended and found pole fire with cross arm burnt through at fuse holder and conductor hanging beside pole below transformer. No ground fire. No injuries or third party damage. No reports of HVI.
257 | PowerCor 19/166 | PowerCor | 2020-05-01 | 0.73958 | -37.6616 | 143.8301 | 16 Sobeys Rd, Napoleons VIC 3352 | 32013707 | BAS022 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0009303 | 20200110PWA_07 | Report received of pole fire and broken crossarm. There was no ground fire, no reported injuries or third party property damage.
258 | PowerCor 19/167 | PowerCor | 2020-05-01 | 0.87153 | -34.7201 | 143.1731 | 8655 Murray Valley Highway, Boundary Bend, Vic. 3599 | 32148923 | BBD021 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0009304 | 20200110PWA_08 | Vic fire reported pole fire. Crew arrived to find one end of pole was burning. Crew isolated and CFA extinguished fire. No ground fire, no reported injuries or third party property damage.
259 | PowerCor 19/168 | PowerCor | 2020-05-01 | 0.30764 | -38.4376 | 143.8114 | 685 Division Road, Murroon | 30052618 | WIN011 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0009344 | 20200115PWA_04 | CFA reported a pole fire in Division Road, Murroon. Crew attended and confirmed a crossarm fire on pole 2 Murroon Spur, no ground fire.
260 | PowerCor 19/169 | PowerCor | 2020-06-01 | 0.18819 | -35.7862 | 144.0295 | 8224 Murray Vally Hwy Kerang East 3579 | 32032025 | KGT003 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0009305 | 20200110PWA_09 | A Powercor fault crew patrolling a faulted SWER line and found a pole fire at the incident location. The pole top ignited but no ground fire reported.
261 | PowerCor 19/170 | PowerCor | 2020-06-01 | 0.67153 | -34.208 | 142.0638 | 66 Oak Ave, Birdwoodton VIC 3505 | 30096077 | MBN014 | 22kV AC | Rural Short | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009306 | 20200110PWA_10 | Report from customer of Pole top/crossarm has caught fire and fallen to the ground. Fire is now out however wires/assets are still hanging off the pole. Crew arrived, they found that the cross arm had burnt from the king bolt. No ground fire, no injuries, no third party damage.
262 | PowerCor 19/171 | PowerCor | 2020-06-01 | 0.52153 | -34.6616 | 142.7595 | 156 Madang Rd, Robinvale Irrigation District Section E VIC 3549 | 30097348 | RVL001 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009307 | 20200110PWA_11 | Customer report of low wire at above address. Crew attended site and found that a cross arm had burnt through at the cross arm strap bolt and one of the conductors was hanging at approx. 5m. No ground fire at site. No injuries or third party damage.
263 | PowerCor 19/172 | PowerCor | 2020-06-01 | 0.68125 | -34.7946 | 142.5649 | 2862 Hattah-Robinvale Rd Liparoo Vic 3549 | 32140710 | WMN021 | 22kV AC | Rural Short | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0009308 | 20200110PWA_12 | ZSS trip to lockout at Wemen Zone Substation. Crew arrived and found a pole fire on 66/22kV pole where 22kV crossarm had burnt through at the king bolt and dropped the top of the pole with the 66kV down to ground. No ground fire, no injury, no third party damage.
264 | PowerCor 19/173 | PowerCor | 2020-06-01 | 0.875 | -34.4032 | 142.2811 | 129 Kulkyne Way Iraak 3494 | 30097098 | RCT014 | 22kV AC | Rural Short | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009310 | 20200110PWA_14 | A Powercor fault crew attending a fault found that a pole fire at the incident location. There was no ground fire or third party damage.
265 | PowerCor 19/174 | PowerCor | 2020-06-01 | 0.47431 | -36.2258 | 143.8518 | 793 MYSIA EAST ROAD,MYSIA,VIC,3518 | 31002708 | CTN002 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0010031 | 20200228PWA_02 | Customer reported wires low enough to touch. On arrival crew found a crossarm had burnt in half. There was no ground fire, no reported injuries or third party property damage.
266 | PowerCor 19/175 | PowerCor | 2020-09-01 | 0.6375 | -37.5301 | 143.888 | 60 Alkera Rd Invermay 3352 | 30003992 | BAN007 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0009316 | 20200113PWA_01 | Vic Fire reported a ground fire at the incident location. A Powercor crew found that FOLCB on the pole (LIS 45326) overheated and fallen debris caused 6*30 grass fire. The fire damage to a customer's fence. There was no reported injuries.
267 | PowerCor 19/176 | PowerCor | 2020-09-01 | 0.69792 | -38.4685 | 143.3075 | 856 Coradjil Rd, Simpson VIC 3266 | 31032683 | CDN001 | 22kV AC | Rural Long | - surge diverter | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very high | 1 | 4.6 | INC-0009317 | 20200113PWA_02 | Crew were sectionalizing line to locate a feeder fault on CDN001. When restoring line, a lighting arrester failed on LIS-964946 "HEYJILL 2" S/S. The debris fell to the ground causing fire approximately 20m x 20m. The CFA and farmer assisted containing the fire. No damage to customer's property or assets identified. Fire burnt underneath wooden fence and around water tank. There was no reported injuries
268 | PowerCor 19/177 | PowerCor | 2020-09-01 | 0.79653 | -36.7513 | 144.2732 | 3 Milroy Street, Bendigo VIC 3550 | 32037243 | BET002 | Low voltage AC (<1kV) | Urban | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009319 | 20200113PWA_03 | Customer at incident address reported sparks dropping from pole and starting ground fire at base of pole. Upon arrival fault crew found that white phase LV isolator at substation "Milroy Valentine 8" had failed and dropped molten material to ground, commencing small fire at base of pole. There was no reported injuries or third party property damage.
269 | PowerCor 19/178 | PowerCor | 2020-09-01 | 0.86806 | -36.8426 | 143.8797 | 3460 Bendigo -Maryborough Road, Laancoorie VIC 3463 | 30019863 | MRO007 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0009320 | 20200113PWA_04 | CFA reported pole fire at incident address, Upon arrival crew found that ISO pole "Waanyarra P4" was burning internally. Crew isolated for CFA to extinguish internal burning. No ground fire, no injuries or 3rd party damage.
270 | PowerCor 19/179 | PowerCor | 2020-10-01 | 0.84861 | -36.5207 | 145.0138 | 1050 Middle Rd, Rushworth VIC 3612, Australia | 30127001 | SHP014 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Severe | 2 | 2 | INC-0009321 | 20200113PWA_05 | Rushworth P119 ACR tripped to lockout. Upon arrival fault crew found that P184 Rushworth had burnt through between HV x-arm kingbolt & stay eyebolt, the pole top assembly dislodged from pole and landed on roadway. No ground fire or 3rd party damage.
271 | PowerCor 19/180 | PowerCor | 2020-10-01 | 0.87431 | -36.3622 | 145.4117 | 6 Fitzgerald Street, Shepparton VIC 3630 | 30129783 | SHN022 | 22kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | INC-0009322 | 20200113PWA_06 | Customer reported pole top sparking and smoking. Upon arrival crew found that intermediate HV/LV pole had ignited at the HV X-arm kingbolt position. No ground fire or 3rd party damage.
272 | PowerCor 19/181 | PowerCor | 2020-10-01 | 0.64375 | -36.7392 | 142.0851 | 1230 Wimmera Hwy Qaontong 3401 | 32097564 | HSM004 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very high | 1 | 1 | INC-0009323 | 20200113PWA_07 | Vic Fire reported a pole fire at the incident location. Upon arrival, a Powercor crew found that a cross arm bunt through and fallen apart. There was no ground fire, no reported injuries or third party property damage.
273 | PowerCor 19/182 | PowerCor | 2020-10-01 | 0.95833 | -36.4345 | 145.4317 | 775 Doyles Road, Kialla VIC 3631 | 30130476 | STN021 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | INC-0009324 | 20200113PWA_08 | CFA reported pole fire at incident location. Upon arrival crew found that an intermediate X-arm on substation pole ( Doyles Lane South P45 ) had ignited and burnt through at the kingbolt position, conductors remained aloft held up by x-arm straps. No ground fire or 3rd party damage.
274 | PowerCor 19/183 | PowerCor | 2020-10-01 | 0.89028 | -36.2953 | 144.5629 | 48 Vise Rd, Bamawm VIC 3561 | 30121008 | SHP012 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | INC-0009326 | 20200113PWA_09 | CFA reported pole fire at the incident location. Upon arrival crew found that an intermediate x-arm on a substation pole ( Hann 8 ) burnt through at the kingbolt position. Conductors remained aloft held up via x-arm straps. No ground fire or 3rd party damage.
275 | PowerCor 19/184 | PowerCor | 2020-11-01 | 0.6875 | -38.0383 | 144.4196 | Outside 110 and 100 Coonawarra Drive, Avalon 3212 | 32085621 | FNS032 | 22kV AC | Rural Short | - transformer (pole mounted) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0009327 | 20200114PWA_01 | The crew were dispatched to a ground fire and blown transformer at the incident location. On arrival the crew found a 10kva transformer had failed causing debris to fall to the ground igniting grass below. Oil had also fallen to ground below. There was some damage to customers fencing and vegetation. No injuries were reported.
276 | PowerCor 19/185 | PowerCor | 2020-11-01 | 0.36528 | -36.1068 | 141.406 | Cnr Nhill-Murrayville rd and E.Juss Rd, Yanac | 32109482 | NHL031 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0009328 | 20200114PWA_02 | Passing motorist reported broken Xarm and pole fire in paddock. Crew attended and found top of pole burnt off and Xarm burnt thru at king bolt. No CFA attended. No ground fire start. No shock or third party damage.
277 | PowerCor 19/186 | PowerCor | 13/01/2020 | 0.69514 | -37.0246 | 143.7498 | 220 Parks Road, Maryborough VIC 3465 | 32020616 | MRO005 | 22kV AC | Rural Long | - underground cable | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009331 | 20200114PWA_05 | CFA reported pole fire & ground fire at incident location. Upon arrival fault crew found that HV cable head had failed at termination ejecting molten material to ground and commencing a small ground fire of 3m x 8m in size, on the road verge extending slightly into an adjacent property. There was no reported injuries.
278 | PowerCor 19/187 | PowerCor | 13/01/2020 | 0.56806 | -37.8803 | 144.7857 | 167 VICTORIA STREET, ALTONA MEADOWS VIC 3028 | 30118483 | LVN022 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0010033 | 20200228PWA_03 | Asset inspector found HV crossarm straps burnt off at HV crossarm, resting on LV crossarm straps. There was no ground fire, no reported injuries or third party property damage.
279 | PowerCor 19/188 | PowerCor | 14/01/2020 | 0.54167 | -35.8838 | 145.4947 | 468 Mywee Rd, Strathmerton 3641 | 30256137 | NKA003 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009341 | 20200115PWA_02 | A customer called to say that wires were down and a fire had started, and he had called the CFA. On arrival the crew found that a tall gum tree located approx. 15m from the line had fallen over the HV conductors, causing one of the conductors to break and fall to the ground. This resulted in a grassfire of approx. 30m x 40m in size. There were no reported injuries.
280 | PowerCor 19/189 | PowerCor | 14/01/2020 | 0.47917 | -36.401 | 145.3994 | 7 Chuck Rd, Sheparton | 33095419 | STN022 | 22kV AC | Urban | - fuse (powder filled) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009345 | 20200115PWA_05 | A Customer who wished to remain anonymous reported that a bird caused an "explosion" on the pole opposite 7 Chuck St and fell to the ground causing a small grassfire. On arrival the crew found that a bird had caused a flashover on the HV fuses of the Substation at the incident location, and had fallen to the ground igniting a grassfire on the nature strip of approx. 2m x 4m. There were no reported injuries or third party damage.
281 | PowerCor 19/190 | PowerCor | 15/01/2020 | 0.76667 | -37.8744 | 143.7657 | Geggies Rd, Corindhap Vic. 3352 | 30005750 | BAS022 | 12.7kV AC (SWER) | Rural Long | - surge diverter | single wire earth return (SWER) | Started by lightning striking a distribution system or a part of a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0009353 | 20200117PWA_03 | A Powercor crew was called to an All Supply Failure report at the Dereel Sth SWER Isolating Substation. When the crew arrived onsite they discovered that a lightning strike had damage a surge diverter mounted on the pole and part of the damaged surge diverter had fallen to the ground causing a small grass fire. The fire burnt approx. 10 sq m of dry grass.
282 | PowerCor 19/191 | PowerCor | 15/01/2020 | 0.79653 | -35.7421 | 143.9617 | 491 Kerang-Koondrook Road, Kerang VIC 3579 | 32029954 | KGT003 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very high | 1 | 1 | INC-0009355 | 20200117PWA_04 | CFA reported pole fire and ground fire at the incident location. Upon arrival crew found that strain/angle pole "P50 Koondrook" had burnt through between pole top assembly and centre phase strain insulator hardware. Conductors remained suspended aloft, burning material however fell to ground and ignited a grass fire along the road verge, approximately 20M x 100M in size. There was no reported injuries.
283 | PowerCor 19/192 | PowerCor | 15/01/2020 | 0.70833 | -37.3308 | 144.5192 | 52 Bowyers Road, Woodend North, VIC 3442 | 33024345 | WND014 | 22kV AC | Rural Short | - pole (concrete) | three phase | Started by lightning striking a distribution system or a part of a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0009356 | 20200117PWA_05 | CFA reported grass fire that commenced at base of pole. Upon arrival crew found evidence of lightning striking CHP "kyneton 1", a ground fire commenced from the base of the concrete pole and burnt 200M x 100M of grass, no 3rd party damage.
284 | PowerCor 19/193 | PowerCor | 15/01/2020 | 0.42292 | -37.3335 | 144.1373 | 22 West Street Daylesford 3460 | 33004683 | BAN008 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0009992 | 20200224PWA_06 | Customer reported a pole outside their property is making arching sounds and he can see smoke and small sparks near conductor(white/blue) on the mains wire. On arrival crew found a hung up EDO fuse, no ground fire or any other damage. There was no ground fire, no reported injuries or third party property damage.
285 | PowerCor 19/194 | PowerCor | 15/01/2020 | 0.75764 | -37.7481 | 144.7721 | 48 PRESIDENT ROAD,ALBANVALE,VIC,3021 | 32163922 | SSE031 | Low voltage AC (<1kV) | Urban | - pole (wood) | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0010036 | 20200228PWA_05 | Report received from vic fire of pole fire. There was no ground fire, no reported injuries or third party property damage. Possible lightning strike.
286 | PowerCor 19/195 | PowerCor | 15/01/2020 | 0.61875 | -35.1036 | 143.3458 | 3571 Murray Valley Hwy Wood Wood 3596 | 32157058 | SHL002 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0010049 | 20200302PWA_05 | Vic Roads reported tree branch falling on main power lines at incident location, heard a loud bang before noticing branch on wire and arcing causing a small fire which has been extinguished, no ground fire, no injuries, no property damage.
287 | PowerCor 19/196 | PowerCor | 16/01/2020 | 0.85556 | -38.2935 | 142.8491 | 772 Princes Hwy, Garvoc | 33098550 | TRG004 | 22kV AC | Rural Short | - guy wire | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0009359 | 20200120PWA_01 | A crew patrolling following an outage found that at P1277 TRG-WBL Line (LIS-408458) the 66kV stay had parted at the helical termination. The stay contacted a HV conductor and the ground. A small grass fire of approx. 22m x 13m = 286m2 in size was found on the road reserve nearby. There was an area of 1/2 m2 fire private property burnt, and no reported injuries.
288 | PowerCor 19/197 | PowerCor | 18/01/2020 | 0.625 | -37.5305 | 143.8344 | 24 Elizabeth Street, Wendouree | 75244598 | BAN004 | Low voltage AC (<1kV) | Urban | - overhead service conductor (residential) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009366 | 20200120PWA_06 | Vic Fire reported a wire down which had caused a grass fire at the incident location. On arrival crew found that a service line had ruptured at the house end roller clamp falling to ground and starting a small grass fire.
289 | PowerCor 19/198 | PowerCor | 18/01/2020 | 0.60347 | -37.5644 | 143.764 | 413 Ballarat -Carngham Road, Bunkers Hill | 33007578 | BAS011 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0009370 | 20200121PWA_02 | Vic Fire reported a grass fire at the incident location, evidently started by Powercor assets. On arrival crew found that a porcelain fuse box had overheated igniting grass below. There was no reported injuries or third party property damage.
290 | PowerCor 19/199 | PowerCor | 19/01/2020 | 0.80486 | -37.6732 | 144.4184 | 5 Chicquita Crt Bacchus Marsh 3340 | PA0054540 | BMH004 | 22kV AC | Rural Short | - transformer (kiosk mounted) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0009374 | 20200121PWA_03 | While patrolling area following thunderstorms field crew were alerted by fore brigade of smoke emanating from kisok substation at incident location. On arrival crew of the substation it was established there was damaged HV cable and a possible damaged kiosk. There was no ground fire, no reported injuries or third party property damage.
291 | PowerCor 19/200 | PowerCor | 19/01/2020 | 0.72639 | -35.3699 | 143.5475 | 99 Back Boga Road Swan Hill 3585 | 32161148 | SHL005 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0009380 | 20200122PWA_01 | Vic fire reported wires down at incident location, caused grass fire. On arrival crew found a FMB had overheated debris ignited grass below. There was no reported injuries or third party property damage.
292 | PowerCor 19/201 | PowerCor | 20/01/2020 | 0.025694 | -36.7052 | 142.205 | 57 Lynott Street, Horsham | 32092095 | HSM009 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009386 | 20200122PWA_02 | Vic Fire reported a pole fire at the incident location. On arrival the fault crew found that a HV crossarm had burned through, and dropped the end of the crossarm onto the LV circuit below. There was no HVI found at customers premises, although a number of smart meters were changed due to damage. There was no reported injuries or third party property damage.
293 | PowerCor 19/202 | PowerCor | 20/01/2020 | 0 | -38.3859 | 142.4916 | 74 Barkly St, Warrnambool 3280 | 30544142 | WBL008 | 22kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0009389 | 20200122PWA_03 | A customer reported to the fire brigade that a pole fire had occurred at the incident location. On arrival the crew found that following misty rain, the pole had burnt through at the eye bolt for the centre phase HV discs. There was no ground fire, and there were no injuries or third party damage reported.
294 | PowerCor 19/203 | PowerCor | 20/01/2020 | 0.41667 | -37.6768 | 142.1907 | 1 Worburtons Rd Mountajup 3294 | 33059281 | HTN005 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0009392 | 20200122PWA_04 | Emergency services reported a pole fire at the incident location. A Powercor crew found that the LV fuse box on the pole ignited due to overheated connections. There were no injuries or ground fire.
295 | PowerCor 19/204 | PowerCor | 20/01/2020 | 0.67986 | -34.6239 | 142.7654 | 37 Happy Valley Road Robinvale Irrigation District Section D 3549 | 32143806 | RVL001 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009394 | 20200122PWA_05 | Following a call from customers Crew found a burnt cross-arm at incident location. There was a small ground fire caused by fallen debris.
296 | PowerCor 19/205 | PowerCor | 20/01/2020 | 0.59375 | -36.287 | 141.3028 | 1256 Broughton Road, Kaniva | 32100850 | NHL031 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0009396 | 20200122PWA_06 | A customer reported a pole fire at the incident locaton. On arrival the fault crew found that a HV crossarm had burned through at the kingbolt, and had dropped down with the HV conductors remaining attached to the crossarm. There was no ground fire, no reported injuries or third party property damage.
297 | PowerCor 19/206 | PowerCor | 22/01/2020 | 0.90139 | -36.0916 | 145.4466 | 13 Gray Street Numurkah 3636 | 33078990 | NKA004 | Low voltage AC (<1kV) | Rural Short | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | INC-0009463 | 20200129PWA_01 | CFA reported wire stared grass fire at incident location, fire now out. On arrival crew found a small branch had contacted LV conductors. Burnt particles fell to ground starting a small grass fire. There was no injuries reported or third party property damage.
298 | PowerCor 19/207 | PowerCor | 22/01/2020 | 0.71736 | -35.6245 | 144.0914 | 365 Koondrook-Murrabit Road Koondrook 3580 | 33021888 | KGT003 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Extreme | 3.5 | 0.7 | INC-0009478 | 20200206PWA_02 | Customer reported wire down, started small grass fire at incident location. There was no conductor damage. CFA on site. There was a small ground fire, no reported injuries or third party property damage.
299 | PowerCor 19/208 | PowerCor | 22/01/2020 | 0.45347 | -36.7204 | 144.6881 | 44 Cornella-Toolleen Rd, Toolleen VIC 3551 | 30336794 | SHP021 | 22kV AC | Rural Long | - fuse (boric acid) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Severe | 2 | 9.2 | INC-0011150 | 20200710PWA_01 | Edo candelling on swer iso. OMS incorrect was a boric acid fuse. Incident found during OMS data review. No ground fire.
300 | PowerCor 19/209 | PowerCor | 23/01/2020 | 0.10972 | -35.9553 | 144.3567 | 4475 Murray Valley Highway Gunbower 3566 | 30029617 | CHA005 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0009421 | 20200123PWA_01 | VIC FIRE reported pole fire at incident location. Crew found Pole fire was put out by fire brigade at Leitchville P121, LIS 704306, burnt around centre phase tee off insulator eye bolt, pole OK, no ground fire. No reported injuries.
301 | PowerCor 19/210 | PowerCor | 23/01/2020 | 0.57639 | -34.5174 | 142.3757 | 3188 Kulkyne Way, Colignan VIC 3494, Australia | 31020287 | RCT013 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very high | 1 | 1 | INC-0009483 | 20200207PWA_09 | HV 22Kv Wooden Crossarm burnt off HV Angle top circuit of HV Angle and Tee Off - small ground fire. There was no reported injuries or third party property damage.
302 | PowerCor 19/211 | PowerCor | 23/01/2020 | 0.52639 | -37.0862 | 141.1435 | 1279 Edenhope-Penola Road Langkoop 3318 | 30084121 | CHM011 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very high | 1 | 1 | INC-0009495 | 20200207PWA_10 | Customer reported pole burning at the top of pole, dry grass at the base, was on fire, customer has put that out, he is calling fire brigade. On arrival crew found pole fire had occurred and debris had ignited grass. There was a 40 15 sq mtr fire, no reported injuries.
303 | PowerCor 19/212 | PowerCor | 24/01/2020 | 0.66736 | -38.7541 | 143.6674 | 27 Pascoe St, Apollo Bay VIC 3233 | 30051538 | CLC013 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0010039 | 20200228PWA_06 | Crossarm fire reported by inspector. On arrival crew found bottom crossarm burnt off. There was no ground fire, no re[ported injuries or third party property damage.
304 | PowerCor 19/213 | PowerCor | 25/01/2020 | 0.66181 | -38.5714 | 142.903 | Dairy -Dunbars Rd, Heytesbury Lower 3268 (approx 1km sth of Curdievale -Port Campbell Rd) | 32056642 | TRG005 | Low voltage AC (<1kV) | Rural Long | - connector / termination | single phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0009501 | 20200207PWA_11 | Fire emergency services reported a pole & ground fire at incident address. On arrival crew found a 20 x 30 mtr grass fire. On examination of substation it was determined that fire was caused by a "hot" joint on the substation 'b' phase. There was no reported injuries.
305 | PowerCor 19/214 | PowerCor | 29/01/2020 | 0.52083 | -37.3863 | 141.5639 | 1787 Nareen Road, Nareen, 3315. On property between between poles LIS 716498 & 716499. (Kilmuir 2 & Kilmuir 3) | 32126181 | HTN006 | 22kV AC | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very high | 1 | 4.6 | INC-0009506 | 20200207PWA_08 | Report received of a grassfire at the incident location. Crew were told that a tip truck with its carrier raised had contacted the overhead line which caused arcing and debris from this incident started the grass fire (10 by 10meters burnt). The truck and its owner had left the site and no details were forthcoming. CFA attended site. There was no reported injuries.
306 | PowerCor 19/215 | PowerCor | 29/01/2020 | 0.65625 | -38.1713 | 144.1417 | 1781 Barrabool Rd, Gnarwarre 3221 | 33041740 | WPD011 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0009511 | 20200207PWA_07 | Powercor received customer reports of no supply. Additional reports were also received of a fire at the incident location. When crews arrived they found a vehicle accident with a HV pole had occurred resulting in pole failure and coming to ground together with HV conductors. The vehicle had come to rest on its roof and was engulfed in flames together with a 400m section of vegetation along the road side reserve. The fire area followed in the vicinity of the fallen HV conductors. Emergency services confirmed the driver had been killed in the accident
307 | PowerCor 19/216 | PowerCor | 30/01/2020 | 0.77569 | -37.7644 | 144.768 | 10 Wandsworth Ave, Deer Park VIC 3023 | 30118460 | SU021 | Low voltage AC (<1kV) | Urban | - overhead conductor (bare; steel) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0009523 | 20200207PWA_06 | Customer reported wire down and grass fire at incident location. MFB attended to control 0.5m x 0.5m grass fire. Attending crew found the fire was caused by a burnt out IPC on East bus fuse white phase hitting the ground after LV main cable broke at connection. No injuries or property damage.
308 | PowerCor 19/217 | PowerCor | 31/01/2020 | 0.61597 | -36.7949 | 144.3409 | 1 Woodlea Close Strathfieldsaye 3551 | 32051730 | BGO013 | 22kV AC | Rural Short | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | INC-0009544 | 20200206PWA_01 | Customer reported a large tree snapped in half now laying on conductors, wire sagging concerned wire could snap with weight. Crew found small ground fire roughly 1m2, where conductor had arced along the fence before the feeder dropped out. There was a small ground fire, no reported injuries or third party property damage.
309 | PowerCor 19/218 | PowerCor | 31/01/2020 | 0.95278 | -35.3169 | 141.2151 | 1037 GUNAMALARY RD -MURRAYVILLE VIC 3512 | 32152937 | OYN001 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Severe | 2 | 2 | INC-0009549 | 20200205PWA_06 | Vicfire advised they had just extinguished a small pole fire at the incident location. On arrival crew found there had been a crossarm fire. There was no ground fire, no reported injuries or third party property damage.
310 | PowerCor 19/219 | PowerCor | 31/01/2020 | 0.67431 | -37.6552 | 143.6713 | 39 Bandys Road, Smythesdale 3351 | 33002842 | BAS021 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Severe | 2 | 9.2 | INC-0009587 | 20200205PWA_01 | Vic fire reported a grass fire (8ha) at incident location. On arrival crew found a overheated FOLCB with one fuse base on the ground. There was no reported injuries. Damage sustained to pasture and fencing.
311 | PowerCor 19/220 | PowerCor | 2020-01-02 | 0.47153 | -36.0357 | 142.8997 | SUNRAYSIA HWY -BIRCHIP VIC 3483 | 32016825 | CTN001 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very high | 1 | 4.6 | INC-0009546 | 20200205PWA_04 | Vicfire attended to extinguish pole fire at the incident location. On arrival crew found crossarm burnt in half at king bolt position. The railway side conductor was approx. 1m from the ground but was over rail reserve and as such not a threat to the general public. There was no ground fire, no reported injuries or third party property damage.
312 | PowerCor 19/221 | PowerCor | 2020-01-02 | 0.34375 | -36.642 | 142.7006 | Wimmera Hwy, Rupanyup 3388 | 32107806 | STL006 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0009585 | 20200204PWA_03 | Vic fire reported a pole fire at the above location on a SWER intermediate pole. There was a small patch of stubble burnt, no reported injuries or third party property damage.
313 | PowerCor 19/222 | PowerCor | 2020-01-02 | 0.10069 | -37.2835 | 142.9187 | 3 Spalding st Ararat 3377 | 32113387 | ART034 | 22kV AC | Rural Short | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0009586 | 20200204PWA_04 | Report revived of smoke and sparks coming from top of pole at incident location. There was no ground fire, no reported injuries but report of third party damage due to HVI.
314 | PowerCor 19/223 | PowerCor | 2020-04-02 | 0.90069 | -35.2079 | 143.4021 | 2267 MURRAY VALLEY HIGHWAY,VINIFERA,VIC,3591 | 33069333 | SHL002 | 22kV AC | Rural Long | - capacity balancing units | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009687 | 20200210PWA_02 | Customer reported fire on top of pole and sparking wires at incident location. Upon arrival crew found that the fire had been extinguished by the CFA. There appears to have been a HV capacitor fault, no damage to pole. There was no ground fire, no reported injuries or third party property damage.
315 | PowerCor 19/224 | PowerCor | 2020-06-02 | 0.43056 | -36.2542 | 144.9814 | 2094 Curr Rd, Tongala | 33089386 | KYM004 | Low voltage AC (<1kV) | Rural Long | - overhead service conductor (other) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009690 | 20200210PWA_03 | Customer rang to reported ground fire start at the incident address. A crew attended and found a customers tree had rubbed through the 2W grey service cable from pole to house. This resulted in the service breaking and falling to the ground starting a grass fire. Area burnt estimated at 160m2 ( 4mx40m ). There was no reported injuries.
316 | PowerCor 19/225 | PowerCor | 2020-06-02 | 0.76736 | -36.6217 | 145.3096 | 1567 Longwood-Shepparton Rd Moorilim 3610 | 33088592 | MNA034 | 12.7kV AC (SWER) | Rural Long | - insulator tie wires / connections | single wire earth return (SWER) | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0009694 | 20200210PWA_04 | Following a call from customer, crew attended low wire at above address at Murchison pole 156. On arrival crew found a low conductor and burnt area underneath pole (4/10 sq mtr). There was no injuries, no third party property damage.
317 | PowerCor 19/226 | PowerCor | 2020-06-02 | 0.62639 | -37.7557 | 144.7387 | Western Hwy (8A Sherdley Green, Caroline Springs VIC 3023, Australia ) | 30110149 | SU035 | 22kV AC | Urban | - fuse (boric acid) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0009695 | 20200210PWA_05 | Vic fire reported fire start at above incident location. On arrival crew found a following a transformer fault one HV BA fuse had ruptured, debris has started a small grass fire. There was a small oil leak. There was no reported injuries or third party property damage.
318 | PowerCor 19/227 | PowerCor | 2020-06-02 | 0.55556 | -36.3712 | 145.4984 | 400 BOUNDARY ROAD, PINE LODGE VIC 3631 | 32192679 | STN024 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0010587 | 20200518PWA_10 | Following report of supply failure crew found a burnt out EDO fuse unit.
319 | PowerCor 19/228 | PowerCor | 2020-07-02 | 0.7875 | -36.0399 | 141.5761 | Hiscocks Track Netherby 3418 | 32099082 | NHL016 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0009709 | 20200211PWA_01 | Report relieved of a pole fire at the incident location. On arrival crew found pole top burnt , CFA attended and extinguished the fire. There was no ground fire, no reported injuries or third party property damage.
320 | PowerCor 19/229 | PowerCor | 2020-09-02 | 0.52917 | -38.1528 | 144.1635 | 13 Nobles road Gnarwarre | 33104059 | WPD011 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very high | 1 | 4.6 | INC-0009686 | 20200210PWA_01 | Pine tree fell into during strong easterly wind, igniting trees and causing a small grass fire of approximately 10 by 6 metres. Some damage to 2 sections of farm fencing. No injuries
321 | PowerCor 19/230 | PowerCor | 2020-09-02 | 0.31528 | -34.2759 | 142.1776 | 175 Belar Ave Ext, Red Cliffs VIC 3496 | 30098049 | RCT021 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009715 | 20200211PWA_02 | Report received of pole fire at incident location. On arrival crew found crossarm burnt off and conductor down. There was no ground fire, no reported injuries or third party property damage.
322 | PowerCor 19/231 | PowerCor | 2020-09-02 | 0.31528 | -34.2758 | 142.1759 | 183 Belar Ave Ext, Red Cliffs VIC 3496 | 32148522 | RCT021 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009718 | 20200211PWA_05 | Crew investigated area fault, on arrival found 2 poles consecutive poles that had cross arms burnt. HV wire down. CFA in attendance. There was no ground fire, no reported injuries or third party property damage.
323 | PowerCor 19/232 | PowerCor | 2020-09-02 | 0.38403 | -34.2334 | 142.1509 | 933 Sandilong Ave, Irymple VIC 3498 | 30095918 | MDA023 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009719 | 20200211PWA_08 | Customer reported wire down at property. ON arrival crew found that a crossarm had burnt through. There was no ground fire, no reported injuries or third party property damage.
324 | PowerCor 19/233 | PowerCor | 2020-09-02 | 0.29306 | -34.2428 | 142.2015 | 207 Belar Ave, Irymple VIC 3498 | 32141632 | RCT011 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009720 | 20200211PWA_11 | Vic Fire reported pole fire at above location. When crew arrived they were able to isolate before HV cross arm collapsed. HV cross arm burnt through at king bolt. No injuries or third party damage. No ground fire.
325 | PowerCor 19/234 | PowerCor | 2020-09-02 | 0.26042 | -34.2241 | 142.1749 | 798 Karadoc Ave, Irymple VIC 3498 | 32148297 | MDA023 | 22kV AC | Rural Short | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009722 | 20200211PWA_14 | Vic Fire reported wires sparking at corner of Karadoc and Fourteenth St. When crew arrived, they found a HV/LV wooden pole had burnt through at the LV king bolt, and the top of the pole had broken off and wires were low. Suspected HVI, inspector called to investigate. No ground fire, no third party damage or injuries.
326 | PowerCor 19/235 | PowerCor | 2020-10-02 | 0.34306 | -37.8975 | 144.6483 | 26 Edgar St Werribee 3030 | 32167520 | WBE033 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0009725 | 20200211PWA_16 | A passer-by reported a HV wire on LV wires at the incident location. Upon arrival a Powercor fault crew found that a cross arm bunt through and fallen HV conductor caused HVI. There was no ground fire and no reported injuries.
327 | PowerCor 19/236 | PowerCor | 2020-11-02 | 0.65069 | -37.6473 | 141.0233 | 1491 Old Lindsay Road Strathdownie | 32131144 | HTN002 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0009730 | 20200212PWA_01 | Fire brigade advised of a pole fire possibly caused by a ground fire. The attending crew identified that a pole fire had occurred and spread into grassland. An area estimated to be several acres (1.5 Ha) of private pasture was burnt. No damage to fencing of nearby pine plantation. No injuries reported
328 | PowerCor 19/237 | PowerCor | 2020-11-02 | 0.54167 | -38.1526 | 143.2371 | 1260 Camperdown-Lismore Rd, Camperdown (Kariah) | 32059880 | CDN004 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0009755 | 20200212PWA_06 | A customer called to report a pole fire and a wire down at the incident location. On arrival the crew found a HV wooden termination cross arm on the substation pole had burnt off. There was a small 5 sq m grass fire. There was no reported injuries or third party property damage.
329 | PowerCor 19/238 | PowerCor | 2020-11-02 | 0.89861 | -38.281 | 141.6148 | 249 PRINCES HIGHWAY, BOLWARRA VIC 3305 | 32135413 | PLD001 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0010588 | 20200520PWA_02 | Customer reports fuse hanging off pole. On arrival crew found a cross-arm had burnt at the EDO mounting position
330 | PowerCor 19/239 | PowerCor | 2020-12-02 | 0.95903 | -37.9331 | 144.6913 | 170 Diggers Road, Werribee South | 30109960 | WBE034 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0009818 | 20200214PWA_02 | MFB called to report a pole fire at LIS-203084. On arrival crew found that tracking had caused the dressing down crossarm to burn in half. There was no ground fire, no reported injuries or third party property damage.
331 | PowerCor 19/240 | PowerCor | 13/02/2020 | 0.85486 | -37.8562 | 144.8167 | 19 Deavey Ct, Altona VIC 3018, Australia | 33073532 | AL006 | 11kV AC | Urban | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009848 | 20200217PWA_01 | MFB reported Sparking wires at end of Jordan Close, Altona. Fire is out in a paddock. On arrival the crew found that metallic balloons had caused a flashover at the incident location. There was a 5 sq metre fire in the paddock. MFB attended. There was no reported injuries or third party property damage.
332 | PowerCor 19/241 | PowerCor | 14/02/2020 | 0.55556 | -37.8224 | 144.8326 | 25 Paw Paw Road, Brooklyn, 3012. | 30103015 | BLT016 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0009851 | 20200217PWA_02 | Report received from customer of part supply. There appears to be a fault with the box on pole and small grass fire started below. On arrival crew found that a FOLCB had burnt out and hot debris had fallen into grass below starting a small fire (0.2x0.2 sqm). There was no injuries or third party property damage.
333 | PowerCor 19/242 | PowerCor | 14/02/2020 | 0.67917 | -37.5279 | 142.7171 | 218 Yarram Gap Rd, Willaura 3379 | 32098473 | ART033 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started by lightning striking a distribution system or a part of a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0009854 | 20200217PWA_03 | A crew was responding to an area fault following a lightning storm. A member of the public stopped the crew and reported a burning fuse tube at the above location. On arrival the crew found that the transformer had been struck by lightning and the EDO fuse tube had hung up and was candling. There was no ground fire or third party damage.
334 | PowerCor 19/243 | PowerCor | 17/02/2020 | 0.70278 | -37.6356 | 142.5118 | WINTOC, 5269 GLENELG HIGHWAY, GLENTHOMPSON | 33055592 | HTN005 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0009971 | 20200220PWA_01 | An EDO HV Fuse hung up and a ground fire was found at the base of the pole type substation.
335 | PowerCor 19/244 | PowerCor | 19/02/2020 | 0.59931 | -37.8471 | 144.8098 | 69 Horsburgh Dr, Altona North VIC 3018. | 30271646 | BLTS-AL | 66kV AC | Rural Long | - crossarm (steel) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009973 | 20200220PWA_02 | Grass fire was reported near base of pole, attending crew found center phase 66kV insulator has broken off its mount. The conductor was resting on the 66kV steel cross-arm and evidence of current passing through the wooden pole to earthed 11kV bracket was found.
336 | PowerCor 19/245 | PowerCor | 21/02/2020 | 0.40833 | -38.2667 | 144.6604 | 14 Hobson Street Queenscliff 3225 | 30288947 | DDL012 | 22kV AC | Rural Short | - underground cable | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0010003 | 20200225PWA_05 | MFB reported sparking wire. Crew found HV centre phase cable head termination failed at LA bracket, made safe, minimal fire damage on ground. No reported injuries or third party property damage.
337 | PowerCor 19/246 | PowerCor | 21/02/2020 | 0.44097 | -35.1082 | 142.4872 | 1255 COCAMBA ROAD, OUYEN VIC 3490 | 32147058 | OYN005 | 12.7kV AC (SWER) | Rural Long | - fuse (EDO fuse) | single wire earth return (SWER) | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0010589 | 20200520PWA_03 | Customer reported fuse down. One arrival crew found EDO tube had burnt in half.
338 | PowerCor 19/247 | PowerCor | 23/02/2020 | 0.99653 | -37.5389 | 143.8804 | 3 Norman St, Ballarat Nth | 33006984 | BAN015 | 22kV AC | Rural Short | - insulators | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009997 | 20200225PWA_01 | VICFIRE reported a ground fire start at the at the incident location. A crew attended and found a possum had flashed over at Norman Mathoura P19. The possum fell to the ground and started a grass fire on the road side of approx. 250m2 ( 25mx10m ). CFA was in attendance and extinguished fire. There was no injuries or third party property damage.
339 | PowerCor 19/248 | PowerCor | 24/02/2020 | 0.23889 | -35.8061 | 144.2083 | 44 Western Road, Cohuna VIC 3568 | 33022821 | CHA006 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0009999 | 20200225PWA_03 | CFA reported pole fire at the incident location. Upon arrival fault crew found that a FOLCB had faulted and burnt the box. No ground fire or damage to concrete pole, CFA attended.
340 | PowerCor 19/249 | PowerCor | 25/02/2020 | 0.01875 | -37.7695 | 144.6093 | 1753-1769 MOUNT COTTRELL ROAD, MOUNT COTTRELL VIC 3024 | 30106376 | MLN011 | 22kV AC | Rural Short | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0010591 | 20200520PWA_04 | Crew responding to a report of power outage found an EDO fuse had burnt in half.
341 | PowerCor 19/250 | PowerCor | 26/02/2020 | 0.24097 | -38.1362 | 141.6188 | Outside 58 Barclay St, Heywood | 32125133 | PLD001 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0010041 | 20200302PWA_01 | Customer reported seeing flames coming from top of pole and sparks falling to the ground into paddock. On arrival, the crew identified the centre phase bridging insulator has burnt through the pole. No ground fire was evident (wet ground), no damage to property, no shocks or injuries reported.
342 | PowerCor 19/251 | PowerCor | 2020-01-03 | 0.41111 | -38.1366 | 141.6767 | 40 Prices lane. Homerton | 30556949 | PLD001 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started in or originated from a distribution system | HBRA only | 1 | Very high | 1 | 1 | INC-0010042 | 20200302PWA_02 | Customers reported Low volts, motors not running properly, lights are dimming, attending crew found HV earth (ISO) damaged and pole base burnt. pole required replacement
343 | PowerCor 19/252 | PowerCor | 2020-02-03 | 0.45833 | -36.7287 | 142.1988 | 34 McTavish Boulevard, Horsham, 3400. | 30228434 | HSM009 | Low voltage AC (<1kV) | Urban | - LV pillar | three phase | Started by any other thing forming part of or coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0010057 | 20200303PWA_01 | MR BRIAN HARMER, REC Steve 0407 340 836 adv concrete truck has nudged pillar on nature strip in front of property. The Pillar was smoking and making noise. On arrival crew found that pillar had been dislodged causing shorting and overheating which scorched the ground underneath. There was no injuries or third party property damage.
344 | PowerCor 19/253 | PowerCor | 2020-03-03 | 0.60417 | -37.8415 | 144.2775 | 42-100 MCLEANS HIGHWAY, STAUGHTON VALE VIC 3340 | 30252610 | CRO013 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0010080 | 20200304PWA_01 | Powercor received advice of wire broken and limited power. Attending crew found that tree had failed at ground level and brought down one HV conductor. Small ground fire had self extinguished. Residents had not been in attendance recently so it unknown when fire occurred.
345 | PowerCor 19/254 | PowerCor | 2020-04-03 | 0.23264 | -34.3104 | 142.1899 | 47 Heath Street Red Cliffs 3496 | 31019780 | RCT022 | 22kV AC | Rural Short | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0010093 | 20200305PWA_03 | Customer advised pole outside is on fire. CFA attended and extinguished fire. On arrival crew found pole had been on fire near the king bolt position. There was no ground fire, no reported injuries or third party property damage.
346 | PowerCor 19/255 | PowerCor | 2020-04-03 | 0.36806 | -34.3045 | 142.185 | 91 Kauri St, Red Cliffs 3496 | 31020020 | RCT023 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0010094 | 20200305PWA_04 | A customer reported a cross-arm fire at the incident location. On arrival the crew found that the HV cross-arm on Kauri Coorong P4 (LIS-4796) had burnt in half at the kingbolt, causing the two halves to fall onto the LV cross-arm below. There were no reported ground fires, HVI or injuries.
347 | PowerCor 19/256 | PowerCor | 2020-04-03 | 0.56458 | -36.1282 | 144.762 | 133 GOULBURN ROAD, ECHUCA VIC 3564 | 30123584 | ECA003 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0010561 | 20200520PWA_06 | Powercor crew responding to a report of a pole fire found cross-arm had burnt
348 | PowerCor 19/257 | PowerCor | 2020-04-03 | 0.63264 | -34.353 | 142.2835 | 228 JOHNS WAY, RED CLIFFS VIC 3496 | 32152209 | RCT014 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0010567 | 20200520PWA_05 | Report of pole fire at incident location.
349 | PowerCor 19/258 | PowerCor | 2020-05-03 | 0.66458 | -36.49 | 144.9704 | Baker Cres, Stanhope, Vic 3623 | 30222928 | SHP021 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0010571 | 20200520PWA_07 | Report of pole fire at incident location, attending crew found pole burnt above transformer.
350 | PowerCor 19/259 | PowerCor | 2020-08-03 | 0.56458 | -37.9679 | 144.3008 | Poultry Farm, 415 Carrs Rd, Anakie 3213 | 30312074 | CRO013 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0010118 | 20200310PWA_02 | Powercor received a call from Vic Fire advising of wires down and a fire start at the incident address. When crews arrived they found an excavator being driven on the property had contacted the HV overhead conductor resulting in conductor damage to all three phases and a 20m x 30m grass / paddock fire. No shock or injuries were experienced by the excavator operator who is also the property owner.
351 | PowerCor 19/260 | PowerCor | 2020-09-03 | 0.79653 | -37.6856 | 144.5863 | Smith Street cnr Henry Street, Melton, 3337 (2-4 SMITH STREET, MELTON VIC 3337) | 30322147 | MLN023 | 22kV AC | Rural Short | - dropper / bridge | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0010123 | 20200310PWA_04 | MFB reported sparking pole near 68 reserve road melton. On arrival crew advised that a dead-crow at the base of HVCHP P3 LIS-828102 appears to have caused a large -flashover across all 3 phases, resulting in damage to all 3 phases of the HVCHP terminations / HV UG cable. There was no reported grass-fire, HVI, injury or shocks as a result of this incident.
352 | PowerCor 19/261 | PowerCor | 2020-10-03 | 0.54583 | -37.9478 | 141.3686 | Cnr of Johnsons Rd and Balds Rd Winnap 3304 | 30095338 | PLD003 | 12.7kV AC (SWER) | Rural Long | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0010125 | 20200311PWA_01 | A tree harvester cut down a tree branch on to SWER line. On arrival, a Powercor fault crew found that the tree branch on the conductors and small ground fire about 10 Sqm. The crew made the place safe.
353 | PowerCor 19/262 | PowerCor | 2020-12-03 | 0.41667 | -37.144 | 144.1886 | 221 Kemps Bridge Rd, Guildford 3451 | 30038431 | CMN001 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0010146 | 20200313PWA_03 | A farmer reported a tree took down mains wires at the incident location. On arrival the crew found that the farmer was cutting a tree approx. 15m from the HV Line, when it fell onto the 22kV 3 phase HV conductors. HV conductor broke and fell to the ground causing a small grassfire approx. 10m2 in size. There was no reported injuries or third party property damage.
354 | PowerCor 19/263 | PowerCor | 13/03/2020 | 0.83472 | -37.1929 | 143.3727 | 1602 Pyrenees Hwy, Amphitheatre VIC 3468 | 32022861 | MRO008 | 22kV AC | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0010150 | 20200316PWA_01 | Vic fire reported wires down and grass fire at incident location. On arrival found a large tree branch had fallen across HV conductors. Conductors still in the air and a ground fire started undermeath line. There was no injuries or third party property damage.
355 | PowerCor 19/264 | PowerCor | 13/03/2020 | 0.84931 | -37.5518 | 143.8686 | 501 Sherrard St cnr Napier St Black Hill 3350 | 32012126 | BAN007 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0010153 | 20200316PWA_03 | A crossarm fire resulted in the high voltage conductor falling with the insulator coming to rest on the low voltage x arm. There was reported to be a HVI. There was no ground fire, no reported injuries.
356 | PowerCor 19/265 | PowerCor | 14/03/2020 | 0.55417 | -38.3169 | 142.7468 | 8559 Princes Hwy, Panmure 3265 | 32058973 | TRG004 | Low voltage AC (<1kV) | Rural Short | - fuse (any other type) | single phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0010154 | 20200316PWA_04 | A customer called to advise that what he described as a "capacitor" had caught fire on his meter board. On arrival the crew found that one of the meter board fuses had overheated causing minor damage to the wooden meter board. There was no ground fire, no reported injuries or third party property damage.
357 | PowerCor 19/266 | PowerCor | 15/03/2020 | 0.12014 | -38.4659 | 144.0652 | 20 Old Neuk Rd Moggs Creek | 32070006 | WPD014 | 22kV AC | Rural Short | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0010575 | 20200520PWA_08 | Crew attending to an outage found fuse carrier had burnt.
358 | PowerCor 19/267 | PowerCor | 15/03/2020 | 0.81319 | -36.3432 | 145.1323 | 1636 LILFORD ROAD, LANCASTER VIC 3620 | 32189439 | KYM003 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0010576 | 20200520PWA_09 | Crew attending a report of part supply found arcing EDO fuse.
359 | PowerCor 19/268 | PowerCor | 16/03/2020 | 0.56319 | -38.0094 | 142.8136 | 1513 Mortlake-Ararat Rd, Mortlake 3272 | 32061459 | TRG002 | 22kV AC | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0010161 | 20200317PWA_02 | At 13:31 the Woorndoo P84 ACR went to lockout. While patrolling, the fault crew found that the HV conductors wrapped together between poles 140-140E Woorndo line. Line appears to have been struck by an unknown vehicle. The fault current at the ACR caused molten metal to be ejected from the ACR connections igniting grass belo, resulting in 20x100m of roadside reserve being burnt. The fire site was approximately 7.5 km's from the conductor contact site. there were no reported injuries or third party property damage.
360 | PowerCor 19/269 | PowerCor | 17/03/2020 | 0.53056 | -36.3231 | 145.068 | 276 Bolitho Rd, Kyabram 3620 | 30130988 | SHTS-KYM1 | 66kV AC | Unknown | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0010169 | 20200318PWA_02 | Vicfire reported a wire down and a grassfire at the incident location. On arrival the crew found that a large branch from a tree had fallen onto the 66kV OH HV conductors resulting in a ground fire of approx. 30m x 10m= 300m2 of road reserve. The HV conductors did not fall to the ground. There was no reported injuries or third party damage.
361 | PowerCor 19/270 | PowerCor | 18/03/2020 | 0.47292 | -37.1568 | 142.5282 | 310 Grampians Road (corner Wattletree road) Halls Gap 3381 | 30333974 | STL005 | Low voltage AC (<1kV) | Rural Long | - overhead conductor (ABC) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very high | 1 | 4.6 | INC-0010176 | 20200319PWA_03 | Vic Fire reported a tree has bought down wires across road and caused grass fire at incident location. Emergency services on site. Crew found a tree damaged LV ABC between LIS: 840255 and LIS: 74877, bringing down 4 x bays of 95mm and 150mm cable, The transformer HV bushing also damaged, There was a a 8m x 6m grass fire, 2 x private vehicles damaged by falling cable. There was no reported injuries.
362 | PowerCor 19/271 | PowerCor | 18/03/2020 | 0.65208 | -37.9381 | 144.5921 | 470 Wests Rd, Werribee VIC 3030 | 33071639 | WBE023 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0010199 | 20200320PWA_02 | A Powercor fault crew attending a fault on WBE023 feeder found that the feeder HV overhead conductors contacted by an excavator at Werribee tip yard at the incident location. The conductor damaged and fell on to the ground. There was a small grass fire about one Sqm but no injures reported. The excavator works for the tip yard but no more details available. The crew made the place safe and all repairs have been completed. The protection operated.
363 | PowerCor 19/272 | PowerCor | 19/03/2020 | 0.57986 | -37.7908 | 142.324 | Hamilton-Chatsworth Rd, Penshurst VIC 3289, Australia | 31018721 | NRB-HTN | 66kV AC | Unknown | - pole (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very high | 1 | 4.6 | INC-0010200 | 20200320PWA_03 | Call received from Vic Fire advising of a fire Penshurst - approx 3k east Dunkeld-Penshurst rd. At this time NRB-HTN 66kv line operated to Lockout. On arrival crew advised that centre phase pole top assembly had dislodged resulting in a pole fire near the crossarm straps. Debris started a grass fire estimated to be 2000 sq m of roadside reserve. There was no reported injuries.
364 | PowerCor 19/273 | PowerCor | 20/03/2020 | 0.57292 | -37.9239 | 141.2753 | 28 Ascot St, Dartmoor VIC 3304 | 30089487 | PLD003 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0010217 | 20200323PWA_02 | Vic fire reported smoldering pole at incident location. ON arrival crew found a crossarm has burnt through. The fire self extinguished. There was no ground fire, no reported injuries or third party property damage.
365 | PowerCor 19/274 | PowerCor | 26/03/2020 | 0.48958 | -37.8264 | 144.8574 | Opposite 65-69 Kyle Rd Altona North 3025 | 30569902 | BLT020 | 66kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0010245 | 20200327PWA_01 | MFB reported powerlines down and wires were sparking. On arrival the crew found that multi circuit pole BLTS-NT Pole 6 (LIS-957045) had a pole fire mid way up the pole causing the top section to fall over but remain in the air. Two cars were reported as having damage caused by small pieces of molten aluminium and pieces of charcoal. There were no reported injuries, HVI or ground fire.
366 | PowerCor 19/275 | PowerCor | 2020-02-04 | 0.084028 | -35.9281 | 144.3658 | 78 Gum Lagoon Road, Gunbower, VIC 3566 | 32033196 | CHA005 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0010289 | 20200406PWA_02 | Following an all supply failure, a crew found a pole fire at incident location. NAO arranged for CFA to attend to extinguish fire. There was no ground fire, no reported injuries or third party property damage.
367 | PowerCor 19/276 | PowerCor | 2020-03-04 | 0.3125 | -38.1236 | 141.6372 | 14 Bell St Heywood | 3026900 | PLD003 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0010288 | 20200406PWA_01 | A powercor crew attending a fault located a pole fire at the incident location. The pole was half burnt through at the crossarm brace position. There was no ground fire, no reported injuries or third party property damage.
368 | PowerCor 19/277 | PowerCor | 2020-04-04 | 0.53958 | -35.1861 | 143.316 | CHINKAPOOK-NYAH WEST ROAD, CHINKAPOOK VIC 3546 | 32157434 | SHL002 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very high | 1 | 1 | INC-0010602 | 20200520PWA_10 | Crew responding to a report of a pole fire found found HV crossarm burnt.
369 | PowerCor 19/278 | PowerCor | 2020-05-04 | 0.76042 | -38.3601 | 141.4056 | CA 8 Peacocks Road, Cape Bridgewater VIC 3305 | 30240886 | PLD006 | 66kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0010319 | 20200407PWA_01 | Powercor crew attending to outage in area became aware of a pole fire on shared pole.
370 | PowerCor 19/279 | PowerCor | 2020-09-04 | 0.79028 | -37.4266 | 144.8627 | 1108 BOLINDA-DARRAWEIT ROAD, DARRAWEIT GUIM | 33025397 | GSB012 | 22kV AC | Rural Short | - pole (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0010347 | 20200414PWA_01 | Report received of pole and transformer on fire at incident location. On arrival the crew found that fire had been extinguished by CFA. There was no ground fire, no reported injuries or third party property damage.
371 | PowerCor 19/280 | PowerCor | 2020-09-04 | 0.33542 | -35.2041 | 143.3632 | 215 HOBSON ROAD,NYAH WEST,VIC,3595 | 33069006 | SHL002 | 22kV AC | Rural Long | - transformer (pole mounted) | three phase | Started by lightning striking a distribution system or a part of a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0010607 | 20200520PWA_12 | Report received of a transformer struck by lighting. Transformer was on fire, now smoking
372 | PowerCor 19/281 | PowerCor | 2020-09-04 | 0.46181 | -37.5906 | 143.9655 | 2754 OLD MELBOURNE ROAD, DUNNSTOWN VIC 3352 | 30004990 | BAS023 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0010610 | 20200520PWA_11 | Report received of a pole fire. On arrival crew found cross-arm burnt at EDO mounting position.
373 | PowerCor 19/282 | PowerCor | 2020-11-04 | 0.81528 | -36.3431 | 145.1749 | O/S 1230 LILFORD RD. MERRIGUM | 30130456 | KYM003 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0010352 | 20200414PWA_02 | Report received of small grass fire and wire down at the incident location. On arrival crew found that a conductor had fractured at the 22kv insulator and fallen to the ground starting a small grass fire. There was no reported injuries or third party property damage.
374 | PowerCor 19/283 | PowerCor | 13/04/2020 | 0.67847 | -37.7031 | 144.8061 | 1017 Old Calder Hwy Service Rd, Keilor VIC 3036 | 26810509 | SA006 | Low voltage AC (<1kV) | Rural Short | - LV pillar | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0010361 | 20200415PWA_02 | Customer advised that pillar at front of his property had caught fire. Crew attended onsite the fire brigade was at the incident location with the paralleling pillar taped off. A vehicle had ran the pillar over but no one had any details. The flashover caused a small fire on the nature strip. There was no reported injuries or third party property damage.
375 | PowerCor 19/284 | PowerCor | 14/04/2020 | 0.61458 | -38.0133 | 143.482 | 3200 Foxhow Rd, Berrybank. | 30049834 | CDN004 | Low voltage AC (<1kV) | Rural Long | - overhead service conductor (residential) | single phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0010382 | 20200416PWA_01 | A customer called to report a service wire broken mid-span and a small grass fire. On arrival the crew found that a grey service cable had ruptured mid span and fallen to the ground. The live end of the service cable ignited a small grass fire of around 40 sq metres. There was no injuries or third party property damage reported.
376 | PowerCor 19/285 | PowerCor | 18/04/2020 | 0.74931 | -36.1485 | 144.8227 | 411 Brown Rd, Echuca Village VIC 3564 | 30125952 | ECA005 | 22kV AC | Rural Short | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0010407 | 20200420PWA_02 | Call from customer advising tree down on mains wires, sparking and starting to catch fire and CFA had been called. On arrival crew found a large branch had fallen. The tree is located on private property on the opposite side of the road from the HV line. HV conductor was down but no ground fire was evident. Burn marks identified on branch. No ground fire, no injuries, no third party damage.
377 | PowerCor 19/286 | PowerCor | 20/04/2020 | 0.94861 | -38.2604 | 144.2001 | MUNGARA, 475 HUNTS ROAD, PARAPARAP VIC 3240 | 33045623 | WPD014 | 22kV AC | Rural Short | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0010621 | 20200520PWA_13 | Crew responding to an outage found that a fuse had hung up and burnt.
378 | PowerCor 19/287 | PowerCor | 23/04/2020 | 0.74792 | -34.2927 | 142.1987 | 121 Azolia Street Red Cliffs 3496 | 32152465 | RCT023 | Low voltage AC (<1kV) | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0010443 | 20200424PWA_01 | Customer reported wooden x-arm on power pole has caught fire, wires do not look damaged yet, burning into pole. OK, customer will call Emergency Services. On arrival crew found pole fire was at king bolt of LV Xarm. Made safe, no ground fire, CFA attended. No reported injuries or third party property damage.
379 | PowerCor 19/288 | PowerCor | 23/04/2020 | 0.78958 | -34.2061 | 142.177 | 2 Eleventh Street (corner Cowra Avenue)Mildura 3500 | 32155128 | MDA024 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0010450 | 20200424PWA_02 | CFA reported a pole fire at incident location. Crew found that the top position HV xarm had burnt allowing the white phase insulator to drop down on the lower HV conductors. CFA attended and put out the fire. There was no ground fire, no reported injuries or third party property damage.
380 | PowerCor 19/289 | PowerCor | 29/04/2020 | 0.45833 | -38.3072 | 144.3298 | 240 Fischer Street, Torquay, 3228. (rear of property). | 30346842 | WPD022 | Low voltage AC (<1kV) | Rural Short | - LV pillar | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0010468 | 20200430PWA_01 | Report received of pillar fire at incident location. On arrival crew found an lv pillar had been destroyed and small patch of burnt ground. There was no reported injuries or third party property damage.
381 | PowerCor 19/290 | PowerCor | 30/04/2020 | 0.90972 | -35.0652 | 142.3152 | 9 Martin avenue, Ouyen VIC 3496 | 32148103 | OYN007 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0010485 | 20200504PWA_01 | CFA reported a pole fire at the incident location. Upon arrival the fault crew found that a 3 phase LV FOLCB had burnt resulting in an all supply fail. There was no ground fire or 3rd party damage.
382 | PowerCor 19/291 | PowerCor | 2020-01-05 | 0.43403 | -37.3458 | 144.4404 | 2 CADDYS LANE, TYLDEN VIC 3444 | 30342390 | WND024 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started in or originated from a distribution system | within electric line construction area | 19.8 | Low-moderate | 0.2 | 3.96 | INC-0010481 | 20200505PWA_01 | Fault crew investigating an outage found substation pole burning at ground level. Crew was preparing to isolate supply at tee off further up the line when burnt pole fell.
383 | PowerCor 19/292 | PowerCor | 2020-12-05 | 0.72569 | -38.3879 | 142.4838 | 2 Banyan Street, Warrnambool | 30135617 | WBL008 | Low voltage AC (<1kV) | Urban | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0010595 | 20200513PWA_02 | Report received of pole fire at incident location. On arrival a crew found a Krone box on fire. THere was no ground fire, no reported injuries or third party property damage.
384 | PowerCor 19/293 | PowerCor | 13/05/2020 | 0.59028 | -36.4391 | 145.241 | 305 Dhurringile Rd, Tatura VIC 3616, Australia (6-7 Rose Court Tatura 3616) | 33093071 | MNA013 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0010686 | 20200520PWA_01 | MNA013 Feeder went to lockout. On arrival crew found a small branch (200mm long) had blown onto the line on the west side of pole 65 Tatura line. There was signs of a flashover to crossarm and small burn marks on the branch. There was no ground fire , no reported injuries or third party property damage.
385 | PowerCor 19/294 | PowerCor | 15/05/2020 | 0.94306 | -38.2825 | 144.6123 | 23 Albert St, Point Lonsdale | 30071219 | DDL012 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0010657 | 20200518PWA_05 | Report received of a pole fire in Albert st Point Lonsdale. On arrival the crew found that an overheated FOLCB had resulted in a pole fire. Falling debris also resulted in a small ground fire.
386 | PowerCor 19/295 | PowerCor | 17/05/2020 | 0.82639 | -38.074 | 144.3587 | 120 Bacchus Marsh Rd, Corio VIC 3214, Australia | 35207919 | FNS011 | Low voltage AC (<1kV) | Rural Short | - lamps (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0011069 | 20200703PWA_03 | Public light fire. No gorund fire.
387 | PowerCor 19/296 | PowerCor | 18/05/2020 | 0.65139 | -36.9653 | 143.5132 | Maryborough-st Arnaud Rd, Rathscar VIC 3465, Australia | 32024807 | MRO005 | 22kV AC | Rural Long | - pole (wood) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | INC-0010683 | 20200519PWA_03 | Vicfire advised of fire caused by tractor operator hitting pole and bringing it and the overhead conductors to the ground. Tractor operator advised to remain in tractor until PCA crew onsite. On arrival crew found that a tractor/sprayer had collided with a pole . Police and CFA on site. There was a small grass fire , no reported in juries or third party proper try damage.
388 | PowerCor 19/297 | PowerCor | 19/05/2020 | 0.79167 | -38.1951 | 144.3567 | 30 Grove Rd, Marshall VIC 3216, Australia | 31013080 | GLE013 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0010697 | 20200521PWA_01 | Customers called in to report a conductor brought down by tree branch. The crew attended and confirmed all 3 phases had been brought down by a tree branch. There was a small burn mark on the ground next to the conductors. There was no reported injuries or third party property damage.
389 | PowerCor 19/298 | PowerCor | 22/05/2020 | 0.67361 | -38.2813 | 141.6155 | 249 Princes Hwy, Bolwarra 3305 | 31033424 | PLD001 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | INC-0010743 | 20200525PWA_02 | A tree clearing crew reported that a PTA (pole top assembly) had burnt off the pole at the incident location, P519X KRT-PLD No2 R. On arrival the crew found that a bridging insulator had caused a section of the top of the pole to be burnt. There was no ground fire, and no other reported damage or injuries.
390 | PowerCor 19/299 | PowerCor | 22/05/2020 | 0.71319 | -36.7738 | 144.3114 | 27 Plante Court Strathdale | 60349574 | BGO022 | Low voltage AC (<1kV) | Urban | - services pit | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0010744 | 20200525PWA_03 | Customer reported electricity pit out front of property was on fire but had been extinguished. Customer reported a number of neighbors with no power and partial power. When crew arrive they found that there had been evidence of a fire in the service pit with melted assets inside. No injuries or third party damage.
391 | PowerCor 19/300 | PowerCor | 22/05/2020 | 0.44236 | -38.315 | 144.1699 | 370 FLAXBOURNE ROAD,PARAPARAP,VIC,3240 | 32084233 | WPD014 | 22kV AC | Rural Short | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | within electric line construction area | 19.8 | No forecast | 0.1 | 1.98 | INC-0011070 | 20200703PWA_04 | EDO found burnt in half on ground. No ground fire.
392 | PowerCor 19/301 | PowerCor | 23/05/2020 | 0.64583 | -37.8063 | 142.8023 | 3174 Mortlake-Ararat Rd, Woorndoo. | 32060550 | TRG002 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | INC-0010747 | 20200525PWA_05 | Powercor Employee was driving on the road at the incident location, when he noticed a burn mark on the cross-arm of P263 Woorndoo Line. On closer inspection, it was found that the crossarm had burnt most of the way through at the strap bolt. All of the conductors were still in position, and there was no ground fire.
393 | PowerCor 19/302 | PowerCor | 24/05/2020 | 0.33889 | -38.099 | 144.3229 | UNIT 3 89 ROLLINS ROAD, BELL POST HILL VIC 3215 | 30070328 | GL015 | Low voltage AC (<1kV) | Rural Long | - fuse (any other type) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0010749 | 20200525PWA_07 | A fault crew attended an all supply failure at the incident location. On arrival the crew found that a meter board fuse had overheated and burnt a small area of the meter board. There was no other fire or damage reported.
394 | PowerCor 19/303 | PowerCor | 25/05/2020 | 0.65486 | -36.0553 | 144.1193 | 74 VICTORIA STREET,PYRAMID HILL,VIC,3575 | 32031168 | CHA006 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0011071 | 20200703PWA_05 | Cross arm fire reported.
395 | PowerCor 19/304 | PowerCor | 26/05/2020 | 0.81319 | -38.4117 | 144.1669 | 55A Belton St, Anglesea 3230 | 30066251 | WPD021 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0010777 | 20200527PWA_02 | Vicfire reported a pole fire at the incident location. On arrival the crew found that an LV fused mains box had overheated and failed. The box dropped debris and melted plastic to the ground, but there was no ground fire. here was no other damage or injuries reported.
396 | PowerCor 19/305 | PowerCor | 26/05/2020 | 0.75208 | -38.1149 | 144.3224 | 1 Rowe St, Hamlyn Heights 3215 | 32069696 | GL013 | Low voltage AC (<1kV) | Urban | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0010778 | 20200527PWA_03 | A customer and Vicfire both reported a fire on a pole at the incident location. On arrival the crew found that an LV FSD isolator had overheated and caught fire. There was no ground fire, other damage or injuries reported.
397 | PowerCor 19/306 | PowerCor | 26/05/2020 | 0.74583 | -38.2579 | 144.5214 | 29 Field St N, Ocean Grove 3226 | 32076059 | DDL011 | Low voltage AC (<1kV) | Rural Short | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0010779 | 20200527PWA_04 | MFB Communications reported a pole fire at the incident location. On arrival the crew found that a transformer LV isolator overheated, causing the attached lead insulation to catch fire, melt and fall to the ground. There were no reported injuries, ground fire or other damage.
398 | PowerCor 19/307 | PowerCor | 29/05/2020 | 0.81528 | -37.7396 | 144.6395 | 463-467 Paynes Rd, Rockbank 3335 | 33076291 | MLN021 | 22kV AC | Rural Short | - transformer (pole mounted) | three phase | Started by lightning striking a distribution system or a part of a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | INC-0010856 | 20200602PWA_01 | MFB reported a pole fire at incident location. On arrival crew found a transformer had failed and caught fire briefly. There was no ground fire, no reported injuries or third party property damage. Possible lightning strike.
399 | PowerCor 19/308 | PowerCor | 30/05/2020 | 0.63889 | -38.2955 | 142.3687 | Stadium, High Street, KOROIT 3282 (76 High St, Koroit VIC 3282, Australia) | 30271815 | KRT013 | 22kV AC | Rural Long | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0010857 | 20200602PWA_02 | Emergency services reported a pole fire at incident location. When crews arrived they found a HV insulated dropper lead to Pole type S/S "High-King 42" had failed and required replacement. No evidence or reports received of ground fire starts, injuries or third party property damage
400 | PowerCor 19/309 | PowerCor | 2020-05-06 | 0.47847 | -36.0486 | 144.1145 | 86 Kelly St, Pyramid Hill VIC 3575 | 30024621 | CHA006 | Low voltage AC (<1kV) | Rural Long | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0011176 | 20200714PWA_03 | FSD fire - no ground fire. Found during OMS data review.
401 | PowerCor 19/310 | PowerCor | 2020-08-06 | 0.55972 | -36.1801 | 145.3548 | 208 McPhersons Rd, Mundoona VIC 3635 | 33080324 | SHN011 | 22kV AC | Rural Long | - fuse (boric acid) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | INC-0011178 | 20200714PWA_04 | Following fault call, Boric acid fuse found hung up and burnt as switch pole. No ground fire. Incident found during OMS data review
402 | PowerCor 19/311 | PowerCor | 2020-12-06 | 0.26944 | -38.2774 | 144.4898 | 11 Jasper Ave, Barwon Heads 3227 | 30072968 | GLE013 | Low voltage AC (<1kV) | Rural Short | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0010952 | 20200612PWA_02 | Vicfire called to report a pole fire at the incident location. On arrival the crew found that the red phase connection of an FSD Krone box on the substation pole had overheated and burnt out. There was no ground fire or any reported injuries or other damage.
403 | PowerCor 19/312 | PowerCor | 14/06/2020 | 0.64722 | -34.9788 | 142.3654 | 196 Vallance Road OUYEN | 32151770 | OYN003 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | INC-0010975 | 20200616PWA_01 | Report received of pole fire at incident location. On arrival crew found top burnt off SWER pole. Fire extinguished. There was no ground fire, no reported injuries or third party property damage.
404 | PowerCor 19/313 | PowerCor | 17/06/2020 | 0.36319 | -37.9834 | 143.4908 | 3538 Foxhow-Berrybank Road Berrybank 3323 | 30049762 | CDN004 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | INC-0010991 | 20200618PWA_01 | GRAINCORP OPERATIONS reported pole on fire and wire down. Crew found a damaged pole due to a pole fire, needs to be replaced, There was no ground fire, no reported injuries or third party property damage.
405 | PowerCor 19/314 | PowerCor | 20/06/2020 | 0.99167 | -38.339 | 141.5989 | 120 Blair Street, Portland | 33060158 | PLD004 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0011011 | 20200622PWA_03 | CFA reported a pole fire at the above address. The crew attended and found a faulted Krone box on the sub pole. It had overheated and melted. No ground fire was involved. CFA attended the incident. There was no ground fire, no reported injuries or third party property damage.
406 | PowerCor 19/315 | PowerCor | 22/06/2020 | 0.99236 | -36.2526 | 144.8243 | 1768 ODEA ROAD, STRATHALLAN VIC 3622 | 31025963 | ECA005 | 22kV AC | Rural Short | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0011040 | 20200624PWA_04 | Powercor crew responded to advice of a pole that was on fire. On arrival the crew identified that the high voltage transformer leads have malfunctioned.
407 | PowerCor 19/316 | PowerCor | 24/06/2020 | 0.81319 | -38.1818 | 144.4337 | 455 Bellarine Highway, Moolap. | 31011250 | GLE024 | Low voltage AC (<1kV) | Rural Short | - fuse (any other type) | single phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | INC-0011045 | 20200625PWA_01 | Customer reported smoldering meterboard, no visible flames. On arrival crew found a powercor fuse on the meter board had overheated and caught fire. Meter board slightly burnt and fuse melted. There was no ground fire, no reported injuries or third party property damage.
408 | PowerCor 19/317 | PowerCor | 25/06/2020 | 0.64583 | -38.2777 | 141.6417 | 8582 Princes Hwy, Allestree VIC 3305 | 30308761 | PLD001 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | INC-0011053 | 20200629PWA_01 | Customer reporting was driving and noticed asset on powerpole was on fire. On arrival crew advised junction box has caused small fire which has self extinguished. There was no ground fire, no reported injuries or third party property damage
409 | PowerCor 19/318 | PowerCor | 25/06/2020 | 0.92431 | -36.0924 | 145.443 | 101 Melville St, Numurkah VIC 3636 | 30304093 | NKA004 | 22kV AC | Rural Short | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0011054 | 20200629PWA_02 | Vic Fire reported sparking and arcing at transformer at above address. On arrival, crew found failed insulated HV lead. HV fuse had operated. Evidence of arcing between two leads. No ground fire, no injuries, no third party damage.
410 | PowerCor 19/319 | PowerCor | 26/06/2020 | 0.96181 | -38.5549 | 143.2149 | 590 or 712 CENTRE ROAD, COORIEMUNGLE 3268 | 30256933 | COB011 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | INC-0011058 | 20200629PWA_03 | CFA Reported fire. Crew attended and found customer pole mounted krone fuse box had burnt out, causing pole fire. No ground fire, shocks or injuries reported.
411 | PowerCor 19/320 | PowerCor | 27/06/2020 | 0.82847 | -38.4074 | 144.1849 | 4 Noble St, Anglesea | 30289267 | WPD021 | Low voltage AC (<1kV) | Rural Short | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0011061 | 20200629PWA_05 | Vicfire Reported crossarm fire. Crew attended and found pole mounted FSD glowing hot and melting, no pole fire. There was no ground fire, no reported injuries or third party property damage.
412 | PowerCor 19/321 | PowerCor | 28/06/2020 | 0.48889 | -37.9558 | 144.3031 | 415 CARRS ROAD,ANAKIE,VIC,3213 | 30312072 | CRO013 | 22kV AC | Rural Short | - dropper / bridge | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | INC-0011060 | 20200629PWA_06 | Customer reported flames and smoke coming from pole on his property, farm has lost supply. Crew found a HV lead on the sub pole had burnt out and required replacing.
413 | PowerCor 19/322 | PowerCor | 30/06/2020 | 0.74236 | -38.3362 | 143.1761 | 190 Thorntons Rd E, South Purrumbete VIC 3260 | 30046394 | CDN001 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | INC-0011182 | 20200715PWA_01 | Following reports of no supply an EDO fuse was found burnt but hung up. There was no ground fire. Found during OMS data review.
414 | PowerCor 19/323 | PowerCor | 18/12/2019 | 0.74097 | -36.7613 | 144.2955 | 2 MICHAEL STREET, BENDIGO,VIC,3550 | 32052992 | BGO022 | Low voltage AC (<1kV) | Urban | - overhead service conductor (residential) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0011587 | 20200908PWA_02 | Customer advised half of a tree has fallen onto swire , wire is sparking with sparks reaching the ground, the sparks have already caused 2 lawn fires. Attending crew replaced aerial service cable.
415 | PowerCor 19/324 | PowerCor | 2020-05-06 | 0.79514 | -38.254 | 144.5592 | 21-29 Ocean Grand Dr, Ocean Grove VIC 3226, Australia | 32080289 | DDL024 | 22kV AC | Rural Short | - fuse (powder filled) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0011183 | 20200715PWA_02 | Report of pole top fire. On arrival crew found a PF fuse has candled. There was no ground fire. Incident found during oms data review.
416 | Jamena 19/20 | Jamena | 2019-09-07 | 0.38921 | -37.7654 | 144.8888 | UNIT 4 12 CHICAGO STREET, MARIBYRNONG VIC 3032 | A029617 | YVE22 | Low voltage AC (<1kV) | Urban | - fuse (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 182968 | 20200224JEM_01 | Transformer isol krone box burnt out
417 | Jamena 19/21 | Jamena | 16/07/2019 | 0.723 | -37.7546 | 144.8642 | 38 BORDEAUX STREET, AVONDALE HEIGHTS VIC 3034 | A025384 | BY14 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | PM10294803 | 20200224JEM_02 | Pole top / crossarm fire
418 | Jamena 19/22 | Jamena | 2019-12-11 | 0.29792 | -37.8275 | 144.8713 | 9 GREENE ST, SOUTH KINGSVILLE VIC 3015 (RAIL EASEMENT SOUTH SIDE, GREENE ST, SOUTH KINGSVILLE VIC 3015) | A028141 | FW5 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | PM10298364 TE188677 | 20191112JEM_01 | Pole top / crossarm fire
419 | Jamena 19/23 | Jamena | 20/11/2019 | 0.50833 | -37.6738 | 144.8668 | VACANT LAND, 206-300 WESTERN AVENUE, MELBOURNE AIRPORT VIC 3045 | A041484 | AW14 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | PM10298633 TE189206 | 20191206JEM_02 | Bird Strike resulting in small grass fire
420 | Jamena 19/24 | Jamena | 21/11/2019 | 0.61389 | -37.7113 | 144.8864 | EASEMENT EX WESTFIELD SHOPPING TOWN, TULLAMARINE VIC 3043 | A096144 | AW9 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | PM10298673 TE189398 | 20191217JEM_03 | Lightning strike igniting a small grass fire
421 | Jamena 19/25 | Jamena | 21/11/2019 | 0.39861 | -37.7341 | 144.9825 | F.COX RESERVE, BETWEEN ELIZABETH ST AND PETERSON AVE, COBURG NORTH VIC 3058 (nearest address is 29 PETERSON AVE, COBURG NORTH VIC 3058) | A034855 | CN8 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | PM10298665 TE189573 | 20191122JEM_01 | Large Tree brought down HV conductor in high winds igniting a small grass fire
422 | Jamena 19/26 | Jamena | 26/11/2019 | 0.23958 | -37.74 | 144.9343 | 53A MITCHELL PARADE, PASCOE VALE SOUTH VIC 3044 | A093964 | CS2 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-Moderate | 0.2 | 0.04 | PM10298833 TE189778 TE189806 | 20191217JEM_04 | Pole top / crossarm fire
423 | Jamena 19/27 | Jamena | 26/11/2019 | 0.27361 | -37.7403 | 144.9627 | 8 MAIN STREET, COBURG VIC 3058 | A050129 | CS13 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-Moderate | 0.2 | 0.04 | PM10298730 TE189779 | 20191217JEM_05 | Pole top / crossarm fire
424 | Jamena 19/28 | Jamena | 20/12/2019 | 0.63681 | -37.7318 | 145.0571 | 155 BAMFIELD ROAD, HEIDELBERG WEST VIC 3081 | A110840 | NH3 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 190853 | 20200104JEM_02 | Pole top / crossarm fire
425 | Jamena 19/29 | Jamena | 21/12/2019 | 0.1995 | -37.8059 | 144.8846 | 2 DICKSON STREET, KINGSVILLE VIC 3012 | A103413 | FW8 | Low voltage AC (<1kV) | Urban | - fuse (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 190905 PM10299503 | 20200104JEM_01 | Krone LV 3 phase isolator burnt out
426 | Jamena 19/30 | Jamena | 29/12/2019 | 0.26597 | -37.6483 | 144.9343 | 52 GLENELG STREET, COOLAROO VIC 3048 | A039091 | BDVCO | 66kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 191103 PM10299555 | 20191229JEM_01 | Pole failure at stay eyebolt location causing clashing and a small grass fire
427 | Jamena 19/31 | Jamena | 30/12/2019 | 0.5 | -37.7808 | 144.8722 | 12 HAMPSTEAD ROAD, MAIDSTONE VIC 3012 | A025397 | BY14 | 22kV AC | Urban | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Extreme | 3.5 | 0.7 | 191278 PM10299593 | 20191230JEM_01 | Flashover on isolator pole, cause unknown
428 | Jamena 19/32 | Jamena | 31/12/2019 | 0.20833 | -37.778 | 144.885 | 131 ROSAMOND ROAD, MAIDSTONE VIC 3012 | A009426 | BYES | 66kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 191384 PM10299615 | 20200103JEM_09 | Pole top / crossarm fire
429 | Jamena 19/33 | Jamena | 31/12/2019 | 0.50833 | -37.6579 | 144.9562 | 48 JESICA ROAD, CAMPBELLFIELD VIC 3061 | A013782 | ST23 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | PM10299671 | 20200103JEM_04 | Pole top / crossarm fire
430 | Jamena 19/34 | Jamena | 31/12/2019 | 0.46319 | -37.7408 | 144.9057 | 32 KERFERD STREET, ESSENDON NORTH VIC 3041 | A084805 | ES26 | 11kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 191441 | 20200103JEM_14 | Pole top / crossarm fire
431 | Jamena 19/35 | Jamena | 31/12/2019 | 0.43681 | -37.8593 | 144.8867 | 83 BAYVIEW STREET, WILLIAMSTOWN VIC 3016 | A071392 | NT15 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 191438 PM10299599 | 20200103JEM_11 | Pole top / crossarm fire
432 | Jamena 19/36 | Jamena | 31/12/2019 | 0.32361 | -37.7958 | 144.8849 | 88 ELEANOR STREET, FOOTSCRAY VIC 3011 | A064748 | FW8 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 191418 PM10299619 | 20200103JEM_12 | Pole top / crossarm fire
433 | Jamena 19/37 | Jamena | 31/12/2019 | 0.28056 | -37.7331 | 144.8809 | 561 KEILOR ROAD, NIDDRIE VIC 3042 | A057021 | AW7 | 22kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 191408 PM10299568 | 20200103JEM_05 | Pole top / crossarm fire
434 | Jamena 19/38 | Jamena | 31/12/2019 | 0.25139 | -37.7091 | 144.9091 | 34 WILLIAM STREET, GLENROY VIC 3046 | A092669 | PV14 | 11kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 191398 PM10299570 PM10299611 | 20200103JEM_13 | Pole top / crossarm fire
435 | Jamena 19/39 | Jamena | 31/12/2019 | 0.21875 | -37.7953 | 144.9043 | 1 MOORE STREET, FOOTSCRAY VIC 3011 | A039191 | FE6 | 22kV AC | Urban | - fuse (powder filled) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 191392 PM10299617 | 20200103JEM_08 | HV fuse units candling
436 | Jamena 19/40 | Jamena | 31/12/2019 | 0.16806 | -37.746 | 144.8721 | 53 RACHELLE ROAD, KEILOR EAST VIC 3033 | A058363 | AW6 | 22kV AC | Urban | - fuse (powder filled) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 191377 PM10299612 PM10299613 | 20200103JEM_01 | HV fuse units candling
437 | Jamena 19/41 | Jamena | 31/12/2019 | 0.21597 | -37.7029 | 144.9588 | 13 SAGES ROAD, GLENROY VIC 3046 | A035908 | CN4 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 191389 PM10299620 | 20200103JEM_06 | Pole top / crossarm fire
438 | Jamena 19/42 | Jamena | 31/12/2019 | 0.19722 | -37.6431 | 144.8866 | 58 GREENVALE DRIVE, GREENVALE VIC 3059 | A041739 | COO21 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 191382 PM10299569 | 20200103JEM_02 | Pole top / crossarm fire
439 | Jamena 19/43 | Jamena | 31/12/2019 | 0.18611 | -37.7485 | 144.8609 | 28 AMIS CRESCENT, KEILOR EAST VIC 3033 | A095620 | BY11 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 191379 PM10299614 | 20200103JEM_03 | Pole top / crossarm fire
440 | Jamena 19/44 | Jamena | 2020-01-01 | 43831.9042 | -37.6614 | 144.9211 | 19 TAGGERTY CRESCENT, MEADOW HEIGHTS VIC 3048 | A037360 | BD14 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | PM10299635 | 20200103JEM_07 | Pole top / crossarm fire
441 | Jamena 19/45 | Jamena | 2020-05-01 | 43835.434 | -37.7261 | 144.9513 | 106-108 BAKERS ROAD, COBURG NORTH VIC 3058 | A031277 | CN5 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-Moderate | 0.2 | 0.04 | PM10299668 | 20200106JEM_02 | Pole top / crossarm fire
442 | Jamena 19/46 | Jamena | 2020-05-01 | 43835.5 | -37.704 | 145.0099 | 1007 HIGH STREET, RESERVOIR VIC 3073 | A034223 | TT10 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-Moderate | 0.2 | 0.04 | PM10299669 | 20200106JEM_03 | Pole top / crossarm fire
443 | Jamena 19/47 | Jamena | 2020-05-01 | 43835.5042 | -37.7476 | 144.8797 | 56 ROSEHILL ROAD, KEILOR EAST VIC 3033 | A093373 | KTSES | 66kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-Moderate | 0.2 | 0.04 | PM10299667 | 20200105JEM_01 | Pole top / crossarm fire
444 | Jamena 19/48 | Jamena | 2020-05-01 | 43835.6215 | -37.8285 | 144.892 | 21 SIMCOCK AVENUE, SPOTSWOOD VIC 3015 | A058929 | YVE12 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-Moderate | 0.2 | 0.04 | PM10299674 | 20200106JEM_01 | Pole top / crossarm fire
445 | Jamena 19/49 | Jamena | 2020-07-01 | 43837.1007 | -37.6107 | 144.9279 | 127 BRIDGEWATER ROAD, CRAIGIEBURN VIC 3064 | A022053 | ST32 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | PM10299716 | 20200107JEM_02 | Pole top / crossarm fire
446 | Jamena 19/50 | Jamena | 2020-07-01 | 43837.7847 | -37.7323 | 144.9457 | 281 GAFFNEY STREET, PASCOE VALE VIC 3044 | A092906 | CS12 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | PM10299710 | 20200107JEM_04 | Pole top / crossarm fire
447 | Jamena 19/51 | Jamena | 2020-10-01 | 43840.9208 | -37.731 | 144.9508 | 10 MARION STREET, COBURG NORTH VIC 3058 | A044166 | CS12 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | PM10299769 | 20200110JEM_02 | Pole top / crossarm fire
448 | Jamena 19/52 | Jamena | 20/01/2020 | 43850.7833 | -37.7056 | 145.0093 | 1 HOBBS CRESCENT, RESERVOIR VIC 3073 | A018624 | TT10 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-Moderate | 0.2 | 0.04 | PM10300043 | 20200120JEM_01 | Pole top / crossarm fire
449 | Jamena 19/53 | Jamena | 21/01/2020 | 43851.4243 | -37.7032 | 145.0087 | 3 GELLIBRAND CRESCENT, RESERVOIR VIC 3073 | A027736 | TT11 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-Moderate | 0.2 | 0.04 | PM10300054 PM10300057 | 20200121JEM_01 | Pole top / crossarm fire
450 | Jamena 19/54 | Jamena | 26/01/2020 | 43856.3869 | -37.7317 | 145.0846 | 3 ANNE CT, YALLAMBIE VIC 3085 (LOWER PLENTY ROAD, OPPOSITE MARTINS LN, VIEWBANK VIC 3084) | A130238 | NH2 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | PM10300155 | 20200824JEM_01 | Pole top / crossarm fire
451 | Jamena 19/55 | Jamena | 2020-12-02 | 43856.4286 | -37.6626 | 144.957 | 58 GLENBARRY RD, CAMPBELLFIELD VIC 3061 | A033201 | BD13 | 22kV AC | Urban | - underground cable | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-Moderate | 0.2 | 0.04 | PM10300769 | 20200824JEM_02 | Raychem CHP termination burnt due to unknown cause
452 | Jamena 19/56 | Jamena | 19/02/2020 | 0.58542 | -37.7188 | 144.9779 | 13 IMAROO STREET, FAWKNER VIC 3060 (MERRI CREEK TRAIL, FAWKNER VIC 3060) | A022864 | CN10 | 22kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | PM10300886 | 20200305JEM_02 | Pole partially burnt due to contact by bare 22kV conductor.
453 | Jamena 19/57 | Jamena | 23/02/2020 | 0.47917 | -37.5683 | 144.6707 | 115-131 NAPIER STREET, DIGGERS REST VIC 3427 | A054571 | SBY13 | 22kV AC | Rural Short | - fuse (boric acid) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | PM10300896 | 20200223JEM_01 | Boric Acid fuse candling ignited a small grass fire.
454 | Jamena 19/58 | Jamena | 13/03/2020 | 0.80833 | -37.7567 | 144.8611 | 8 ORLEANS ROAD, AVONDALE HEIGHTS VIC 3034 | A025217 | BY14 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | PM10301501 | 20200403JEM_02 | Pole top / crossarm fire
455 | Jamena 19/59 | Jamena | 13/03/2020 | 0.89931 | -37.7868 | 144.8793 | 68 BALLARAT ROAD, MAIDSTONE VIC 3012 | A035670 | BY12 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | PM10301502 | 20200403JEM_03 | Pole top / crossarm fire
456 | Jamena 19/60 | Jamena | 2020-07-04 | 0.70833 | -37.8007 | 144.9048 | 55-59 HOPKINS STREET, FOOTSCRAY VIC 3011 | A090499 | FE6 | Low voltage AC (<1kV) | Urban | - fuse (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-Moderate | 0.2 | 0.04 | PM10302388 | 20200505JEM_02 | Krone LV 3 phase isolator burnt out
457 | Jamena 19/61 | Jamena | 2020-09-04 | 0.78194 | -37.6344 | 144.8172 | 5 BLACKWELLS LANE, BULLA VIC 3428 | A123600 | COO11 | 22kV AC | Rural Short | - fuse (boric acid) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-Moderate | 0.2 | 0.92 | PM10302469 | 20200422JEM_01 | Candling BA fuse observed by network operator.
458 | Jamena 19/62 | Jamena | 2020-12-04 | 0.12917 | -37.7514 | 144.9668 | 11 THE GROVE, COBURG VIC 3058 | A067165 | CS5 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-Moderate | 0.2 | 0.04 | PM10302522 | 20200420JEM_01 | Pole top / crossarm fire
459 | Jamena 19/63 | Jamena | 2020-03-06 | 0.26736 | -37.7156 | 144.8618 | 5 BEVERAGE DRIVE, TULLAMARINE VIC 3043 | A085908 | AW3 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | Report 20200603JEM_01 | 20200603JEM_01 | MFB report council tree on wires sparking.
460 | CitiPower 19/20 | CitiPower | 16/07/2019 | 0.78056 | -37.7948 | 145.0638 | 1122 BURKE ROAD,BALWYN NORTH,VIC,3104 | 30167864 | L022 | Low voltage AC (<1kV) | Urban | - luminaires (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0007572 | 20190724PWA_04 | MFB reported a pole fire at the above incident location. Upon crew arrival, they reported a faulty 150W public lighting head unit which had caught on fire. There was no reported injuries or ground fire. Crew organized a public lighting head unit to be replaced the next day
461 | CitiPower 19/21 | CitiPower | 2019-12-08 | 0.76875 | -37.8416 | 144.9761 | 26 QUEENS ROAD MELBOURNE 3004 | 30213189 | SK019 | Low voltage AC (<1kV) | CBD | - luminaires (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0008158 | 20190912PWA_01 | Report of lantern fire at incident location. MFB attended and extinguished pole fire. There was no ground fir, no reported injuries or third party property damage.
462 | CitiPower 19/22 | CitiPower | 22/08/2019 | 0.88472 | -37.8427 | 144.9878 | 32 Nicholson St, South Yarra VIC 3141 | 30216014 | BC024 | Low voltage AC (<1kV) | Urban | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0007972 | 20190827PWA_02 | Resident reported main wire on the ground and part on the tree at the above incident location. Was small fire in tree, now just smoldering. There was no ground fire, no reported injuries or third party property damage.
463 | CitiPower 19/23 | CitiPower | 18/10/2019 | 0.65625 | -37.7611 | 144.9967 | Cnr Spencer Street & Woolton Avenue, Thornbury | 30184890 | NC013 | 11kV AC | Urban | - overhead conductor (covered uninsulated) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0008633 | 20191106PWA_01 | Resident reported a flash of electricity that was seen & heard shooting down to footpath on the pole located on the Cnr Spencer Street & Woolton Avenue, Thornbury . Attending crew found connection had parted from gas switch.
464 | CitiPower 19/24 | CitiPower | 20/12/2019 | 0.79861 | -37.7555 | 145.0083 | 76 Collins St, Thornbury VIC 3071 | 30194938 | NC004 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | INC-0009214 | 20191223PWA_07 | Passerby reported pole fire, corner of Tharrat St and Collins. Pole dropping molten material onto the ground. Started a fire but is out now. On arrival Crew advise connection box overheated. Debris form overheated box has ignited a small grass fire (6 by 4m approx.). The fire self extinguished.
465 | CitiPower 19/25 | CitiPower | 20/12/2019 | 0.75694 | -37.8205 | 145.0996 | 301 Mont Albert Rd, Surrey Hills VIC 3127 | 30177913 | RD014 | Low voltage AC (<1kV) | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | INC-0009215 | 20191223PWA_08 | Customer reported wire is sparking and dripping molten bits to the ground and causing grass fires. Crew advise small burn marks on ground less than size of a dollar coin. Smoldering grass due to hot debris from overheated IPC. There was no reported injuries or third party property damage.
466 | CitiPower 19/26 | CitiPower | 24/12/2019 | 0.92708 | -37.8346 | 145.0507 | 35 PLEASANT ROAD,HAWTHORN EAST,VIC,3123 | 30201569 | CL011 | Low voltage AC (<1kV) | Urban | - luminaires (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009225 | 20191230PWA_03 | Report received of street light on fire. Crew attended to find public light lantern had caught fire and was burnt out. Fire had self extinguished. No ground fire.
467 | CitiPower 19/27 | CitiPower | 30/12/2019 | 0.70417 | -37.8048 | 145.0632 | 7 Wills St Balwyn North 3104 | 30166282 | L001 | Low voltage AC (<1kV) | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Extreme | 3.5 | 0.7 | INC-0009238 | 20191231PWA_08 | Customer reported a wire resting in the tree out the front of property and that caused a fire at property all the way up to front door. On arrival crew reported that an overhanging branch made contact with LV cables causing LV phases to make contact. This caused sparking as result the sparks fell upon the customers front lawn. The resulting fire was approx. 8 x 5m. There was no reported injuries.
468 | CitiPower 19/28 | CitiPower | 30/12/2019 | 0.82569 | -37.7841 | 145.0791 | opposite 5 Highview Rd Balwyn North 3104 | 30180008 | WD011 | 11kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Extreme | 3.5 | 0.7 | INC-0009240 | 20191231PWA_10 | Customer reported hearing 2 loud bangs at the time the power flickered then went out. Crew reported a tree branch made contact with the HV conductor causing the phases to make contact causing sparks to fall resulting in a 1x1m ground fire. There was no reported injuries
469 | CitiPower 19/29 | CitiPower | 31/12/2019 | 0.19722 | -37.8626 | 144.9859 | 56 Argyle St. St Kilda, 3182 | 30211577 | SK009 | 11kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009253 | 20200102PWA_09 | Following report of pole fire, on arrival crew found cross-arm mounted with HV isolators has broken due to cross-arm fire. There was no ground fire, no reported injuries or third party property damage.
470 | CitiPower 19/30 | CitiPower | 31/12/2019 | 0.2875 | -37.752 | 144.9348 | 546 Moreland Rd, Brunswick West VIC 3055 | 30157029 | NS010 | 11kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009256 | 20200103PWA_02 | Report recieved of a crossarm fire at incident location. On arrival crew found HV crossarm burnt through causing conductors to clash. There was reports of HVI at several premises There was no ground fire or injuries.
471 | CitiPower 19/31 | CitiPower | 31/12/2019 | 0.20833 | -37.8647 | 145.0003 | 49 HOTHAM STREET, ST KILDA EAST, 3183. | 30218625 | AR-BC | 66kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009245 | 20200102PWA_02 | Vic fire reported pole fire in Hotham St. outside BC Zone Substation. Crew advise pole fire due to tracking, fire brigade on site have extinguished fire. There was no ground fire, no reported injuries or third party property damage.
472 | CitiPower 19/32 | CitiPower | 31/12/2019 | 0.19444 | -37.8636 | 145.0166 | 5 FINDON AVENUE,CAULFIELD NORTH,VIC,3161 | 30219923 | AR004 | 11kV AC | Urban | - overhead conductor (bare; copper) | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009242 | 20191231PWA_12 | Report received of a pole being hit by lightning at the incident location. On arrival the crew found end burnt off crossarm and conductors on ground. There was a possibility of HV injection. There was no ground fire, no reported injuries
473 | CitiPower 19/33 | CitiPower | 31/12/2019 | 0.20972 | -37.8319 | 144.9511 | 146-148 Montegue South Melbourne, 3205. | 30167035 | MG009 | 11kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009241 | 20191231PWA_11 | Report received of conductors down at incident location. On arrival crew advised of pole fire, road side the high voltage isolator has burnt of at its securing bolt and half the cross-arm has broken off. There was no ground fire, no reported injuries or third party property damage.
474 | CitiPower 19/34 | CitiPower | 2020-03-01 | 0.87708 | -37.8363 | 145.0626 | 411 Camberwell Road, Camberwell, VIC 3124 | 30174779 | CL011 | Low voltage AC (<1kV) | Urban | - overhead service conductor (residential) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0009273 | 20200107PWA_06 | MFB reported wire down and ground fire in front of the above incident location. On arrival, crew noticed the ground fire was already put out and the found a broken tree branch had fallen onto an Low Voltage (LV) overhead service cable. There was a ground fire (6x4mts) in customers front yard. There was no reported injuries and minor damage to customers side fence.
475 | CitiPower 19/35 | CitiPower | 15/01/2020 | 0.45347 | -37.8352 | 144.9589 | 181 Cecil Street South Melbourne 3205 | 30174143 | AP006 | Low voltage AC (<1kV) | Urban | - connector / termination | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009357 | 20200117PWA_06 | Customer report of powerline down, caused ground fire, MFB onsite. Crew found blue phase LV conductor on ground. Ground fire of approx. 250mm2 There was no reported injuries or property damage.
476 | CitiPower 19/36 | CitiPower | 15/01/2020 | 0.71458 | -37.844 | 144.943 | 38 Rouse Street, Port Melbourne, VIC 3207 | 30203431 | AP003 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0009351 | 20200117PWA_02 | Customer reported fire/arching on pole at the above incident location. On arrival, crew noticed LV Crom Box was damaged and melted. There was no ground fire, no injuries or third party damage.
477 | CitiPower 19/37 | CitiPower | 21/01/2020 | 0.7125 | -37.8562 | 144.9903 | 135 Albert St, Windsor VIC 3181 | 30217885 | BC020 | Low voltage AC (<1kV) | Urban | - connector / termination | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0009410 | 20200122PWA_08 | MFB reported pole fire at the above incident location. On arrival, the crew found an Low Voltage (LV) cable head pole conductor tie (red phase) had broken due to faulty Insulation Piercing Connector (IPC) overheating, caught on fire. There was a minor fire on the pole at the point of IPC but no ground fire. There was no third party damaged and no reported injuries.
478 | CitiPower 19/38 | CitiPower | 30/01/2020 | 0.69444 | -37.8189 | 145.0089 | 103 Palmer St, Richmond VIC 3121. Pole LIS 6450 out front of incident address. | 30195068 | NR002 | Low voltage AC (<1kV) | Urban | - connector / termination | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0009537 | 20200207PWA_05 | Report received of arcing and sparking and small ground fire at incident location. On arrival crew found that a D connection had overheated showering hot debris igniting grass below. There was no reported injuries or third party property damage.
479 | CitiPower 19/39 | CitiPower | 13/03/2020 | 0.86042 | -37.7751 | 144.944 | 469 Brunswick Road, West Brunswick | 30159559 | WB013 | 6.6kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0010152 | 20200316PWA_02 | Customer reporting pole sparking and glowing bright red, coming from the top of the pole. He also thinks xarm is broken. On arrival, faults crew found that a HV cross arm on pole no 46899 had burnt through. There was suspected HVI, test by LEI found no evidence of HVI. There was no ground fire, no reported injuries or third party property damage.
480 | CitiPower 19/40 | CitiPower | 29/04/2020 | 0.45833 | -37.7673 | 145.0082 | 42 Kellet Street, Northcote, 3070. (Southwest corner Kellet & Wales Streets). | 30192711 | NC006 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0010471 | 20200430PWA_02 | Report retrieved of pole fire at incident location. On arrival crew found an overheated Krone box had caught fire. There was no ground fire, no reported injuries or third party property damage.
481 | CitiPower 19/41 | CitiPower | 21/05/2020 | 0.77778 | -37.8557 | 145.0029 | 8 Craven St, PRAHRAN | 30169029 | BC013 | Low voltage AC (<1kV) | Urban | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0010716 | 20200522PWA_01 | Report received of pole fire at incident location. On arrival crew found a LV bridge had overheated and insulation had caught fire. There was no ground fire, no reported injuries or third party property damage.
482 | CitiPower 19/42 | CitiPower | 23/05/2020 | 0.20139 | -37.7656 | 144.9492 | Outside 70 Pearson St, West Brunswick | 30155687 | WB002 | Low voltage AC (<1kV) | Urban | - luminaires (minor road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0010748 | 20200525PWA_06 | Customer reported street light on cnr. of Pearson St. and Victoria St. on fire at top of pole. Small flames and debris falling to ground. MFB attended. There was no ground fire, no reported injuries or third party property damage.
483 | CitiPower 19/43 | CitiPower | 2019-04-07 | 0.84167 | -37.8312 | 145.0934 | 16 ARUNDEL CRESCENT,SURREY HILLS,VIC,3127 | 30175594 | RD005 | Low voltage AC (<1kV) | Urban | - overhead service conductor (residential) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0011588 | 20200908PWA_03 | Service wire has broken away from the house and caught fire. Attending crew replaced service cable.
484 | Ausnet 19/20 | Ausnet | 2019-03-07 | 43649.8222 | -38.0382 | 145.2548 | 1 JEFFREY STREET, HAMPTON PARK VIC 3976 | 505164 | HPK23 | Low voltage AC (<1kV) | URBAN | - lamps (minor road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | E0022303 | 20190708SPN_05 | Street light on pole LIS505164 caught fire and burnt. Fire likely resulted from failed ignitor or PE Cell.
485 | Ausnet 19/21 | Ausnet | 2019-04-07 | 43650.9437 | -37.6453 | 144.9756 | 490 COOPER STREET, EPPING VIC 3076 | 5712445 | EPG33 | Low voltage AC (<1kV) | URBAN | - connection box | three phase | Otherwise started by a distribution system | HBRA only | 1 | NO FORECAST | 0.1 | 0.1 | E0022366 | 20190708SPN_04 | Fuse box failure believed to be due to poor connections
486 | Ausnet 19/22 | Ausnet | 2019-06-07 | 43652.8194 | -38.6722 | 146.6926 | 15 VICTORIA STREET, PORT ALBERT VIC 3971 | 2624442 | FTR23 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | E0022445 | 20190708SPN_02 | Candled EDO HV Fuse
487 | Ausnet 19/23 | Ausnet | 2019-07-07 | 43653.8174 | -36.338 | 146.3036 | 1 WARATAH DRIVE, WANGARATTA VIC 3677 | 5119925 | WN2 | 22kV AC | RURAL LONG | - surge diverter | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | E0022450 | 20190708SPN_01 | Caused by lightning
488 | Ausnet 19/24 | Ausnet | 2019-09-07 | 43655.0625 | -37.9487 | 145.4816 | 100 PATERNOSTER ROAD, COCKATOO VIC 3781 | 400246 | BGE12 | 22kV AC | RURAL SHORT | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | NO FORECAST | 0.1 | 0.46 | E0022620 | 20190809SPN_02 | Candled Boric Acid HV fuse
489 | Ausnet 19/25 | Ausnet | 2019-09-07 | 43655.25 | -38.0429 | 146.0092 | 560 MCDOUGAL ROAD, NEERIM SOUTH VIC 3831 | 2706750 | WGL24 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | HBRA only | 1 | NO FORECAST | 0.1 | 0.1 | E0022509 | 20190710SPN_02 | Boric Acid HV fuse has candled
490 | Ausnet 19/26 | Ausnet | 2019-10-07 | 43656.9458 | -38.0441 | 145.3304 | 107 GOLF LINKS ROAD, BERWICK VIC 3806 | 2601658157 | CLN14 | 22kV AC | RURAL SHORT | - switch (any other type) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | E0022644 | 20190809SPN_05 | Birds nest found on manual gas switch. Flashover has occurred and damaged the supply side bushings of the switch. Switch replaced and animal proofing to be installed.
491 | Ausnet 19/27 | Ausnet | 2019-11-07 | 43657.1424 | -37.7612 | 145.3544 | 2 ANDERSON STREET, LILYDALE VIC 3140 | 1008057 | LDL12 | 22kV AC | URBAN | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | E0022634 | 20190809SPN_03 | A Dead tree failed just above ground level where there was significant decay and the tip contacted the outside HV conductor where it smouldered for a while before it broke at the point of contact and ended up resting on the outer 2 phases of the LV. No evidence of ground fire. There was strong wind and heavy rain at the time of the incident. There was no visible evidence of fire on the assets, conductor or ground as a result of this incident. The tree was outside the clearance space with the trunk located approx. 4m from the nearest conductor. The tree showed some limb damage but nothing was on site at the time of the investigation. The tree was last inspected on 16/01/17 and was not identified as hazardous at the time. However, the investigation has concluded the dead tree should have been identified by the Assessor as a hazard and he has now been made aware of this error.
492 | Ausnet 19/28 | Ausnet | 2019-12-07 | 43658.9799 | -37.7089 | 145.051 | 70 GRANGE BOULEVARD, BUNDOORA VIC 3083 | 906948 | WT9 | Low voltage AC (<1kV) | URBAN | - lamps (major road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | E0022802 | 20190717SPN_01 | 250W HPS street light has failed and caught fire. Investigation concluded the fire originated at the terminal block within the luminaire as a result of an unknown failure.
493 | Ausnet 19/29 | Ausnet | 15/07/2019 | 43661.375 | -37.8037 | 145.3057 | 12 TENNYSON AVENUE, KILSYTH VIC 3137 | 1005921 | CYN13 | 22kV AC | URBAN | - switch (disconnector/isolator) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | E0022832 | 20190717SPN_03 | The centre phase bushing of the manual gas switch has failed resulting in fire. The fire was contained on the pole top and there was no evidence of ground fire. The investigation was inconclusive and the exact cause of the bushing failure and subsequent fire is unknown at this time.
494 | Ausnet 19/30 | Ausnet | 19/07/2019 | 43665.3597 | -37.8469 | 145.2219 | 743 BORONIA ROAD, WANTIRNA VIC 3152 | 5625514 | BRA11 | Low voltage AC (<1kV) | URBAN | - lamps (major road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | E0023220 | 20190722SPN_03 | Investigation concluded that the igniter appears to have failed resulting in the street light catching fire. No evidence of ground fire
495 | Ausnet 19/31 | Ausnet | 23/07/2019 | 43669.4181 | -37.8943 | 145.4168 | 89 FAIRY DELL ROAD, MONBULK VIC 3793 | 1304731 | BGE24 | 22kV AC | RURAL SHORT | - fuse (boric acid) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | NO FORECAST | 0.1 | 0.46 | E0023367 | 20190809SPN_04 | Candled BA HV fuse. No evidence of ground fire
496 | Ausnet 19/32 | Ausnet | 28/07/2019 | 43674.7917 | -37.6829 | 145.1142 | 257 PLENTY RIVER DRIVE, GREENSBOROUGH VIC 3088 | 5811828 | ELM31 | Low voltage AC (<1kV) | URBAN | - lamps (major road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | E0023631 | 20190809SPN_06 | A faulty igniter appears to be the likely cause for the luminaire failure and subsequent fire
497 | Ausnet 19/33 | Ausnet | 13/08/2019 | 43690.4792 | -37.9315 | 145.5571 | 2904 GEMBROOK-LAUNCHING PLACE ROAD, GEMBROOK VIC 3783 | 416465 | OFR23 | Low voltage AC (<1kV) | RURAL LONG | - connection box | three phase | Otherwise started by a distribution system | HBRA only | 1 | NO FORECAST | 0.1 | 0.1 | E0024924 | 20190821SPN_05 | LV fuse box on pole caught fire. A suspected low voltage loose service cable connection within the fused mains box causing it to fail and ignite as a result. The fire was contained within the box only and there was no damage to pole and no evidence of ground fire.
498 | Ausnet 19/34 | Ausnet | 15/08/2019 | 43692.4167 | -37.8168 | 145.3259 | 56-72 CANTERBURY ROAD, MONTROSE VIC 3765 | 1005239 | CYN21 | 22kV AC | URBAN | - fuse (powder filled) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | E0025012 | 20190821SPN_06 | Fuse appears to have been damaged, allowing water to enter the fuse element resulting in fuse candling.
499 | Ausnet 19/35 | Ausnet | 19/08/2019 | 43696.4979 | -38.3996 | 145.5374 | 1395 BASS HIGHWAY, GRANTVILLE VIC 3984 | 2802989 | LLG13 | Low voltage AC (<1kV) | RURAL SHORT | - connection box | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | NO FORECAST | 0.1 | 0.46 | E0025162 | 20190821SPN_07 | A faults crew was called to a pole fire and, upon arrival, the crew found an FOLCB that had caught fire. No evidence of ground fire. The FOLCB was completely destroyed and it was not possible to determine the cause of the failure and subsequent fire due to the amount of damage. The FOLCB had melted and molten plastic fell to the ground but did not cause a ground fire as conditions were very wet.
500 | Ausnet 19/36 | Ausnet | 23/08/2019 | 43700.6347 | -38.5092 | 145.2923 | 3 STRADBROKE CRESCENT, SURF BEACH VIC 3922 | 2809385 | WGI32 | Low voltage AC (<1kV) | RURAL SHORT | - lamps (major road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | E0025373 | 20190917SPN_01 | Upon arrival, the fault crew identified the ground at the base of the pole seemed to be smoking and there was a small burn mark on the ground at the base of the pole. The grass around the pole was brown. The ground was smouldering but there was no flame. The concrete pole was live when the fault crew arrived. Further investigation identified that the connections at the street light had burnt and the neutral connection was burnt off in the junction box both as a result of corrosion. It appears the pole had become live as a result of the active conductor supplying the light in the junction box and the light bracket.
501 | Ausnet 19/37 | Ausnet | 30/08/2019 | 43707.7708 | -37.9502 | 146.9518 | 459 MEWBURN PARK ROAD, MAFFRA VIC 3860 | 2515178 | MFA22 | 22kV AC | RURAL LONG | - fuse (boric acid) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | E0025785 | 20190903SPN_01 | BA HV Fuse has candled. No evidence of ground fire or damage to pole. Candled BA HV fuse replaced with new and supply restored
502 | Ausnet 19/38 | Ausnet | 2019-04-09 | 43712.2708 | -37.5082 | 148.1365 | 415 TIMBARRA ROAD, BUCHAN VIC 3885 | 1904854 | BDL41 | 12.7kV AC (SWER) | RURAL LONG | - fuse (EDO fuse) | single wire earth return (SWER) | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | NO FORECAST | 0.1 | 0.46 | E0025909 | 20190917SPN_04 | Candled 5k EDO SWER Fuse
503 | Ausnet 19/39 | Ausnet | 2019-04-09 | 43712.3611 | -38.4779 | 145.9275 | 29 BEGG STREET, LEONGATHA VIC 3953 | 2003532 | LGA23 | 22kV AC | RURAL LONG | - fuse (boric acid) | three phase | Otherwise started by a distribution system | HBRA only | 1 | NO FORECAST | 0.1 | 0.1 | E0025906 | 20190917SPN_03 | Candled 6k BA HV Fuse
504 | Ausnet 19/40 | Ausnet | 2019-07-09 | 43715.859 | -38.5114 | 145.2974 | BRUCE AVENUE, SURF BEACH VIC 3922 | 2809410 | WGI32 | 22kV AC | RURAL SHORT | - dropper / bridge | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | E0026059 | 20190917SPN_07 | Pole fire reported on transformer pole. Pole is a termination pole with a pole mounted transformer installed on the supply side of the pole. HV fuses were installed on the back of the pole with the centre phase connection between the fuse and the over head going over the top of the steel termination arm. Upon investigation, it appears that the centre phase dropper cable failed at the tail, coming to rest on the term arm. The line and substation fuses failed to operate and the dropper/crossarm continued to be back-fed through the transformer resulting in a pole top fire. Fire was contained at the pole top and did not make it to the ground as it was a particularly wet night.
505 | Ausnet 19/41 | Ausnet | 2019-11-09 | 43719.2743 | -37.5635 | 145.5039 | 1059 MYERS CREEK ROAD, TOOLANGI VIC 3777 | 1400989 | WYK24 | 22kV AC | RURAL SHORT | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within electric line construction area | 19.8 | NO FORECAST | 0.1 | 1.98 | E0026200 | 20190918SPN_01 | 6k BA HV fuse has candled
506 | Ausnet 19/42 | Ausnet | 2019-01-10 | 43739.0333 | -37.9349 | 145.5993 | 620 BEENAK EAST ROAD, GEMBROOK VIC 3783 | 417099 | OFR23 | 22kV AC | RURAL LONG | - overhead conductor (bare; steel) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | NO FORECAST | 0.1 | 0.1 | E0027058 | 20191015SPN_01 | Tree has failed at the rootball and fallen onto and bringing down the O/H HV conductors resulting in a ground fire. The tree in question was located 25m from the HV line and uprooted, falling perpendicular to and over the line. There were no externally visible signs of potential hazard so this failure could not have been predicted. There are thousands of similar trees adjacent to this spur, all in reasonably good condition. The span was last inspected on the 12th of June 2019 and last cleared on the 27th of September 2018.
507 | Ausnet 19/43 | Ausnet | 2019-01-10 | 43739.5938 | -36.1471 | 146.9431 | WODONGA SALEYARDS, 120 WHYTES ROAD, BANDIANA VIC 3691 | 5209508 | WOTS25 | 22kV AC | RURAL SHORT | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | NO FORECAST | 0.1 | 0.46 | E0027114 | 20191015SPN_02 | Container lift operator had loaded a container on the Container Lift and was waiting for a truck to arrive to load it on. He had his lunch with him in the cabin of the container lift and decided to drive to where his car was parked in the shade to have lunch while he was waiting. He reversed the container lift along the internal roadway and came into contact with the overhead conductor. He heard a sparking noise initially followed by a loud bang and saw a flash out of the corner of his eye. He stopped the Container lift when he noticed conductors on the ground and spot fires in the direction he was travelling. He drove the Container lift forward about 6-10m away from the fallen power lines, exited the Container Lift with a chemical powder fire extinguisher and walked back to extinguish the fire before waiting for another worker and his supervisor to arrive. They inspected the Container Lift and proceeded to drive it away to load the truck. They were not able to continue working though due having no power at the site to operate the weighbridge. The Container lift had been moved and continued to be used after the incident and had a container slung under the yellow platform at the time of the incident. There were flash marks visible on the mast of the Container Lift at a number of sites. As the Container lift had been moved, the height was simulated and the mast of the Contain Lift raised into the height they believed it to have been at the time of the incident. Highest flash marks were measures at 7.2m and the lowest at 6.5m. Two phases of the three conductors had broken and fallen to the ground. The third remaining conductor had some discolouration from the flash but appeared okay. The height of the remaining conductor over the road was measured at 5.9m after the incident. Upon completion of repairs the conductors were measured at 7.9m above ground. There was no damage to the poles or insulators either side of the incident.
508 | Ausnet 19/44 | Ausnet | 2019-06-10 | 43744.5472 | -37.8741 | 147.8584 | 705 METUNG ROAD, METUNG VIC 3904 | 1901172 | BDL6 | 22kV AC | RURAL SHORT | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0027380 | 20191010SPN_01 | Conductor has broken midspan resulting in ground fire (approx 1m x 3m). Upon further investigation corrosion was identified on the conductor which is believed to have cause the conductor to break during high winds experienced at the time of failure. Conductor repaired and supply restored. Follow up inspection organised to determine if corrosion present on the remaining O/H conductor.
509 | Ausnet 19/45 | Ausnet | 2019-07-10 | 43745.3875 | -37.2538 | 145.797 | 10 BACK EILDON ROAD, THORNTON VIC 3712 | 4711025 | RUBA12 | 22kV AC | RURAL LONG | - fuse (boric acid) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0027390 | 20191008SPN_01 | Fuse Candled: The top and bottom contact of the fuse carrier were still in place in the Unit. Fuses carrier had jammed closed and failed to dislodge once fuse link had operated. There was no fire on the ground.
510 | Ausnet 19/46 | Ausnet | 2019-07-10 | 43745.934 | -37.7533 | 145.2122 | 36 HODSON ROAD, WARRANDYTE VIC 3113 | 1206025 | RWN31 | Low voltage AC (<1kV) | RURAL SHORT | - underground service cable (residential) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0027449 | 20191010SPN_02 | 2 x 4 wire services caught fire in conduit on pole and burnt to FOLCB.
511 | Ausnet 19/47 | Ausnet | 2019-09-10 | 43747.3958 | -37.8512 | 148.0393 | PRINCES HWY, LAKE TYERS BEACH VIC 3909 | 1903088 | NLA34 | 22kV AC | RURAL SHORT | - fuse (boric acid) | three phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0027565 | 20191010SPN_03 | Candled HV Boric Acid Fuse
512 | Ausnet 19/48 | Ausnet | 16/10/2019 | 43754.375 | -38.5486 | 145.9438 | 18 KOONWARRA-INVERLOCH ROAD, KOONWARRA VIC 3954 | 2001276 | LGA14 | 22kV AC | RURAL LONG | - fuse (boric acid) | three phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0028034 | 20191017SPN_01 | It appears that a small branch (around 1m long) fell onto one phase of the HV and was gradually blown along the span resulting in the branch ending up approximately 160m from the nearest trees. The O/H conductors transpose from horizontal to vertical construction and, as the wires began to cross under one-another, the branch caused a phase to phase fault resulting in fuse candling when the fuse failed to operate correctly. No failed hazard Trees found during onsite visit. Three small gum branches less than 1m long found laying on ground in paddock under line with burn marks located approximately 160m from the nearest tree and 70m from LIS2001314 but no evidence of ground fire. This span was last inspected on 29/05/2019 with no hazardous trees identified and all outside clearance space.
513 | Ausnet 19/49 | Ausnet | 23/10/2019 | 43761.041 | -38.5335 | 146.59 | 104 INGLES ROAD, DEVON NORTH VIC 3971 | 2624667 | FTR12 | Low voltage AC (<1kV) | RURAL LONG | - connection box | two phase | Otherwise started by a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | E0028467 | 20191024SPN_01 | FOLCB burnt due to wildlife shorting to ground .
514 | Ausnet 19/50 | Ausnet | 24/10/2019 | 43762.5958 | -38.5276 | 145.4466 | 3170 BASS HIGHWAY, ANDERSON VIC 3995 | 2800755 | WGI23 | 22kV AC | RURAL SHORT | - surge diverter | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | VERY HIGH | 1 | 4.6 | E0028993 | 20191030SPN_01 | A surge diverter has failed at Voltage Regulator site during REFCL stress testing resulting in ground fire which stopped at and was contained by the concrete bund. CFA attended site to extinguish the fire. Damaged Voltage regulator removed from service and replaced with new. Surge diverters replaced and supply restored
515 | Ausnet 19/51 | Ausnet | 24/10/2019 | 43762.7792 | -37.9677 | 146.8672 | TAKUNUMA, 227 MCKINNONS ROAD, TINAMBA VIC 3859 | 2510389 | MFA22 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | E0028698 | 20191025SPN_01 | Candled 6k EDO HV Fuse
516 | Ausnet 19/52 | Ausnet | 25/10/2019 | 43763.7208 | -38.0319 | 145.4932 | 56 REYNOLDS ROAD, PAKENHAM VIC 3810 | 504298 | OFR23 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | E0028807 | 20191028SPN_02 | Candled Boric Acid HV fuse
517 | Ausnet 19/53 | Ausnet | 27/10/2019 | 43765.7083 | -36.2657 | 147.1002 | ENVYDALE, 96 HIBBERSON ROAD, HUON VIC 3695 | 5217174 | WOTS13 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0028829 | 20191029SPN_02 | Candled 6k BA HV Fuse
518 | Ausnet 19/54 | Ausnet | 29/10/2019 | 43767.2049 | -37.803 | 145.3445 | CAMBRIDGE ROAD, MOOROOLBARK VIC 3138 | 1001092 | CYN33 | 22kV AC | URBAN | - fuse (boric acid) | three phase | Otherwise started by a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | E0028907 | 20191029SPN_01 | Candled 25E BA HV Fuse. No evidence of ground fire
519 | Ausnet 19/55 | Ausnet | 2019-01-11 | 43770.6542 | -36.56 | 145.9661 | 126 WALLER STREET, BENALLA VIC 3672 | 3903114 | BN4 | 22kV AC | URBAN | - insulators | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | VERY HIGH | 1 | 0.2 | E0029286 | 20191107SPN_01 | Fault crew dispatched following feeder CB trip and, upon investigation, found a bird had contacted O/H HV conductors at the centre phase insulator on the pole, causing a flash over and starting a ground fire as it fell to ground. Fire self extinguished but Centre phase insulator damaged.
520 | Ausnet 19/56 | Ausnet | 2019-04-11 | 43773.9458 | -37.5925 | 145.0153 | 145 BOUNDARY ROAD, WOLLERT VIC 3750 | 599306 | EPG13 | 22kV AC | RURAL SHORT | - fuse (boric acid) | single phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0029369 | 20191107SPN_02 | Most probable cuase is incorrect installation. No photos or failed equipment was available for detailed investigations to confirm the root cause.
521 | Ausnet 19/57 | Ausnet | 2019-11-11 | 43780.4451 | -38.497 | 145.2577 | 161 SMITHS BEACH ROAD, SMITHS BEACH VIC 3922 | 2808411 | PHI12 | 22kV AC | RURAL SHORT | - fuse (boric acid) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | E0029949 | 20191111SPN_02 | Candled HV BA Fuse on spur tee-off. No evidence of ground fire.
522 | Ausnet 19/58 | Ausnet | 21/11/2019 | 43790.6042 | -38.138 | 146.7934 | ROSEDALE-HEYFIELD ROAD, ROSEDALE VIC 3847 | 2600780 | TGN41 | 22kV AC | RURAL LONG | - surge diverter | three phase | Started by lightning striking a distribution system or a part of a distribution system | HBRA only | 1 | VERY HIGH | 1 | 1 | E0030691 | 20191122SPN_04 | Blown surge arrester on pole 2600780 and started a grass fire.
523 | Ausnet 19/59 | Ausnet | 21/11/2019 | 43790.625 | -37.3686 | 145.0395 | 17 BADEN DRIVE, HEATHCOTE JUNCTION VIC 3758 | 912182 | KLO14 | 22kV AC | RURAL LONG | - overhead conductor (bare; all aluminium conductor) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | SEVERE | 2 | 9.2 | E0030725 | 20191125SPN_02 | Semi-mature swamp gum trunk failure (stem failure) in extreme winds making contact with conductors bringing one phase to ground. No obvious defects were identifiable so failure could not have been predicted.
524 | Ausnet 19/60 | Ausnet | 21/11/2019 | 43790.6667 | -37.803 | 145.3445 | 342 CAMBRIDGE ROAD, MONTROSE VIC 3765 | 1001092 | CYN33 | 22kV AC | URBAN | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | VERY HIGH | 1 | 1 | E0030712 | 20191125SPN_01 | Private decayed tree branch outside of vegetation clearance space failed.
525 | Ausnet 19/61 | Ausnet | 21/11/2019 | 43790.7646 | -38.1735 | 146.2871 | 63 NORTHERN AVENUE, NEWBOROUGH VIC 3825 | 2208258 | MOE13 | 22kV AC | RURAL SHORT | - pole (wood) | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | VERY HIGH | 1 | 0.2 | E0030656 | 20191122SPN_01 | Currently under investigation. Lightning appears to have struck pole
526 | Ausnet 19/62 | Ausnet | 21/11/2019 | 43790.7764 | -37.0571 | 145.8603 | MAINTONGOON ROAD, BONNIE DOON VIC 3720 | 3912765 | MSD2 | 22kV AC | RURAL LONG | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | VERY HIGH | 1 | 4.6 | E0030651 | 20191122SPN_05 | Tree on private property fell due to high winds. At the time of assessment Vegetation is outside the Minimum Clearance Space from any Bare Wire or HV/ABC conductor/s or Uninsulated Apparatus.
527 | Ausnet 19/63 | Ausnet | 21/11/2019 | 43790.8493 | -37.8846 | 145.42 | Gerber Rd Monbulk VIC 3793 | 1320862 | BGE11 | Low voltage AC (<1kV) | RURAL SHORT | - overhead service conductor (residential) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | VERY HIGH | 1 | 4.6 | E0030655 | 20191122SPN_02 | Ground fire started by lightning, not caused by network asset.
528 | Ausnet 19/64 | Ausnet | 22/11/2019 | 43791.9812 | -38.1287 | 146.4859 | 125 TROVATELLO PLACE, TYERS VIC 3844 | 2626341 | TGN31 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0030737 | 20191205SPN_02 | Candled HV Fuse
529 | Ausnet 19/65 | Ausnet | 25/11/2019 | 43794.2194 | -38.2164 | 146.2576 | 2 DAPHNE DRIVE, MOE SOUTH VIC 3825 | 2202289 | MOE31 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0030753 | 20191125SPN_05 | Candled HV Fuse
530 | Ausnet 19/66 | Ausnet | 26/11/2019 | 43795.7278 | -37.6827 | 145.0226 | 4 MARJORY STREET, THOMASTOWN VIC 3074 | 909037 | TT5 | 22kV AC | URBAN | - crossarm (wood) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0031292 | 20191127SPN_01 | Cause of the fire was tracking on the centre phase insulator and as a result the wooden pole top and xarm had caught fire.
531 | Ausnet 19/67 | Ausnet | 28/11/2019 | 43797.4042 | -37.2806 | 144.9441 | 45 WILLOWMAVIN ROAD, KILMORE VIC 3764 | 4716975 | KMS12 | 22kV AC | RURAL SHORT | - surge diverter | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0031380 | 20191128SPN_01 | Crow on line and shorted out LA on bypass
532 | Ausnet 19/68 | Ausnet | 29/11/2019 | 43798.8611 | -36.5705 | 145.932 | LOT 1 FIRTH ROAD, BENALLA VIC 3672 | 3910727 | BN1 | 22kV AC | RURAL LONG | - overhead conductor (bare; steel) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | VERY HIGH | 1 | 4.6 | E0031534 | 20191205SPN_03 | Bird is believed to have contacted exposed HV assets on pole top causing flashover resulting in ground fire. CFA extinguished fire. No damage to assets
533 | Ausnet 19/69 | Ausnet | 30/11/2019 | 43799.0479 | -37.8639 | 145.2525 | 67 LEWIS ROAD, WANTIRNA SOUTH VIC 3152 | 1218894 | BRA11 | 22kV AC | URBAN | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0031535 | 20191205SPN_04 | Bird has contacted switch bushings resulting in pole top fire. No evidence of ground fire
534 | Ausnet 19/70 | Ausnet | 2019-01-12 | 43800.9333 | -37.9222 | 145.4756 | 3 UPPER GRIEVE ROAD, AVONSLEIGH VIC 3782 | 420243 | BGE22 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0031542 | 20200107SPN_11 | Candled fuse (fuse failure)
535 | Ausnet 19/71 | Ausnet | 2019-11-12 | 43810.3958 | -36.7884 | 145.9694 | 18 PEARCE ROAD, LIMA EAST VIC 3673 | 3908199 | BN6 | Low voltage AC (<1kV) | RURAL LONG | - connection box | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0032124 | 20191211SPN_01 | Joint box failure
536 | Ausnet 19/72 | Ausnet | 2019-12-12 | 43811.7306 | -37.7103 | 145.0522 | 20 BARLOW RISE, BUNDOORA VIC 3083 | 5676481 | WT9 | Low voltage AC (<1kV) | URBAN | - LV pillar | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0032323 | 20200107SPN_09 | Impact from vehicle causing LV pillar to catch fire.
537 | Ausnet 19/73 | Ausnet | 16/12/2019 | 43815.2931 | -37.9981 | 145.2279 | 26 CLAREDALE ROAD, DANDENONG VIC 3175 | 524123 | ERTS-HPK 66kV | 66kV AC | N/A | - pole (wood) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0032581 | 20200107SPN_10 | Tracking activity at top of pole likely due to pollution/dust on centre phase disks/eyebolt causing top of pole to smoulder/burn.
538 | Ausnet 19/74 | Ausnet | 16/12/2019 | 43815.634 | -38.0846 | 145.494 | 60 BALD HILL ROAD, PAKENHAM VIC 3810 | 500411 | PHM21 | Low voltage AC (<1kV) | URBAN | - connection box | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0032562 | 20200107SPN_07 | Poor connection (hot joint) resulting in LV fault and overheating of fuse unit.
539 | Ausnet 19/75 | Ausnet | 16/12/2019 | 43815.9069 | -38.1225 | 147.0812 | 1 STEVENS STREET, SALE VIC 3850 | 2503175 | SLE31 | 66kV AC | RURAL LONG | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0032580 | 20200107SPN_05 | Bird (pelican) few into line.
540 | Ausnet 19/76 | Ausnet | 18/12/2019 | 43817.5708 | -36.1143 | 146.8952 | 30 HOVELL STREET, WODONGA VIC 3690 | 5204893 | WO14 | Low voltage AC (<1kV) | URBAN | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | VERY HIGH | 1 | 0.2 | E0032720 | 20191220SPN_02 | truck hit pole, LV conductor to ground, confirmed HVI
541 | Ausnet 19/77 | Ausnet | 19/12/2019 | 43818.6042 | -37.6948 | 145.8032 | 1 OLD WARBURTON ROAD, WARBURTON VIC 3799 | 1408905 | WYK13 | 22kV AC | RURAL SHORT | - overhead conductor (bare; steel) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0032876 | 20191220SPN_01 | Domino effect resulting in tree contacting conductors. The first tree to fail was a dead stag approx. 25 mts from line. The tree has fallen on a 15-20 degree angle towards the line. The tree has fallen into a mature wattle which has failed in the ground due to the impact. The wattle has then hit a tall juvenile mountain ash 9 approx. 250mm dbh causing it to snap at the ground. This tree was 20 mts from the line and has fallen straight across the conductors.
542 | Ausnet 19/78 | Ausnet | 19/12/2019 | 43818.6736 | -37.5931 | 145.2426 | 240 HILDEBRAND ROAD, COTTLES BRIDGE VIC 3099 | 919192 | DRN23 | 12.7kV AC (SWER) | RURAL LONG | - fuse (boric acid) | single wire earth return (SWER) | Otherwise started by a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | E0032873 | 20200107SPN_06 | HV Candled Fuse at Sub
543 | Ausnet 19/79 | Ausnet | 22/12/2019 | 43821.5792 | -37.8274 | 145.2432 | 70 HEATHMONT ROAD, HEATHMONT VIC 3135 | 1220862 | RWT22 | 22kV AC | URBAN | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | E0033011 | 20200107SPN_02 | 25meter tall gumtree located on council road side or Metrail land approximately 16 meters east of pole # 12220863 fell on to 66/22kV overhead conductors on pole # 12220863 causing a conductor tie to break and tree branch to ignite, the fire was contained within the touching branch and did not spread or cause a ground fire .
544 | Ausnet 19/80 | Ausnet | 23/12/2019 | 43822.0806 | -37.0846 | 148.2603 | 250 SNOWY RIVER ROAD, WULGULMERANG EAST VIC 3885 | 1904373 | BDL41 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0033016 | 20200107SPN_04 | 12K BA fuse candled
545 | Ausnet 19/81 | Ausnet | 24/12/2019 | 43823.7674 | -36.6245 | 146.4021 | 3202 WANGARATTA-WHITFIELD ROAD, EDI VIC 3678 | 5101611 | WN5 | 22kV AC | RURAL LONG | - overhead conductor (bare; steel) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | VERY HIGH | 1 | 4.6 | E0033079 | 20200107SPN_03 | large public tree came down on HV conductors at 2 greta rd Wangaratta. crew cut tree clear of conductors. there was no damage to conductors and they did not hit the ground. WN5 CB tripped. CFA called to extinguish small grass fire. crew restored power
546 | Ausnet 19/82 | Ausnet | 25/12/2019 | 43824.9583 | -38.189 | 146.561 | 3 NEFERTITI COURT, TRARALGON VIC 3844 | 2605832 | TGN31 | 22kV AC | RURAL LONG | - surge diverter | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | E0033088 | 20200106SPN_01 | The cause of the incident was a loose connection on the cable head.
547 | Ausnet 19/83 | Ausnet | 26/12/2019 | 43825.9579 | -36.5898 | 146.6979 | 453 BUFFALO RIVER ROAD, BUFFALO RIVER VIC 3737 | 4505857 | MYT22 | 22kV AC | RURAL SHORT | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | VERY HIGH | 1 | 4.6 | E0033084 | 20200205SPN_05 | Eucalyptus Camaldulensis has failed with a combination of bifurcation and drought conditions. Tree was 11 meters from the conductors and wind was around 20-30 km hr gusting
548 | Ausnet 19/84 | Ausnet | 27/12/2019 | 43826.6042 | -38.2708 | 146.4334 | 340 TRAMWAY ROAD, HAZELWOOD NORTH VIC 3840 | 2616413 | MWL24 | 22kV AC | RURAL SHORT | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | E0033097 | 20200106SPN_02 | bird contacted conductor
549 | Ausnet 19/85 | Ausnet | 27/12/2019 | 43826.6042 | -38.2543 | 146.4235 | 240 MONASH WAY, MORWELL VIC 3840 | 2626406 | MWL24 | 22kV AC | RURAL SHORT | - underground cable | three phase | Otherwise started by a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | E0033567 | 20200113SPN_01 | dead bird found on adjacent pole. Under investigation.
550 | Ausnet 19/86 | Ausnet | 29/12/2019 | 43828.5625 | -37.8003 | 145.2956 | 363-365 MT DANDENONG ROAD, CROYDON VIC 3136 | 1003440 | CYN33 | 22kV AC | URBAN | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | VERY HIGH | 1 | 0.2 | E0033113 | 20200106SPN_06 | A thin branch snapped and fell towards the HV, possible HV/LV Contact, or LV Multiphase Contact which ignited the branch which fell to the ground, but did not start any fires at all besides burning itself slightly, as per photos.
551 | Ausnet 19/87 | Ausnet | 30/12/2019 | 43829.7146 | -37.9684 | 146.9405 | 5667 TRARALGON-MAFFRA ROAD, TINAMBA VIC 3859 | 2513225 | MFA22 | 22kV AC | RURAL LONG | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | EXTREME | 3.5 | 0.7 | E0033124 | 20200106SPN_05 | Tractor made contact with HV resulting in damage to powerline.
552 | Ausnet 19/88 | Ausnet | 31/12/2019 | 43830.0431 | -37.6374 | 145.1939 | 4 ARTHURS CREEK ROAD, HURSTBRIDGE VIC 3099 | 925795 | DRN23 | 22kV AC | RURAL LONG | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | E0033126 | 20200106SPN_04 | dead possum found on ACR pole
553 | Ausnet 19/89 | Ausnet | 2020-01-01 | 43831.3257 | -38.4533 | 145.994 | 19 CRIGHTONS ROAD, KOOROOMAN VIC 3953 | 2008257 | LGA13 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | E0033147 | 20200109SPN_03 | Candled HV Fuse
554 | Ausnet 19/90 | Ausnet | 2020-02-01 | 43832.6625 | -38.4122 | 145.8082 | 305 KORUMBURRA-BENA ROAD, KORUMBURRA VIC 3950 | 2009391 | LGA24 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | E0033162 | 20200110SPN_01 | Lightning at pole.
555 | Ausnet 19/91 | Ausnet | 2020-04-01 | 43834.0229 | -37.7351 | 145.2211 | 246 RESEARCH-WARRANDYTE ROAD, NORTH WARRANDYTE VIC 3113 | 1206694 | RWN34 | 22kV AC | RURAL SHORT | - pole (concrete) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within electric line construction area | 19.8 | HIGH | 0.5 | 9.9 | E0033193 | 20200109SPN_02 | Wildlife (possum) came into contact with exposed earth flag bolt on pole top switch and fell onto garden bed covered in wood chips/leaves starting a small grass fire.
556 | Ausnet 19/92 | Ausnet | 2020-04-01 | 43834.9799 | -38.59 | 146.1448 | 37 PEACHES ROAD, FOSTER NORTH VIC 3960 | 2027084 | LGA13 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | HBRA only | 1 | VERY HIGH | 1 | 1 | E0033195 | 20200109SPN_04 | cause lightning
557 | Ausnet 19/93 | Ausnet | 2020-05-01 | 43835.5549 | -37.7693 | 145.2887 | 1 LYONS ROAD, CROYDON NORTH VIC 3136 | 1217188 | CPK11 | 22kV AC | URBAN | - pole (wood) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0033202 | 20200108SPN_05 | Pole burnt 75% through at kingbolt due to dirt and water tracking and leaking electrical current over insulator through damp pole to ground.
558 | Ausnet 19/94 | Ausnet | 2020-05-01 | 43835.7306 | -37.111 | 145.9838 | WINDY RIDGE, 340 CAMPAGNOLOS ROAD, MANSFIELD VIC 3722 | 3913642 | MSD2 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0033207 | 20200108SPN_04 | Candled fuse.
559 | Ausnet 19/95 | Ausnet | 2020-05-01 | 43835.8229 | -37.8689 | 147.9964 | 1 ONEILLS ROAD, LAKES ENTRANCE VIC 3909 | 1902142 | BDL41 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0033208 | 20200108SPN_03 | Candled fuse.
560 | Ausnet 19/96 | Ausnet | 2020-07-01 | 43837.4014 | -38.2162 | 146.0583 | 160 Loch St, Yarragon VIC 3823, Australia | 2203214 | MOE22 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0033319 | 20200107SPN_08 | HV fuse candled due to possum.
561 | Ausnet 19/97 | Ausnet | 2020-07-01 | 43837.8403 | -37.6912 | 145.112 | 27 CARBORA DALE, GREENSBOROUGH VIC 3088 | 5806765 | ELM31 | Low voltage AC (<1kV) | URBAN | - LV pillar | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | E0033386 | 20200108SPN_02 | Cable joint on service cable failed.
562 | Ausnet 19/98 | Ausnet | 14/01/2020 | 43844.6667 | -37.6728 | 145.0018 | 248 EDGARS ROAD, THOMASTOWN VIC 3074 | 908987 | TT9 | 22kV AC | URBAN | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | E0033874 | 20200115SPN_01 | Silver tape from a balloon on HV found onsite as suspect to cause the fire at pole# 908987.
563 | Ausnet 19/99 | Ausnet | 15/01/2020 | 43845.809 | -37.9247 | 145.5117 | 46 MOUNTAIN ROAD, COCKATOO VIC 3781 | 420544 | BGE22 | Low voltage AC (<1kV) | RURAL SHORT | - dropper / bridge | single phase | Started by lightning striking a distribution system or a part of a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0033974 | 20200116SPN_01 | Lightning hit substation pole. blue phase lv leads blown off, LV N down the pole as been on fire. 6 - 8 inches
564 | Ausnet 19/100 | Ausnet | 16/01/2020 | 43846.9597 | -37.3689 | 145.3537 | 959 BREAK ODAY ROAD, GLENBURN VIC 3717 | 1401202 | KLK11 | 12.7kV AC (SWER) | RURAL SHORT | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within electric line construction area | 19.8 | VERY HIGH | 1 | 19.8 | E0034058 | 20200117SPN_04 | Large tree branch fell on SWER conductor, conductor down and caused grass fire.
565 | Ausnet 19/101 | Ausnet | 17/01/2020 | 43847.6062 | -37.8539 | 147.9947 | 5 ODONNELL DRIVE, LAKES ENTRANCE VIC 3909 | 5626658 | BDL41 | 22kV AC | RURAL LONG | - transformer (kiosk mounted) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0034119 | 20200117SPN_06 | Findings by Crew Small fire inside the Kiosk at the LV Bush end It appears the grass has grown up into the LV bus Mainly Smoke damage and little scarring of the LV weber strip Kiosk checked and restored
566 | Ausnet 19/102 | Ausnet | 19/01/2020 | 43849.2667 | -37.8134 | 145.3614 | 1048 MOUNT DANDENONG TOURIST ROAD, MONTROSE VIC 3765 | 1001438 | CYN33 | Low voltage AC (<1kV) | URBAN | - pole (concrete) | single phase | Otherwise started by a distribution system | within electric line construction area | 19.8 | LOW-MODERATE | 0.2 | 3.96 | E0034137 | 20200121SPN_07 | Currently under investigation. Aluminium lug at the Neutral lead on the TX melted falling to the ground was the suspected cause of the small grass fire at the base of pole. This is consistent with the scorch marks found at the pole base. Possible overload on the TX due to number of customers connected.
567 | Ausnet 19/103 | Ausnet | 19/01/2020 | 43849.666 | -38.4781 | 146.5469 | 1 WHITELAWS TRACK, DEVON NORTH VIC 3971 | 2621400 | FTR12 | 22kV AC | RURAL LONG | - fuse (boric acid) | three phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0034139 | 20200121SPN_06 | Candled fuse due to internal degradation.
568 | Ausnet 19/104 | Ausnet | 19/01/2020 | 43849.8229 | -37.8086 | 147.6478 | 125 GREAT ALPINE ROAD, LUCKNOW VIC 3875 | 5830050 | BDL ZSS | 22kV AC | RURAL SHORT | - fuse (powder filled) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0034141 | 20200121SPN_04 | Suspected cause was electrical tracking.
569 | Ausnet 19/105 | Ausnet | 20/01/2020 | 43850.3688 | -38.4922 | 145.9935 | 30 Christoffersens Rd, Nerrena VIC 3953, Australia | 2001124 | LGA14 | 12.7kV AC (SWER) | RURAL LONG | - fuse (EDO fuse) | single wire earth return (SWER) | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0034155 | 20200121SPN_03 | Suspected lightning/storm impact.
570 | Ausnet 19/106 | Ausnet | 20/01/2020 | 43850.8576 | -37.8364 | 145.3603 | 32 Hume Ln, Mount Dandenong VIC 3767, Australia | 1304263 | MDG1 | 6.6kV AC | RURAL SHORT | - overhead conductor (ABC) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within electric line construction area | 19.8 | LOW-MODERATE | 0.2 | 3.96 | E0034250 | 20200121SPN_01 | Fallen tree due to strong winds and heavy rain.
571 | Ausnet 19/107 | Ausnet | 21/01/2020 | 43851.4097 | -36.8928 | 147.7042 | 2630 BENAMBRA-CORRYONG ROAD, BENAMBRA VIC 3900 | 1606823 | BDL8 | 12.7kV AC (SWER) | RURAL LONG | - fuse (boric acid) | single wire earth return (SWER) | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0034345 | 20200123SPN_01 | CANDLED FUSE
572 | Ausnet 19/108 | Ausnet | 21/01/2020 | 43851.6194 | -36.2132 | 147.8693 | 27A GREENWATTLE GAP ROAD, CORRYONG VIC 3707 | 5212236 | WOTS24 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0034333 | 20200121SPN_08 | Fuse hung up. No burn marks on fuse, pole or ground
573 | Ausnet 19/109 | Ausnet | 22/01/2020 | 43852.2229 | -38.1846 | 146.1301 | 409 NORTH CANAL ROAD, TRAFALGAR VIC 3824 | 2202815 | MOE22 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0034355 | 20200123SPN_02 | Fuse Candled.
574 | Ausnet 19/110 | Ausnet | 22/01/2020 | 43852.6278 | -37.726 | 145.1334 | 36 KIRWANA GROVE, MONTMORENCY VIC 3094 | 900363 | ELM34 | Low voltage AC (<1kV) | URBAN | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | SEVERE | 2 | 0.4 | E0034432 | 20200123SPN_04 | Tree branch falling onto LV conductors.
575 | Ausnet 19/111 | Ausnet | 23/01/2020 | 43853.3583 | -37.8135 | 147.7086 | 160 LANES ROAD, NICHOLSON VIC 3882 | 596312 | BDL41 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0034451 | 20200123SPN_03 | Candled fuse.
576 | Ausnet 19/112 | Ausnet | 23/01/2020 | 43853.4806 | -37.1007 | 148.6182 | 2395 MCKILLOPS ROAD, TUBBUT VIC 3888 | 5767736 | BM8B31 | 22kV AC | RURAL SHORT | - overhead conductor (bare; steel) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0034534 | 20200124SPN_01 | Dead pine tree bringing HV conductor to ground.
577 | Ausnet 19/113 | Ausnet | 24/01/2020 | 43854.5417 | -38.1748 | 146.1337 | 141 YULUNGAH ROAD, TRAFALGAR VIC 3824 | 2202060 | MOE22 | 22kV AC | RURAL LONG | - transformer (pole mounted) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0035483 | 20200204SPN_03 | Transformer hit by lightning.
578 | Ausnet 19/114 | Ausnet | 25/01/2020 | 43855.5826 | -37.5834 | 145.3897 | 190 HUNTS LANE, STEELS CREEK VIC 3775 | 1006993 | CPK12 | 22kV AC | RURAL SHORT | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0034608 | 20200128SPN_03 | Candled BA fuse due to internal degradation.
579 | Ausnet 19/115 | Ausnet | 27/01/2020 | 43857.5444 | -38.8302 | 146.1315 | 31 ENNISVALE AVENUE, SANDY POINT VIC 3959 | 2021773 | FTR21 | Low voltage AC (<1kV) | RURAL LONG | - connection box | two phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0034629 | 20200128SPN_02 | Plausible cause is a combination of corroded connection that resulted in an overheated onnection.
580 | Ausnet 19/116 | Ausnet | 27/01/2020 | 43857.5604 | -37.695 | 148.3901 | 69 BIRKINS ROAD, BETE BOLONG VIC 3888 | 1906294 | NLA32 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | E0034630 | 20200128SPN_01 | Candled fuse due to internal degradation.
581 | Ausnet 19/117 | Ausnet | 30/01/2020 | 43860.2236 | -37.8342 | 145.2406 | 84 CUTHBERT STREET, HEATHMONT VIC 3135 | 1220505 | RWT15 | Low voltage AC (<1kV) | URBAN | - connection box | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | VERY HIGH | 1 | 0.2 | E0034823 | 20200130SPN_02 | FOLCB failed from possible loose connection causing box to melt and hot plastic falling on the ground.
582 | Ausnet 19/118 | Ausnet | 31/01/2020 | 43861.8486 | -37.5702 | 145.1783 | 1135 ARTHURS CREEK ROAD, ARTHURS CREEK VIC 3099 | 5637993 | DRN14 | 22kV AC | RURAL SHORT | - overhead conductor (ABC) | three phase | Otherwise started by a distribution system | HBRA only | 1 | SEVERE | 2 | 2 | E0035165 | 20200202SPN_02 | Extreme storms and weather related event.
583 | Ausnet 19/119 | Ausnet | 31/01/2020 | 43861.9076 | -37.7381 | 145.221 | 104 BRACKENBURY STREET, WARRANDYTE VIC 3113 | 1206322 | RWN34 | Low voltage AC (<1kV) | RURAL SHORT | - overhead conductor (ABC) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | SEVERE | 2 | 9.2 | E0035161 | 20200202SPN_01 | Failed ABC IPC connector.
584 | Ausnet 19/120 | Ausnet | 2020-01-02 | 43862.1153 | -38.3658 | 145.6704 | 6525 SOUTH GIPPSLAND HIGHWAY, LOCH VIC 3945 | 2000595 | LLG12 | 22kV AC | RURAL SHORT | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0035163 | 20200202SPN_03 | Plausible cuases are age and humidity.
585 | Ausnet 19/121 | Ausnet | 2020-01-02 | 43862.6361 | -36.2366 | 147.6513 | 170 LUCYVALE ROAD, BERRINGAMA VIC 3691 | 5216793 | WOTS24 | 22kV AC | RURAL LONG | - overhead conductor (bare; aluminium core steel reinforced) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | VERY HIGH | 1 | 4.6 | E0035167 | 20200202SPN_04 | The root cause was fallen tree bringing down conductors.
586 | Ausnet 19/122 | Ausnet | 2020-01-02 | 43862.8243 | -36.5743 | 145.9605 | 232 MANSFIELD ROAD, BENALLA VIC 3672 | 3906619 | BN-MSD 66kV | 66kV AC | N/A | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | VERY HIGH | 1 | 4.6 | E0035168 | 20200303SPN_01 | Fallen tree limb as a result of stroms. Refer to attached site photos.
587 | Ausnet 19/123 | Ausnet | 2020-03-02 | 43864.4389 | -38.5485 | 146.7145 | 366 SOUTH GIPPSLAND HIGHWAY, YARRAM VIC 3971 | 2612575 | FTR23 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0035242 | 20200203SPN_02 | Plausible cause is combination of age and condition.
588 | Ausnet 19/124 | Ausnet | 2020-06-02 | 43867.5611 | -37.5396 | 148.9362 | 596 COMBIENBAR ROAD, CLUB TERRACE VIC 3889 | 1905411 | CNR3 | 22kV AC | RURAL SHORT | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | E0035729 | 20200206SPN_02 | Third party tree clearers dropped tree on live HV conductor.
589 | Ausnet 19/125 | Ausnet | 2020-07-02 | 43868.6111 | -36.8277 | 147.0705 | 1640 GREAT ALPINE ROAD, SMOKO VIC 3741 | 4502036 | BRT21 | 22kV AC | RURAL SHORT | - pole (wood) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | E0035906 | 20200207SPN_01 | Car crashed into pole.
590 | Ausnet 19/126 | Ausnet | 2020-10-02 | 43871.6736 | -38.3962 | 146.3604 | 805 WHITELAWS TRACK, YINNAR SOUTH VIC 3869 | 2627005 | MWL25 | 22kV AC | RURAL SHORT | - overhead conductor (bare; steel) | single phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0036213 | 20200211SPN_02 | The root cause is fallen tree.
591 | Ausnet 19/127 | Ausnet | 2020-12-02 | 43873.4014 | -38.3763 | 145.7056 | 90 LOCH-WONTHAGGI ROAD, LOCH VIC 3945 | 2007693 | LLG12 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0036476 | 20200212SPN_05 | CANDLED FUSE
592 | Ausnet 19/128 | Ausnet | 15/02/2020 | 43876.1583 | -37.2205 | 145.1118 | 570 STRATH CREEK ROAD, BROADFORD VIC 3658 | 4703408 | SMR22 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within electric line construction area | 19.8 | HIGH | 0.5 | 9.9 | E0037028 | 20200217SPN_01 | fuse found candling due to lightning strike. no ground fire
593 | Ausnet 19/129 | Ausnet | 15/02/2020 | 43876.5729 | -38.4643 | 146.0886 | 280 COULTERS ROAD, MARDAN VIC 3953 | 2010360 | LGA13 | 12.7kV AC (SWER) | RURAL LONG | - fuse (boric acid) | single wire earth return (SWER) | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0038983 | 20200225SPN_01 | CANDLED FUSE
594 | Ausnet 19/130 | Ausnet | 16/02/2020 | 43877.7819 | -38.136 | 146.0536 | 782 DARNUM-SHADY CREEK ROAD, SHADY CREEK VIC 3821 | 2706945 | WGL24 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0037076 | 20200217SPN_03 | Plausible cuase is combination of age and condition.
595 | Ausnet 19/131 | Ausnet | 16/02/2020 | 43877.9812 | -36.7412 | 145.5898 | 91 BALMATTUM NORTH ROAD, EUROA VIC 3666 | 3903299 | BN1 | 22kV AC | RURAL LONG | - capacitor | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0037085 | 20200217SPN_04 | Failure of CAP Bank blue phase bushing resulted in a grass fire of 100m x 50m. no clear cause but most likely moisture ingress CFA extinguished fire CAP bank left isolated and tagged do not operate
596 | Ausnet 19/132 | Ausnet | 19/02/2020 | 43880.4382 | -38.0112 | 145.9131 | 75 PALMER ROAD, JINDIVICK VIC 3818 | 2718060 | WGL24 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0040109 | 20200303SPN_02 | Candled fuse.
597 | Ausnet 19/133 | Ausnet | 20/02/2020 | 43881.8451 | -38.0697 | 146.5828 | 555 GLENGARRY NORTH ROAD, GLENGARRY NORTH VIC 3854 | 2626226 | TGN31 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0045657 | 20200323SPN_01 | Candled fuse.
598 | Ausnet 19/134 | Ausnet | 22/02/2020 | 43883.9104 | -38.1095 | 147.0662 | JACK RYANS IRISH BAR, 154 RAYMOND STREET, SALE VIC 3850 | 2501996 | SLE11 | Low voltage AC (<1kV) | URBAN | - lamps (minor road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0038549 | 20200224SPN_01 | Possible over heated connection due to blown glone and no timing mechanism on ignitors (earlier models of HPS lights). Most likely due to the capacitor or the ballast igniting over and over resulting in overheating.
599 | Ausnet 19/135 | Ausnet | 23/02/2020 | 43884.5167 | -37.1922 | 145.6955 | 4991 MAROONDAH HIGHWAY, ALEXANDRA VIC 3714 | 4714153 | RUBA12 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0038555 | 20200224SPN_02 | Plausible cuse is age.
600 | Ausnet 19/136 | Ausnet | 23/02/2020 | 43884.7312 | -37.8155 | 147.4366 | 730 LINDENOW-GLENALADALE ROAD, LINDENOW SOUTH VIC 3875 | 1607114 | BDL44 | 22kV AC | RURAL LONG | - fuse (boric acid) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0038558 | 20200227SPN_02 | Plausible cuase is combination of age and condition.
601 | Ausnet 19/137 | Ausnet | 25/02/2020 | 43886.6069 | -38.1797 | 146.1523 | 52 WHEELBARROW ROAD, TRAFALGAR VIC 3824 | 2203072 | MOE22 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0039007 | 20200225SPN_03 | CANDLED FUSE
602 | Ausnet 19/138 | Ausnet | 25/02/2020 | 43886.7458 | -37.6538 | 148.8209 | BELLBIRD HOTEL, 3872 PRINCES HIGHWAY, BELLBIRD CREEK VIC 3889 | 1910588 | CNR3 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | E0040396 | 20200303SPN_03 | Candled 6A BA fuse
603 | Ausnet 19/139 | Ausnet | 26/02/2020 | 43887.8653 | -37.2897 | 145.2861 | 2752 BROADFORD-FLOWERDALE ROAD, FLOWERDALE VIC 3717 | 4703935 | SMR14 | 22kV AC | RURAL LONG | - fuse (any other type) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0039257 | 20200227SPN_03 | CANDLED FUSE
604 | Ausnet 19/140 | Ausnet | 26/02/2020 | 43887.9181 | -38.242 | 146.792 | 42 FEELYS ROAD, WILLUNG VIC 3847 | 2611076 | TGN41 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0039261 | 20200227SPN_04 | CANDLED FUSE
605 | Ausnet 19/141 | Ausnet | 2020-04-03 | 43894.4743 | -37.7544 | 145.6529 | 3045 WARBURTON HIGHWAY, MILLGROVE VIC 3799 | 1407375 | WYK13 | Low voltage AC (<1kV) | RURAL SHORT | - fuse (any other type) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0040647 | 20200305SPN_01 | LV FUSE FAILED
606 | Ausnet 19/142 | Ausnet | 2020-06-03 | 43896.7035 | -37.7126 | 145.0828 | 401 GREENSBOROUGH ROAD, WATSONIA VIC 3087 | 904031 | WT13 | 22kV AC | URBAN | - pole (wood) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0041526 | 20200306SPN_01 | Pole was hit by lightning on a stormy day resulting in broken pole.
607 | Ausnet 19/143 | Ausnet | 2020-10-03 | 43900.3993 | -36.3731 | 146.28 | 74 SHANLEY STREET, WANGARATTA VIC 3677 | 5103634 | WN4 | Low voltage AC (<1kV) | RURAL SHORT | - transformer (ground outdoor mounted) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0041737 | 20200318SPN_01 | TX caught fire at LV bushings
608 | Ausnet 19/144 | Ausnet | 13/03/2020 | 43903.5 | -38.1467 | 145.4585 | 40 HOBSON ROAD, RYTHDALE VIC 3810 | 516186 | PHM22 | 22kV AC | RURAL SHORT | - fuse (boric acid) | single phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | VERY HIGH | 1 | 1 | E0042988 | 20200313SPN_01 | Caused due to wildlife (bird).
609 | Ausnet 19/145 | Ausnet | 14/03/2020 | 43904.0333 | -37.3938 | 145.0533 | 264 SOUTH MOUNTAIN ROAD, UPPER PLENTY VIC 3756 | 912330 | KLO14 | Low voltage AC (<1kV) | RURAL LONG | - overhead conductor (ABC) | two phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within electric line construction area | 19.8 | HIGH | 0.5 | 9.9 | E0043215 | 20200316SPN_03 | Tree fell and brought down the line.
610 | Ausnet 19/146 | Ausnet | 19/03/2020 | 43909.8708 | -36.106 | 146.8319 | VISY BOARD, 299 MCKOY STREET, WEST WODONGA VIC 3690 | 5652435 | WO13 | Low voltage AC (<1kV) | RURAL SHORT | - lamps (major road) | single phase | Otherwise started by a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | E0045390 | 20200320SPN_01 | Deterioration of connection.
611 | Ausnet 19/147 | Ausnet | 24/03/2020 | 43914.1181 | -37.7271 | 145.1492 | 28 METERY ROAD, ELTHAM VIC 3095 | 921885 | ELM34 | 22kV AC | URBAN | - fuse (any other type) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0045778 | 20200326SPN_01 | Candled fuse.
612 | Ausnet 19/148 | Ausnet | 25/03/2020 | 43915.3333 | -36.3695 | 146.2373 | 453 SHANLEY STREET, WANGARATTA SOUTH VIC 3678 | 5104064 | WN4 | 22kV AC | RURAL SHORT | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0045946 | 20200326SPN_02 | fallen tree. Root Ball unstable. fault NOT caused by branches inside the clearance space contacting the line. Trunk Distance to nearest conductor 14m.
613 | Ausnet 19/149 | Ausnet | 28/03/2020 | 43918.6569 | -37.8468 | 145.2903 | 16 HILLSIDE AVENUE, BORONIA VIC 3155 | 1222987 | BWR13 | Low voltage AC (<1kV) | URBAN | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | E0046123 | 20200130SPN_01 | Falling tree branch hit the LV lines as it dropped to the ground.
614 | Ausnet 19/150 | Ausnet | 28/03/2020 | 43918.9972 | -37.6616 | 145.5292 | 178 MT RIDDELL ROAD, HEALESVILLE VIC 3777 | 1409956 | WYK24 | 22kV AC | RURAL SHORT | - fuse (boric acid) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0046125 | 20200316SPN_01 | Plausible cause is degradation due to age.
615 | Ausnet 19/151 | Ausnet | 30/03/2020 | 43920.7292 | -36.1476 | 146.6397 | Hume Highway, CHILTERN, VIC, 3683 | 5208203 | BWA22 | Low voltage AC (<1kV) | RURAL LONG | - overhead conductor (insulated) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0046230 | 20200401SPN_02 | lv cables on transformer caught fire
616 | Ausnet 19/152 | Ausnet | 30/03/2020 | 43920.8299 | -36.8938 | 145.6242 | 1839 Euroa-Mansfield Rd | 3918898 | BN1 | 22kV AC | RURAL LONG | - fuse (any other type) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0046229 | 20200401SPN_01 | CANDLED FUSE
617 | Ausnet 19/153 | Ausnet | 2020-01-04 | 43922.2292 | -37.7977 | 147.6405 | 30 SHIELDS ROAD, LUCKNOW VIC 3875 | 1612084 | BDL44 | 12.7kV AC (SWER) | RURAL LONG | - fuse (EDO fuse) | single wire earth return (SWER) | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0046529 | 20200401SPN_03 | CANDLED FUSE
618 | Ausnet 19/154 | Ausnet | 2020-02-04 | 43923.3063 | -38.4088 | 146.3028 | 55 FOX AND FANCKES ROAD, BOOLARRA SOUTH VIC 3870 | 2623514 | MWL11 | 22kV AC | RURAL SHORT | - overhead conductor (bare; steel) | three phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0046546 | 20200402SPN_01 | A mechanical failure of the conductor.
619 | Ausnet 19/155 | Ausnet | 2020-04-04 | 43925.616 | -37.7327 | 145.1372 | UNIT 1 2A PORTER STREET, ELTHAM VIC 3095 | 900633 | ELM34 | 22kV AC | URBAN | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0047518 | 20200602SPN_01 | Tree branch fell due to weather conditions
620 | Ausnet 19/156 | Ausnet | 2020-06-04 | 43927.3125 | -37.9823 | 146.8831 | 4945 TRARALGON-MAFFRA ROAD, TINAMBA VIC 3859 | 5723936 | MFA22 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0046598 | 20200508SPN_01 | Plausible cause is age of the EDO Fuse.
621 | Ausnet 19/157 | Ausnet | 2020-08-04 | 43929.8785 | -37.8274 | 145.5986 | 650 GEMBROOK-LAUNCHING PLACE ROAD, HODDLES CREEK VIC 3139 | 1405343 | WYK23 | 22kV AC | RURAL SHORT | - fuse (boric acid) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0046664 | 20200409SPN_01 | CANDLING FUSE
622 | Ausnet 19/158 | Ausnet | 22/04/2020 | 43943.2333 | -37.7528 | 145.7005 | 3494 WARBURTON HIGHWAY, WARBURTON VIC 3799 | 1407922 | WYK13 | 22kV AC | RURAL SHORT | - fuse (boric acid) | three phase | Otherwise started by a distribution system | within electric line construction area | 19.8 | LOW-MODERATE | 0.2 | 3.96 | E0046988 | 20200423SPN_01 | Possom found burnt and dead at the base of the pole which may of caused the fuse not to eject. *Candelling fuse at WT009
623 | Ausnet 19/159 | Ausnet | 24/04/2020 | 43945.5833 | -37.8567 | 145.2396 | TEDDINGTON WAY, WANTIRNA VIC 3152 | 5804193 | BRA32 | Low voltage AC (<1kV) | URBAN | - LV pillar | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0047941 | 20200518SPN_01 | Electrical breakdown,fuses operated due to electrical and mechanical breakdown of the pillar due to the fire.
624 | Ausnet 19/160 | Ausnet | 27/04/2020 | 43948.4743 | -38.4576 | 145.475 | 40 DWYER ROAD, BASS VIC 3991 | 2803195 | LLG13 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0047159 | 20200506SPN_01 | Possible cause is salt air corrosion and moisture inside fuse holder.
625 | Ausnet 19/161 | Ausnet | 28/04/2020 | 43949.3965 | -38.2937 | 145.837 | 25 MOUNTAIN VIEW ROAD, MOUNTAIN VIEW VIC 3988 | 2005050 | LGA24 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0047191 | 20200429SPN_01 | Candling fuse.
626 | Ausnet 19/162 | Ausnet | 2020-04-05 | 43955.1729 | -37.7965 | 145.2563 | 434 MAROONDAH HWY, RINGWOOD VIC 3134 | 1220280 | CYN12 | 22kV AC | URBAN | - transformer (pole mounted) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | E0047402 | 20200416SPN_01 | Transformer has caught fire
627 | Ausnet 19/163 | Ausnet | 13/05/2020 | 43964.8979 | -37.796 | 145.2571 | 436-440 MAROONDAH HIGHWAY, CROYDON VIC 3136 | 1220282 | CYN32 | Low voltage AC (<1kV) | URBAN | - lamps (major road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | E0047827 | 20200514SPN_01 | Dedregation of grey twisted service supplying the pole has made contact with the pole or conductors on the pole.
628 | Ausnet 19/164 | Ausnet | 18/05/2020 | 43969.2708 | -37.8822 | 145.3952 | 1-3 VIEW ROAD, THE PATCH VIC 3792 | 1321440 | BGE11 | 22kV AC | RURAL SHORT | - fuse (boric acid) | three phase | Otherwise started by a distribution system | within electric line construction area | 19.8 | NO FORECAST | 0.1 | 1.98 | E0047942 | 20200518SPN_02 | Found HV fuses were 6k BA Fuses and are wrong fuse rating f or a 200kva. Upgraded all 3 existing 6k HV fuses to 15e BA Fuses at Camm s'Patch S \S. Tested LV off load and on load volts were good
629 | Ausnet 19/165 | Ausnet | 20/05/2020 | 43971.8278 | -37.5936 | 145.1619 | 181 CHAPEL LANE, DOREEN VIC 3754 | 919037 | DRN14 | 12.7kV AC (SWER) | RURAL SHORT | - fuse (boric acid) | single wire earth return (SWER) | Otherwise started by a distribution system | HBRA only | 1 | NO FORECAST | 0.1 | 0.1 | E0048124 | 20200601SPN_03 | Degradation of the fuse
630 | Ausnet 19/166 | Ausnet | 28/05/2020 | 43979.4431 | -38.0693 | 147.0836 | Cnr Bengworden Rd and Hagans Rd Cobains | 2503447 | SLE32 | 22kV AC | RURAL SHORT | - fuse (boric acid) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | E0048980 | 20200529SPN_02 | Fuse was candling with significant tracking when crews arrived onsite, fuse then burnt through and 'operated' in that the circuit was Deenergised but the fuse didn't operate traditionally in dropping out. Crew inspected the site and found nothing else Tube had burnt through about 20 mm from top of the fuse , but no other evidence of burning found
631 | Ausnet 19/167 | Ausnet | 29/05/2020 | 43980.8472 | -38.3237 | 145.6715 | 960 YANNATHAN ROAD, NYORA VIC 3987 | 2006256 | LLG12 | 22kV AC | RURAL SHORT | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | NO FORECAST | 0.1 | 0.46 | E0049149 | 20200601SPN_01 | Crew arrived onsite and found Burnt off BA tube at Lis NO 2006256 top half of tube laying on the ground the other half still in the holder Note no evidence of fire on the ground , Tube had burnt marks where it had come in half. It was an older deteriated fuse
632 | Ausnet 19/168 | Ausnet | 31/05/2020 | 43982.0687 | -37.929 | 145.9611 | 2951 MAIN NEERIM ROAD, NEERIM JUNCTION VIC 3832 | 2700346 | WGL24 | 22kV AC | RURAL LONG | - fuse (boric acid) | three phase | Otherwise started by a distribution system | HBRA only | 1 | NO FORECAST | 0.1 | 0.1 | E0049156 | 20200601SPN_02 | Fuse was hung up and candleing, burn marks contained to fuse only. No fire.
633 | Ausnet 19/169 | Ausnet | 2020-01-06 | 43983.8569 | -37.7907 | 145.3774 | 4 NORTH AVENUE, MOUNT EVELYN VIC 3796 | 1000617 | LDL11 | 22kV AC | URBAN | - overhead conductor (bare; aluminium core steel reinforced) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within electric line construction area | 19.8 | NO FORECAST | 0.1 | 1.98 | E0049200 | 20200602SPN_02 | An approx. 25 meter tall gumtree located within no.6 North Avenue’s premises, setback approx. 9 meters away from nearest overhead conductors between spanned poles #1000617 & 10000618 is suspected to have been uprooted by rain and windy conditions causing the tree to fall onto to and break an open wire 22kV white phase overhead conductor, 2 x polly 22kV insulators and a shared overhead Telstra cable on pole #1000617 with 22kV fault current causing an approx .5x.5m small grass fire and burning the Telstra cable dressed up pole at base of pole and possibly HV injecting Telstra network?
634 | Ausnet 19/170 | Ausnet | 2020-05-06 | 43987.5049 | -37.8118 | 145.4427 | 25 HEAD ROAD, WANDIN EAST VIC 3139 | 1011429 | LDL23 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | NO FORECAST | 0.1 | 0.46 | E0049437 | 20200605SPN_02 | Fuse operated as required but did not drop.
635 | Ausnet 19/171 | Ausnet | 2020-05-06 | 43987.534 | -38.4603 | 145.8173 | 100 SCOTT AND FAHEYS ROAD, KORUMBURRA VIC 3950 | 2006290 | LGA12 | 22kV AC | RURAL SHORT | - fuse (boric acid) | single phase | Otherwise started by a distribution system | HBRA only | 1 | NO FORECAST | 0.1 | 0.1 | E0049447 | 20200605SPN_01 | Crew arrived onsite and found blown 6 K BA fuse at Scott ESTATE Pole 1 LIS no 2006290 - fuse had candle showing burn marks crew advised CEOT of findings Crew inspected the sight no fire on the ground and no cause found
636 | Ausnet 19/172 | Ausnet | 2020-11-06 | 43993.3125 | -37.4188 | 144.9746 | 33 RAGLAN STREET, WALLAN VIC 3756 | 912897 | KLO24 | Low voltage AC (<1kV) | RURAL SHORT | - underground service cable (residential) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | E0049650 | 20200611SPN_04 | older type neutral screen service cable had electrical insulation breakdown
637 | Ausnet 19/173 | Ausnet | 13/06/2020 | 43995.9493 | -38.3305 | 146.5801 | 342 OLD CALLIGNEE ROAD, CALLIGNEE VIC 3844 | 2605584 | TGN23 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | HBRA only | 1 | NO FORECAST | 0.1 | 0.1 | E0049811 | 20200615SPN_03 | Crew arrived onsite found candled EDO fuse 6K EDO fuse Lis 2605584 Richie Pole 3 Single phase 10 KVA transformer No Fire on the ground - Fuse tube burnt only - cause Possum (TGN23FDR)
638 | Ausnet 19/174 | Ausnet | 19/06/2020 | 44001.4347 | -38.0695 | 145.4679 | 14 BEVAN COURT, PAKENHAM VIC 3810 | 5654539 | OFR24 | Low voltage AC (<1kV) | URBAN | - LV pillar | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | E0050223 | 20200622SPN_04 | LV pillar had burnt leads due to loose connections. leads replaced tested, and pillar returned to service.
639 | Ausnet 19/175 | Ausnet | 21/06/2020 | 44003.0243 | -37.755 | 145.2726 | 295-297 YARRA ROAD, WONGA PARK VIC 3115 | 1203571 | CPK11 | 22kV AC | RURAL SHORT | - fuse (boric acid) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | NO FORECAST | 0.1 | 0.46 | E0050241 | 20200622SPN_05 | Fuses had to be cut away due to fuse failing to eject and replaced all faulty components with new ones.
640 | Ausnet 19/176 | Ausnet | 24/06/2020 | 44006.7306 | -38.4274 | 146.8236 | 1003 CARRAJUNG-WOODSIDE ROAD, WOODSIDE NORTH VIC 3874 | 2611451 | FTR23 | 12.7kV AC (SWER) | RURAL LONG | - fuse (boric acid) | single wire earth return (SWER) | Otherwise started by a distribution system | HBRA only | 1 | NO FORECAST | 0.1 | 0.1 | E0050511 | 20200626SPN_02 | Fuse failed to eject. fuse was replaced and supply restored.
641 | Ausnet 19/177 | Ausnet | 24/06/2020 | 44006.984 | -37.9708 | 146.9818 | 205-207 Johnston Street/Station Street maffra | 5829054 | MFA ZSS | 22kV AC | N/A | - transformer (ground outdoor mounted) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | E0050515 | 20200625SPN_01 | Tap changer ruptured due to an internal fault which led to the oil release
642 | Ausnet 19/178 | Ausnet | 26/06/2020 | 44008.8069 | -37.6519 | 145.5185 | 231-235 MAROONDAH HIGHWAY, HEALESVILLE VIC 3777 | 1403422 | WYK24 | Low voltage AC (<1kV) | RURAL SHORT | - luminaires (minor road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | E0050714 | 20200629SPN_01 | PE cell connections overheated due to bad connections.
643 | Ausnet 19/179 | Ausnet | 27/06/2020 | 44009.0681 | -38.454 | 145.2468 | 24 JENNER AVENUE, COWES VIC 3922 | 2806004 | PHI13 | Low voltage AC (<1kV) | URBAN | - switch (disconnector/isolator) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | E0050723 | 20200629SPN_04 | Krone box caught fire due to electrical breakdown.
644 | Ausnet 19/180 | Ausnet | 28/06/2020 | 44010.7222 | -37.8604 | 148.0362 | 5 CHANDLERS ROAD, LAKE BUNGA VIC 3909 | 1902798 | NLA34 | Low voltage AC (<1kV) | RURAL SHORT | - connection box | single phase | Otherwise started by a distribution system | HBRA only | 1 | NO FORECAST | 0.1 | 0.1 | E0050728 | 20200629SPN_07 | FOLCB caught fire due to Connections in box becoming overheated melting the plastic around the terminals then catching fire. The connections in the fuse box became overheated due to corroded connections and more load on terminals due to cold day and customer heaters etc this location is by the sea so in high salt area that would have contributed to corroding connections over time
645 | Ausnet 19/181 | Ausnet | 28/06/2020 | 44010.7319 | -38.6991 | 146.1089 | 25 WORFOLKS ROAD, FISH CREEK VIC 3959 | 2024170 | FTR21 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | HBRA only | 1 | NO FORECAST | 0.1 | 0.1 | E0050727 | 20200629SPN_06 | 22kv BA fuse failed to eject.
646 | Ausnet 19/182 | Ausnet | 21/12/2019 | 43820.7708 | 145.2672 | -37.9179 | 2 JENHILL COURT, ROWVILLE VIC 3178 | 260075464 | FGY12 | Low voltage AC (<1kV) | URBAN | - LV pillar | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | E0033007 | 20200107SPN_12 | low voltage paralleling pillar in the open position failed ; It is suspected the failure was caused by a loose connection or insulation breakdown causing a phase to ground earth fault
647 | Ausnet 19/183 | Ausnet | 2020-03-04 | 43924.6986 | 145.9329 | -38.1643 | 112-118 QUEEN STREET, WARRAGUL VIC 3820 | 2717552 | WGL15 | Low voltage AC (<1kV) | RURAL SHORT | - overhead conductor (insulated) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0046584 | 20200417SPN_01 | Fire at LV switchboard ; Likely cause electrical breakdown of insulation within the switchboard.
648 | United 18/19 | United | 2018-07-09 | 0.040069 | -37.8179 | 145.1761 | SPRINGVALE ROAD, NUNAWADING VIC 3131 | 9751815 | NW 14 | Low voltage AC (<1kV) | Urban | - lamps (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1196382 | 20180716UTD_04 | Street light pole on fire as per MFB spring rd 1n whitehorse, center median. opp ambulance depot. light head nth bound side - LIS = 9751815
649 | United 18/20 | United | 2018-07-23 | 0.50586 | -38.3195 | 144.7105 | 3804 POINT NEPEAN ROAD, PORTSEA VIC 3944 | 1307193 | STO13 | 22kV AC | Urban | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1201097 | 20180725UTD_01 | Tree was on fire as per CFA road side hv condcutor property boundary of 3804 & 3808 - lis#1307193 conductor fire repot# 6826 council tree -no fire when crew arrived
650 | United 18/21 | United | 2018-07-23 | 0.81383 | -38.0672 | 145.1585 | THOMPSONS ROAD, BANGHOLME VIC 3175 | 9679025 | CRM11 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1201286 | 20180727UTD_01 | Probable conductor clashing Thompsons rd adjacent THOMPSON P277 MMBW S/S, small fire which CFA attended.R Clarke fire report. Suspect conductor clash due to high winds - LIS 9679025
651 | United 18/22 | United | 2018-07-24 | 0.78704 | -37.8751 | 145.1246 | MILLER CRESCENT, MOUNT WAVERLEY VIC 3149 | 8802801 | BW 33 | 11kV AC | Urban | - fuse (powder filled) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1201917 | 20180810UTD_01 | Candling PF Fuse Sub placed under LV // prior to opening of the the HV fuses. Footpath side PFF unit requires replacement. LIS= 8802801
652 | United 18/23 | United | 2018-07-28 | 0.75197 | -37.9049 | 145.1234 | 73 CLAYTON ROAD, OAKLEIGH EAST VIC 3166 | 600362 | CDA23 | Low voltage AC (<1kV) | Urban | - lamps (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1203802 | 20180730UTD_01 | Cust reported Pole fire, crew isolated supply at the j/box on the pole fed by an o/head service. street light head (150HPS) needs replacement. LIS # 600362 which is o/s of 73 Clayton Rd Oakleigh east.
653 | United 18/24 | United | 2018-07-31 | 0.89189 | -37.8994 | 145.0953 | UNIT 8 105 ATHERTON ROAD, OAKLEIGH VIC 3166 | 8803853 | OAK32 | Low voltage AC (<1kV) | Urban | - connection box | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1204647 | 20180828UTD_05 | Closest LIS 8803853 - repl burnt out 501 mtr - old mtr 0962856 - no display, new 1362954 - 0 - internal fire - faulty mtr - fire out on arrival
654 | United 18/25 | United | 2018-08-10 | 0.76494 | -38.4572 | 144.9901 | 2150 MORNINGTON-FLINDERS ROAD, FLINDERS VIC 3929 | 1314698 | DMA23 | 22kV AC | Rural Short | - dropper / bridge | single phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1207722 | 20180929UTD_01 | LIS - 1314698. Its actually on MTN Flinders RD and Boyds. Its not at Frank Flinders. Damage high up on pole. Transformer needs to be replaced. 1single ph 50kva pole mount. feeding 2 customer - no fire on arrival - cct dropper blackened only. PM # 1000668807 - Sub Mtn Fldrs P10 Boyd - per Trent Wilson - 3rd call to attend Sat am - VPN advised. Replaced a single phase 50kva transformer, and 1 burnt out lead on the white phase. Tested and left on 238V. ref job 1207724 for further details
655 | United 18/26 | United | 2018-08-17 | 0.81826 | -37.9821 | 145.2151 | CLEELAND STREET, DANDENONG VIC 3175 | 637203 | LD 07 | 22kV AC | Urban | - dropper / bridge | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1210051 | 20180828UTD_01 | lis: 37203 out front of #56 - issues possible from fuse on pole.Crew found the centre phase HV dropper from the bottom of the fuse unit to the vaccum switch. Cap bank has old stile vaccum switches and requires a load buster to isolate. will require operator to attend tomorrow with said load buster to isolate cap bank completely. Is safe for tonight.
656 | United 18/27 | United | 2018-08-18 | 0.060069 | -38.1261 | 145.13 | 45 BOONONG AVENUE, SEAFORD VIC 3198 | 3308283 | FTN14 | Low voltage AC (<1kV) | Urban | - lamps (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1210065 | 20180828UTD_02 | LIS - 3308283, fire brigade leaving, fire out, disconnected street light for safety, s/l head burnt out, new head & globe req'd, Casey & Rod to attend over the weekend - replaced 80w sl head and rewired
657 | United 18/28 | United | 2018-08-24 | 0.1623 | -37.9467 | 145.0063 | 22 QUEENS SQUARE, SANDRINGHAM VIC 3191 | 1817885 | SR 13 | Low voltage AC (<1kV) | Urban | - connection box | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1211952 | 20180828UTD_03 | LIS - 1817885, FMJB on lis#1817885 burnt out and start a small pole fire, damaged to property #22 Queens Sq - Fire report #01542
658 | United 18/29 | United | 2018-08-26 | 0.92153 | -38.0614 | 145.1179 | 10 NEWBERRY AVENUE, BONBEACH VIC 3196 | 3303088 | CRM22 | Low voltage AC (<1kV) | Urban | - connection box | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1212546 | 20180828UTD_04 | replaced 3 phase FMB on lis # 3303088, replaced 2w service to #10 Newberry Ave, height comp, issued 5 day defect on FMB left on, CIA and getting REC tomorrow to do repairs, NST tested and passed, also replaced 2 x 250a din phase white and blue phases
659 | United 18/30 | United | 2018-08-28 | 0.82171 | -37.9033 | 145.0453 | 7 ORMOND ROAD, ORMOND VIC 3204 | 2322622 | BT 09 | 11kV AC | Urban | - connector / termination | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1213290 | 20180909UTD_02 | HV LA needs to be cut clear, LIS# 2322622, crew to return later to cut clear. crew also replaced copper D on the blue phs.
660 | United 18/31 | United | 2018-09-04 | 0.79193 | -37.8513 | 145.125 | 344 BURWOOD HIGHWAY, BURWOOD VIC 3125 | 7050956 | EB 11 | Low voltage AC (<1kV) | Urban | - lamps (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1215353 | 20180909UTD_06 | LIS# 7050956 Public lighting pole in centre mediam strip (tramways pole)250a HPS lantern will need to be replaced.
661 | United 18/32 | United | 2018-09-07 | 0.78439 | -37.787 | 145.1344 | 732 DONCASTER ROAD, DONCASTER VIC 3108 | 7061755 | DC 04 | Low voltage AC (<1kV) | Urban | - lamps (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1216628 | 20180916UTD_04 | Disconnected burnt out p/light head on lis: 7061755 - refer to s/light crew to replace 150w hps light - supply on to 1/732 when crew arrived - crew carried out nst and passed at unit - no fire when crew arrvied.
662 | United 18/33 | United | 2018-09-09 | 0.78333 | -38.3376 | 145.1751 | 16 SUDHOLZ STREET, BITTERN VIC 3918 | 8823764 | HGS23 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1216829 | 20180916UTD_06 | Repl UG fuse boxes #11 and 14 Sudholz at lis 8823764 -fire was out on arrival - 3ph fuse box at #14 shorted and cause fire at pole - poss loose connection
663 | United 18/34 | United | 2018-09-11 | 0.84571 | -38.2841 | 145.1887 | FRANKSTON-FLINDERS ROAD, HASTINGS VIC 3915 | 1105560 | HGS33 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1217573 | 20180929UTD_04 | LIS#= 1105560 - due to an earlier animal fault on ACR 7521, HV conductors clashed started small grass fire, 6mtrs sq approx. Fire report filled out #05633.
664 | United 18/35 | United | 2018-09-12 | 0.42778 | -37.8803 | 144.9974 | HOTHAM STREET, ELSTERNWICK VIC 3185 | 2306611 | EW 08 | 11kV AC | Urban | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1217844 | 20181001UTD_02 | Fault current from a nearby fault caused a HV bridge to blow on anchor pole in Hotham st corner of Hotham Ave spitting molten metal into the grass below causing a small ground fire.
665 | United 18/36 | United | 2018-09-15 | 0.40477 | -37.9626 | 145.0602 | 26 WILSON STREET, CHELTENHAM VIC 3192 | 1814983 | HT 11 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1219025 | 20181001UTD_03 | LIS - 1814983. operator found HV strain xarm burned through at the xarm strap, the LV xarm was also damaged. Both x-arms replaced
666 | United 18/37 | United | 2018-09-25 | 0.49514 | -37.8415 | 145.2001 | CARLINGA DRIVE, VERMONT VIC 3133 | 7031165 | RWT35 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1222030 | 20181002UTD_01 | Truck hit tree which caused branches to make contact and catch fire (MFB) with HV O/H conductors at LIS#7031165.
667 | United 18/38 | United | 2018-09-27 | 0.55569 | -37.8113 | 145.1742 | GLADYS STREET, NUNAWADING VIC 3131 | 7032815 | NW 21 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1222712 | 20181019UTD_02 | Refer to t/o : 1222705 - no fire when crew arrived - fire ignition report not required - unable to group due to abnormal switching (this job was cause of NW21 feeder reclose) - address now 30 gladys av as per mfb. Crew found the remains of a bunch of helium balloons in the HV at LIS#7032815. Caused damage to HV disc insulators and 2 X HV X-arms. AP#45935 issued at 1600 to replace x-arms & discs - crew repalced x2 us21 hv x-arms (strain) on lis: 7032815 - Notification 1000678128.
668 | United 18/39 | United | 2018-09-27 | 0.82964 | -37.8894 | 145.2204 | 31 WESTBURN GROVE, SCORESBY VIC 3179 | 617315 | MGE21 | 22kV AC | Urban | - fuse (powder filled) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1222828 | 20181002UTD_03 | Centre phase white HV fuse candelling... to lv// and isolate. Fuse unit was not properly closed, replaced 16a pff... no interruption.
669 | United 18/40 | United | 2018-10-09 | 0.85978 | -37.902 | 145.1499 | 509 FERNTREE GULLY ROAD, GLEN WAVERLEY VIC 3150 | 611790 | GW 05 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1225875 | 20181012UTD_01 | Pole fire lis 0611790 O/S 509 FTG Rd Glen Waverly. Dual cct 66kv pole with GW5 22KV FDR & LV. CFA attended. Small section of GW5 between DN0594 & Fault crew replaced burnt x arm.
670 | United 18/41 | United | 2018-10-15 | 0.44252 | -37.8976 | 145.0361 | 196 BOORAN ROAD, ORMOND VIC 3204 | 2322822 | CFD25 | 11kV AC | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1227219 | 20181016UTD_01 | Cap Bank "Booran-Beaty" lis2322822, red phase lead burnt off ……a caller reported a fire at the top of the pole but there was no fire damage
671 | United 18/42 | United | 2018-10-16 | 0.39444 | -38.4627 | 144.9946 | 2216 MORNINGTON-FLINDERS ROAD, FLINDERS VIC 3929 | 8827247 | DMA23 | 22kV AC | Rural Short | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 1227570 | 20181018UTD_03 | HV fuse candelled... to open and replace..LIS 8827247 "MTN Flind P7 - Boyds"
672 | United 18/43 | United | 2018-10-16 | 0.85347 | -38.3166 | 145.1941 | 42 SALMON STREET, HASTINGS VIC 3915 | 1109493 | HGS32 | 22kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1227966 | 20181018UTD_04 | LIS 1109493, 22kV HV strain/LV term pole, caught on fire due to tracking/salt air, burnt behind LV arm/kingbolt, tracking marks down pole to LV arm.Fire contained to upper section of pole/xarm only.
673 | United 18/44 | United | 2018-10-20 | 0.45251 | -37.8901 | 145.0652 | 396 NEERIM ROAD, CARNEGIE VIC 3163 | 2327331 | EM 10 | 11kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1229633 | 20181022UTD_01 | Pole will req replacing - burnt of behind the LV x arm - traffic control will be req - HV Strain pole with HV isolators and off set lv x arm with LV undergound - lis 2327331 - ok to change next couple of weeks.
674 | United 18/45 | United | 2018-10-31 | 0.47917 | -37.9286 | 145.149 | 893-895 PRINCES HIGHWAY, SPRINGVALE VIC 3171 | 9227806 | SVW45 | 22kV AC | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1232005 | 20181101UTD_01 | See TE#1231733 Succ Recl. Damage to WPh PF Fuse unit at DN0545 PRINCES HWY and replaced Damaged fuse unit caused by flashover - LIS 9227806
675 | United 18/46 | United | 2018-11-05 | 0.49941 | -37.9816 | 145.2024 | 27 WILMA AVENUE, DANDENONG VIC 3175 | 633695 | NP 36 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1233104 | 20181109UTD_01 | Broken X/ARM, crossarm fire lis#0633695 Wilma Ave.
676 | United 18/47 | United | 2018-11-06 | 0.43019 | -37.9756 | 145.0166 | 611 BALCOMBE ROAD, BLACK ROCK VIC 3193 | 1812587 | BR 04 | 11kV AC | Urban | - underground cable | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1233313 | 20181224UTD_01 | Lightning struck CHP in Bluff cnr of Beach rd, all 6 S/D's failed and require replacement. S/D's cut clear and ASR. PN#1000685078
677 | United 18/48 | United | 2018-11-20 | 0.732 | -37.8629 | 145.0359 | 53 THANET STREET, MALVERN VIC 3144 | 2313937 | K 06 | 11kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1238291 | 20181206UTD_03 | Emergency switching to remove council tree branch from across HV/LV, LIS=2313937
678 | United 18/49 | United | 2018-11-21 | 0.084722 | -38.1395 | 145.1206 | 122 GOULD STREET, FRANKSTON VIC 3199 | 3309214 | FTN14 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1238431 | 20181206UTD_04 | Confirmed fire start, krone box caught on fire, cause of ignition unknown. Crew cut clear abc and krone box in gould st at LIS# 33009214.
679 | United 18/50 | United | 2018-11-21 | 0.89087 | -38.3656 | 145.2016 | COOK ROAD, HMAS CERBERUS VIC 3920 | 8826921 | HGS31 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1238816 | 20181206UTD_06 | large cypress hedge on defense land growing close to HV. LIS# 8826921 to LIS# 1110586 branch has burnt through & has been removed by fire crew, tree clearers on site assessing any further follow up required.
680 | United 18/51 | United | 2018-11-23 | 0.69583 | -38.3203 | 144.7135 | NEPEAN PLACE, PORTSEA VIC 3944 | 1307258 | STO22 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1239371 | 20181206UTD_05 | Pole fire at LV x arm on pole Lis#1307258. P/N #1000687738 fire report #6725, also refer #1239371
681 | United 18/52 | United | 2018-11-29 | 0.070891 | -37.9878 | 145.1007 | DE HAVILLAND ROAD, MORDIALLOC VIC 3195 | 1806824 | MC 06 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1241272 | 20181206UTD_10 | Light misty rain at time of outage.Pole fire & broken x arm at CH4083 NOP between MC9 & MC6. lis 1806824.
682 | United 18/53 | United | 2018-12-05 | 0.66067 | -37.8129 | 145.1733 | 303 SPRINGFIELD ROAD, NUNAWADING VIC 3131 | 7037165 | NW 21 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1243691 | 20190114UTD_01 | A possum contacted live asseyts caught fire and landed on top of krone box LIS 7037165
683 | United 18/54 | United | 2018-12-13 | 0.5298 | -37.8279 | 145.1585 | 5 NAUGHTON GROVE, BLACKBURN VIC 3130 | 7035862 | NW 21 | 22kV AC | Urban | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1246753 | 20190121UTD_01 | private tree ok at the moment abt 400ml from HV, was only touching HV due to heavy rain, tracking caused smoke where tree was touching HV. 1 branch had burnt through & was on the groun
684 | United 18/55 | United | 2018-12-14 | 0.74155 | -38.2755 | 145.0243 | 14 GREENLAW CRESCENT, MOUNT MARTHA VIC 3934 | 1102908 | DMA24 | 22kV AC | Rural Short | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1247316 | 20181227UTD_01 | Cause was car into pole LIS# 1102908 in Greenlaw Cres. Wood pole with steel x-arm Inter /angle. HV conductor was knocked off insulator and made contact with Cypress tree and burnt 2 braches
685 | United 18/56 | United | 2018-12-15 | 0.95951 | -37.9156 | 145.0604 | 198 EAST BOUNDARY ROAD, BENTLEIGH EAST VIC 3165 | 2334491 | OR 24 | 11kV AC | Urban | - dropper / bridge | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1247640 | 20190121UTD_02 | Possum flashed over and caused a flashover on a pole -MFB reported pole on fire but was out by the time crew arrived.
686 | United 18/57 | United | 2018-12-17 | 0.29251 | -37.9162 | 145.0048 | 18 HAMMOND STREET, BRIGHTON VIC 3186 | 1804900 | NB 25 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1247853 | 20181227UTD_02 | A Pole Mounted FMJB for neutral screen cable across road out of HAMMOND HAMPTON blew up. Athis caused a small grass fire which was promptly extinguished
687 | United 18/58 | United | 2018-12-22 | 0.088519 | -38.2571 | 145.1896 | 1510 FRANKSTON-FLINDERS ROAD, TYABB VIC 3913 | 1108044 | HGS33 | 22kV AC | Rural Short | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1249550 | 20181227UTD_03 | 22kv insultor polymeric need to be replaced and also the LV tee off xarm fire report # 6827. LIS # 1108044. Pole missing 1/3 thickness at LV t off x arm.
688 | United 18/59 | United | 2018-12-27 | 0.91531 | -37.8969 | 145.1043 | FERNTREE GULLY ROAD, OAKLEIGH VIC 3166 | 2324619 | OAK35 | 11kV AC | Urban | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1250584 | 20190111UTD_01 | A possum flashed over HV at anchor pole PO-2324619 breaking wrap on and dropping conductor into the LV dropping the OHC to the ground causing a small grass fire.
689 | United 18/60 | United | 2018-12-29 | 0.67639 | -37.7668 | 145.1362 | 16 BAMFIELD CLOSE, TEMPLESTOWE VIC 3106 | 7060057 | BU 09 | Low voltage AC (<1kV) | Urban | - underground cable | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1250886 | 20181231UTD_01 | UG pillar has melted upillar had caught fire due to failed connection inside wall next to pillar was blackened. no burn marks on ground. fire report# 3010. Lis 7060057 - street light pole next to Pillar
690 | United 18/61 | United | 2019-01-01 | 0.074618 | -37.9026 | 145.0436 | UNIT 2 14 ULUPNA ROAD, ORMOND VIC 3204 | 2322759 | BT 09 | Low voltage AC (<1kV) | Urban | - connection box | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1251214 | 20190102UTD_01 | Removed the jbox from poa and rapaired active and neutral connection at poa. UE j/box caused fire and damaged cust fascia and smoke damage to house.Supply on Fire ignition report num is 01567. LIS 8803375
691 | United 18/62 | United | 2019-01-15 | 0.35764 | -38.3776 | 144.8065 | 58 PENINSULA AVENUE, RYE VIC 3941 | 1303949 | STO14 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1254645 | 20190115UTD_01 | HV inter x-arm needs to be changed, LIS# 1303949, fire start, fire report to be provided by crew, cause elements mist/fog
692 | United 18/63 | United | 2019-01-16 | 0.6148 | -37.8503 | 145.0697 | 20 CUSDIN STREET, GLEN IRIS VIC 3146 | 2310837 | K 08 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1255253 | 20190118UTD_01 | fire start report#TBA fmb at pole end caught fire, replaced fmb and reterminated leads. test and left on. cause unknown
693 | United 18/64 | United | 2019-01-18 | 0.65037 | -38.3001 | 145.1536 | 265A HODGINS ROAD, HASTINGS VIC 3915 | 1106008 | HGS23 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | single phase | Started by lightning striking a distribution system or a part of a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 1255946 | 20190211UTD_06 | EIV advised 1540pm. new mter required. damage appears to be caused by lightning. Closest LIS 1106008
694 | United 18/65 | United | 2019-01-24 | 0.35417 | -38.3778 | 145.1404 | 8 LUXTON DRIVE, SOMERS VIC 3927 | 1107139 | HGS23 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | Very High | 1 | 1 | 1257480 | 20190124UTD_01 | UE responsible gum tree branch broken and resting on the HV OHC at LUXTON 1 SANDY POINT s/s. SSummer Auditor (Brett)witnessed Flames on branch whilst it was resting on the OHC. LIS 1107139
695 | United 18/66 | United | 2019-01-24 | 0.46647 | -38.1356 | 145.1291 | 78 DANDENONG ROAD W, FRANKSTON VIC 3199 | 3308696 | FTN14 | Low voltage AC (<1kV) | Urban | - connection box | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1257579 | 20190125UTD_01 | 3ph folcb at pole end, burnt out due to deterioration, tested ok & left on, lis 33008696,
696 | United 18/67 | United | 2019-01-24 | 0.55745 | -37.9067 | 145.0092 | MILROY STREET, BRIGHTON EAST VIC 3187 | 2333154 | NB 34 | Low voltage AC (<1kV) | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1257657 | 20190125UTD_02 | An Ampact Connection failed on LV CHP BLUE PHASE. Caused a grass fire which was quickly extinguished, beleive it is UE grass outside ZSS. LIS 2333154
697 | United 18/68 | United | 2019-01-24 | 0.82367 | -37.9025 | 145.0686 | 31 DALNY ROAD, MURRUMBEENA VIC 3163 | 2315112 | OR 35 | Low voltage AC (<1kV) | Urban | - dropper / bridge | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1257876 | 20190125UTD_03 | Replaced blue phs tx lead, lead burnt off and started ground fire, 1-1.5 sqr mtr on nature strip, was out on arrival. Fire start report , photos obtained, LIS 2315112
698 | United 18/69 | United | 2019-01-27 | 0.65227 | -37.9988 | 145.2561 | 41 FRAWLEY ROAD, HALLAM VIC 3803 | 616529 | DN 22 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1259338 | 20190130UTD_01 | LIS#: 0616529 - Fire ignition report filled out (9740) - small grass fire started where conductors met ground <2m sq out front of #41 Frawley Rd after truck brought them down
699 | United 18/70 | United | 2019-01-28 | 0.61677 | -38.0824 | 145.186 | FRANKSTON-DANDENONG ROAD, CARRUM DOWNS VIC 3201 | 3318989 | DVY24 | 22kV AC | Rural Short | - dropper / bridge | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | Very High | 1 | 1 | 1259452 | 20190130UTD_02 | Lis3318989, bird across LA's @ FS0047. LA's slightly blackened on sth side of switch. still intact and in service. remains of small grass fire observed in the vacinity. Fire report#00711. est 50m2, Grass.
700 | United 18/71 | United | 2019-01-30 | 0.56137 | -37.934 | 145.2173 | ILLAWARRA AVENUE, ROWVILLE VIC 3178 | 9339466 | LD 06 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1260132 | 20190131UTD_02 | Boom from excavator into HV, started small fire, photos obtained, LIS 9339466
701 | United 18/72 | United | 2019-01-30 | 0.70753 | -37.7744 | 145.1831 | SPRINGVALE RD, DONVALE | 7071454 | NW 13 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1260218 | 20190205UTD_02 | Tree on HV overhead Springvale Rd causing cable to fail and broken crossarms starting a small 2msq ground fire LIS 7071454 -near DT1208. HV conductors down, this is a separate event to Creek Rd Event
702 | United 18/73 | United | 2019-01-30 | 0.71181 | -37.8184 | 145.1961 | CREEK ROAD, MITCHAM VIC 3132 | 7030642 | RWT12 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1260219 | 20190201UTD_01 | Tree on HV overhead Creek Rd repoteted as burning (separate evnt to Springvale Rd Event) near LIS 7030642
703 | United 18/74 | United | 2019-01-30 | 0.73478 | -38.046 | 145.2266 | 875 TAYLORS ROAD, DANDENONG SOUTH VIC 3175 | 622594 | DVY24 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | Very High | 1 | 1 | 1260279 | 20190131UTD_03 | Fire igition report 9741 - small grass fire approx 2m sq was cause by hv conductors hitting the ground due to council tree - LIS 0622594
704 | United 18/75 | United | 2019-01-30 | 0.90069 | -37.9134 | 145.1167 | NORTH ROAD, CLAYTON VIC 3168 | 2332439 | OE-SVTS | 66kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1260234 | 20190201UTD_02 | 66kv h/v x-arm was on fire (not on fire when crew arrived) - fire ignition report #04451 (fire contained to x-arm only) - h/v term x-arm to be replaced - LIS 2332439
705 | United 18/76 | United | 2019-02-01 | 0.060417 | -38.1776 | 145.1656 | 250 ROBINSONS ROAD, LANGWARRIN VIC 3910 | 3310277 | TBTS-FTS | 66kV AC | Rural Short | - insulators | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 1261024 | 20190211UTD_03 | Also refer #1261039 per MFB, grass fire in area has damaged lis # 3310277 fire start whispir to be sent, Blue phase 66kv insul damaged causing leakage to base of pole small grass fire.
706 | United 18/77 | United | 2019-02-03 | 0.69653 | -37.8397 | 145.1836 | STEVENS ROAD, VERMONT VIC 3133 | 7031909 | NW 33 | Low voltage AC (<1kV) | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 1261667 | 20190211UTD_04 | White phase LV ampac connection for the south cct had burnt off @ lis # 7031909 - repaired - small burnt area approx 12inches X 12 inches fire report #03093 - caused by melting metal falling on ground.
707 | United 18/78 | United | 2019-02-04 | 0.74306 | -37.7583 | 145.1083 | PAMELA GROVE, TEMPLESTOWE LOWER VIC 3107 | 7068515 | BU 06 | 22kV AC | Urban | - fuse (powder filled) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1262122 | 20190211UTD_05 | replaced 20a pff blue phase hv fuse... small fire on ground possible due to fuse candelling and garbage bin fire. Fire report # 03094 - crew emailed photos to NCC Control Hv fuse had blown and fuse had candelled . Scorch marks on ground from fuse elements & poreclain . 23 Airds Rd Templestowe LIS 7068515
708 | United 18/79 | United | 2019-02-06 | 0.89674 | -37.9842 | 145.2446 | MARIE STREET, DOVETON VIC 3177 | 621692 | DN 10 | 22kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1263336 | 20190214UTD_01 | Pole fire in Marie St, 1 north of Louis St. Centre phase insulator breaking down and pole burning. Pole was burning down to the Telstra box. Replaced HV and LV x-arms on pole LIS 0621692. Asset only fire.
709 | United 18/80 | United | 2019-02-06 | 0.92014 | -38.3679 | 144.7696 | MELBOURNE ROAD, BLAIRGOWRIE VIC 3942 | 1316290 | STO21 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 1263429 | 20190214UTD_02 | T-off x-arm burnt through Melbourne Rd, cnr Kirkwood, LIS 1316290. HV conductor resting near LV. Splash marks on blue phase LV -
710 | United 18/81 | United | 2019-02-07 | 0.56758 | -37.95 | 145.175 | PRINCES HIGHWAY, SPRINGVALE VIC 3171 | 618315 | SVW55 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1263568 | 20190214UTD_03 | Pole lis # 0618315 fire ignition report #: 1097. Fire damage obseved in the vacinity of 10x5m - A vehicle has hit a telecommunications cable between lis 0618315 and 0629124 causing wire strand to flick up to the HV.
711 | United 18/82 | United | 2019-02-07 | 0.72388 | -37.9966 | 145.0737 | MONACO STREET, PARKDALE VIC 3195 | 9864653 | M 35 | Low voltage AC (<1kV) | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1263632 | 20190214UTD_04 | LV leads have burnt out, likely flames at some point due to 1st call comments and damage. No fire started on ground per crew, refer #1263633 - lis 9864653
712 | United 18/83 | United | 2019-02-11 | 0.49576 | -38.0331 | 145.2018 | HAMMOND ROAD, DANDENONG VIC 3175 | 623109 | DVY31 | Low voltage AC (<1kV) | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1264499 | 20190218UTD_01 | Truck has hit LV slack span causing Red phase conductor to fall to the ground starting a 30sqm grass fire. LIS 0624964
713 | United 18/84 | United | 2019-02-15 | 0.52435 | -38.1496 | 145.1152 | NEPEAN HIGHWAY, FRANKSTON VIC 3199 | 8819481 | FSH31 | Low voltage AC (<1kV) | Urban | - lamps (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1266284 | 20190220UTD_01 | 150W HP Sodium street light fire - LIS 8819481
714 | United 18/85 | United | 2019-02-18 | 0.30088 | -37.9141 | 145.1846 | COLUMBIA PARK PRE SCHOOL, 26-28 COLUMBIA DRIVE, WHEELERS HILL VIC 3150 | 614322 | MGE34 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1266695 | 20190305UTD_01 | Gum tree on Private property at 26-28 Columbia Dve dropped 3m branch across HV and was starting to burn. C/R shortened feeder and opened MGE34 CB and branch was flicked off with operating stick
715 | United 18/86 | United | 2019-02-25 | 0.83681 | -38.1061 | 145.1722 | 44 OGRADYS ROAD, CARRUM DOWNS VIC 3201 | 8814069 | FTN24 | Low voltage AC (<1kV) | Urban | - connector / termination | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1269387 | 20190227UTD_02 | Replcd white phase lv fused isolator 315 amp hrc white phase fuse & copper lead to the mains had burnt out and caused a small 1m grass fire under pole fire report # 6961 - O'Grady - Shearwater S/Stn lIS 8814069
716 | United 18/87 | United | 2019-02-25 | 0.96603 | -38.356 | 144.7584 | 2 LABUAN STREET, SORRENTO VIC 3943 | 1306287 | STO13 | 22kV AC | Urban | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1269343 | 20190226UTD_02 | White phase 15a BA fuse blown and HV ABC dropper from bottom fuse unit burnt out. (assumed molten metal caused ignition as small ground fire around base of pole (4m2). LIS 1306287 Labuan-Hughes S/Stn
717 | United 18/88 | United | 2019-02-28 | 0.83472 | -37.9364 | 145.0997 | 34 DALBEATTIE DRIVE, CLARINDA VIC 3169 | 2330277 | CDA22 | Low voltage AC (<1kV) | Urban | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1270485 | 20190304UTD_01 | t/x was not on fire - Repaired burnt red phs isol lead on t/x and also neutral lead - replaced 1phs grey twisted service to #25 Delbeattie Dr with new 2c black twisted service - nst'ed and passed - cuse: red phs and neutral rubbing together over time LIS 2330277
718 | United 18/89 | United | 2019-03-01 | 0.43681 | -38.2321 | 145.1911 | 6 BUSHY COURT, SOMERVILLE VIC 3912 | 1109065 | HGS33 | 22kV AC | Rural Short | - fuse (powder filled) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1270642 | 20190304UTD_03 | HV PFF operation . Fuse malfunction broken PF causing small fire at base of pole crew taking photos & doing fire report rep# 6941. 1 ph sub LIS 1108611
719 | United 18/90 | United | 2019-03-01 | 0.54167 | -37.9014 | 145.1033 | 5 WILLIAM STREET, OAKLEIGH VIC 3166 | 2325899 | OE 15 | Low voltage AC (<1kV) | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 19000090760 | 20190304UTD_02 | Human Error - LV Catenery flicked up into LV causing splashing and a small grass fire 2mSQ - lis 2325899
720 | United 18/91 | United | 2019-03-01 | 0.78683 | -37.8588 | 145.0711 | Brownell Rd between Ashburton Rd and Rosedale Rd | 2336334 | RD 04 | Low voltage AC (<1kV) | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1270887 | 20190423UTD_01 | Crew replaced burnt out Transformer LV Isol blade on White phase. Cause was combination of heat and elec overload.
721 | United 18/92 | United | 2019-03-02 | 0.36234 | -38.3608 | 144.8871 | 1491 POINT NEPEAN ROAD, ROSEBUD VIC 3939 | 1301093 | RBD22 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1271001 | 20190304UTD_04 | Mechanical failure of HV & LV x arms in Pt Nepean Rd RBD. see event 1271005 lis 1301093 & at 1301094 small fire started at base of pole 1X1 M. fire report being done by fault crew
722 | United 18/93 | United | 2019-03-02 | 0.70624 | -37.9008 | 145.0129 | 240 NORTH ROAD, BRIGHTON EAST VIC 3187 | 2305826 | BT 10 | Low voltage AC (<1kV) | Urban | - connector / termination | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1271119 | 20190305UTD_02 | Burnt out red ph IPC connection - 150mm copper thru 19325 Alum - fire cause council tree to catch fire - small fire only on branch - fire report #03665 - lis 2305826 - whisper sent
723 | United 18/94 | United | 2019-03-02 | 0.75556 | -37.9831 | 145.0713 | UNIT 1 112 WARRIGAL ROAD, PARKDALE VIC 3195 | 1809079 | M 35 | 11kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1271164 | 20190306UTD_01 | Xarm fire - replaced HV inter x-arm. 3 x HV insulators, and replaced 10mtrs of 19/200 copper conductor, restored 2300 - lis 1809079
724 | United 18/95 | United | 2019-03-03 | 0.76787 | -38.1861 | 145.1733 | 120 BARRETTS ROAD, LANGWARRIN SOUTH VIC 3911 | 3321371 | FSH32 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | Severe | 2 | 2 | 1271399 | 20190306UTD_02 | Fire ignition report Number 6727, caused by sparks from melted folcb, small grass fire approx 1 mtr square. whispir sent - lis 3321371
725 | United 18/96 | United | 2019-03-04 | 0.13772 | -38.3084 | 145.0323 | OLD MOOROODUC ROAD, DROMANA VIC 3936 | 1104930 | DMA24 | 66kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 1271429 | 20190306UTD_03 | REF TO# 1271428 -report of fire start by cfa see event 1271429. Patrol found bark on DMA 24 centre ph at lis 1104930. Old Moorooduc rd After emergency switching bark removed and appears to have significant burn marks. MTN-DMA 66kv line in on same pole. fire approx 30 X 40 M. Grass burn only no asset damage. Whispir sent, UE Emerg manager advised. Crew adv Photos obtained/fire report raised and details provided to NC.
726 | United 18/97 | United | 2019-03-05 | 0.044757 | -38.3352 | 144.9764 | PALM GROVE, DROMANA VIC 3936 | 8825277 | DMA21 | 66kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1271730 | 20190308UTD_01 | Sleeve let go at Heales RD & Pt Nepean Rd Dromana. This caused the conductor to clash LIS#8825277 Seacombe and Pen link freeway,starting a small grass fire. Fire Ignition report 04453, Photos Taken.
727 | United 18/98 | United | 2019-03-10 | 0.68715 | -37.9267 | 144.9943 | 44 NEW STREET, BRIGHTON VIC 3186 | 1805858 | MR 32 | 11kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1273660 | 20190320UTD_03 | X arm fire at LIS#1805858, req replacement. ASR except sth cct out of NEW N51-WOLSELEY - Fire Ignition Report #: 02525 EAP #47848 issued @ 1745 by DVL. Crew replaced hv inter x-arm and sleaved out damaged lv mains on red phs on south cct of NEW N51 WOLSELEY - Notification 1000701147. U/E Mgr: N Sequeira adv x-arm had burn marks but did not cause a fire elsewhere.
728 | United 18/99 | United | 2019-03-12 | 0.48252 | -37.9885 | 145.1025 | 17 SIBTHORPE STREET, MORDIALLOC VIC 3195 | 9116184 | MC 09 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1273955 | 20190328UTD_01 | X arm fire failed, light rain rotten, AP issued and repairs complteted. LIS = 9116184
729 | United 18/100 | United | 2019-03-19 | 0.51667 | -38.3334 | 145.0192 | 675 DUNNS CREEK ROAD, DROMANA VIC 3936 | 1307507 | DMA15 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 1275359 | 20190321UTD_01 | Truck pulled down Hv O/H ex Tee off conductors on private property LIS#1307507.. Can isolate spur via L/L/C's for repair. Tip truck has brought down HV conductors, HV to be repaired, SUB VINEYARD BITTERN isolated, Winery left off supply whilst repairs undertaken, details passed onto Tony Sidney to arrange urgent repairs to HV. DUEA# 1515, photos obtained. Emailed details to Wayne Kelly, mgmt to sent whispir RWORKS# 1000702729. OHC repaired / replaced and ASR to VINEYARDS BITTERN @20:10
730 | United 18/101 | United | 2019-03-25 | 0.6375 | -38.3531 | 145.0249 | 31 BOWRINGS ROAD, RED HILL VIC 3937 | 1308142 | DMA13 | 22kV AC | Urban | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | Very High | 1 | 1 | 1277685 | 20190328UTD_04 | Also ref TBL 1277502. Fire start whisper sent. High wind brought down council tree in Bald Hills Nature Reserve fell on HV line sparking grass fire, fire report #6962, photos sent to NCC Dispatch. NSR, 2 subs off for duration of repairs, damage bw lis 1308142 - 43. HV conductors brought down/damaged and require repair/resag, PM notification 1000703555 Zinfra DAO org construction to atend tonight, operator will be req to restore after works compl, repairs made and supply restoredsee T/E#1277502. replaced a 40a BA on blue phase
731 | United 18/102 | United | 2019-03-25 | 0.67569 | -38.0603 | 145.1828 | 316 Worsley Rd, Bangholme VIC 3175, Australia | 623721 | DVY24 | 22kV AC | Rural Short | - insulator tie wires / connections | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1277714 | 20190416UTD_01 | Wire down Worsley Rd. Small fire 2mx2m fire brigade on site when crew arrived. Whisper sent fire start. Fire Report #03745. replaced 1m of 7/080 cu OHC, cause failed at the HV Tie.
732 | United 18/103 | United | 2019-03-25 | 0.74258 | -38.3283 | 144.9737 | 2 NEPEAN HIGHWAY, DROMANA VIC 3936 | 8825074 | DMA14 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1277811 | 20190328UTD_02 | Refer # 1277759 HV crossarm broken at LIS#8825074. Pole + xarm fire, fire report #02543. crew replaced pole lis#8825074.
733 | United 18/104 | United | 2019-03-29 | 0.67366 | -37.8911 | 145.1884 | 71 Madigan Dve, Glen Waverley | 612985 | MGE23 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1279282 | 20190429UTD_01 | Private Tree branch over HV in Madigan Cnr Waverly Rd & conductor damaged requiring repair. LIS 0612985
734 | United 18/105 | United | 2019-03-30 | 0.32008 | -37.9192 | 144.9905 | 12 Dendy St, Brighton | 1804866 | NB 35 | 11kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1279435 | 20190416UTD_05 | HV inter x-arm burnt off at arm strap at T-Off pole LIS 1804866 DENDY ST, cnr RAMSAY ST. Replaced Inter x-arm at T-off, Insulators replaced and conductor sleeved. Work completed under Access Permit. Fire Start- Fire Ignition report # 3095 not # 1000704184 Whispir sent
735 | United 18/106 | United | 2019-03-31 | 0.76271 | -38.3616 | 144.7807 | 2811 POINT NEPEAN ROAD, BLAIRGOWRIE VIC 3942 | 1302637 | STO23 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1279708 | 20190424UTD_01 | REF TO# 1279731 no fire strat - xarm burnt through via consistant tracking on the 22Kv - replaced HV inter x-arm. Replaced burnt out 400a krone box LIS# 1302637 PN# 1000704256
736 | United 18/107 | United | 2019-04-03 | 0.12361 | -37.9368 | 145.1428 | 24A Westall Rd, Westall | 629253 | SV 16 | 22kV AC | Urban | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1280721 | 20190424UTD_04 | Approx 8m squared grass fire caused by this fault, fire brigade attended and extinguished duty officer advised @ pole 0629253 - FHV spreaders required lis 0629253-0629254
737 | United 18/108 | United | 2019-04-03 | 0.35155 | -38.37 | 145.0072 | 241 Arthurs Seat Rd, Red Hill | 9863702 | DMA15 | 22kV AC | Rural Short | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 1280756 | 20190416UTD_06 | LIS 9863702, opp 241 Arthurs Seat Rd, Crew insp pole, no damage to pole, grass fire at base of pole (approx 40m sq), fire caused by possum. Fire out when crew arrived/MFB on site. Fire report #02045.
738 | United 18/109 | United | 2019-04-04 | 0.39028 | -38.2189 | 145.2415 | Opposite 71 East Rd, Somerville | 3300039 | HGS33 | 22kV AC | Rural Short | - transformer (pole mounted) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 1281179 | 20190429UTD_02 | Leaking oil from tx, and small grass fire started at base of pole, mfb have extinguished. 1m2 fire start. 5-6m2 of oil on ground. Fire repor# 02046 photo's taken and emailed.
739 | United 18/110 | United | 2019-04-06 | 0.49015 | -37.9111 | 145.0378 | 169 MCKINNON ROAD, MCKINNON VIC 3204 | 2326708 | BT 15 | Low voltage AC (<1kV) | Urban | - overhead service conductor (residential) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1281852 | 20190520UTD_01 | Servicewire has caught fire at poa, supply is off, fire is out. business name is Som of a Burch, next to train station.replaced simpi crimp on active connection at POA, supply restored, overlaod LIS 2326708
740 | United 18/111 | United | 2019-04-21 | 0.91353 | -38.4777 | 144.9931 | 2080 BONEO ROAD, FLINDERS VIC 3929 | 1313131 | DMA23 | 22kV AC | Rural Short | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 1285605 | 20190506UTD_02 | Top of pole broken and fell down, pole top fire extinguished by CFA on site. center ph dressing down insulator tracking onto x-arm caused fire due to dirt on insulator and light rain at the time. LIS 1313131
741 | United 18/112 | United | 2019-04-24 | 0.33436 | -38.0028 | 145.2268 | 23-25 SOUTH GIPPSLAND HIGHWAY, DANDENONG SOUTH VIC 3175 | 8813163 | DN 02 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1285992 | 20190510UTD_01 | LIS 8813163 FOLCB burnt out/no fire present other than at FOLCB, MFB attended to extinguish. Crew repl FOLCB, repaired cables, rFire report 01484, Photos taken, to be sent to NCC Dispatch inbox
742 | United 18/113 | United | 2019-04-26 | 0.31876 | -38.3612 | 144.7816 | 2801 POINT NEPEAN ROAD, BLAIRGOWRIE VIC 3942 | 1302382 | STO23 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1286296 | 20190510UTD_02 | lis# 1302382 - point nepean rd 1 pole east of st johns wood. opp 2801 Pt Nepean Rd Blairgowrie Crossarm Fire at strap bolt
743 | United 18/114 | United | 2019-05-07 | 0.91667 | -37.8659 | 145.0758 | 32 MUNRO AVENUE, ASHBURTON VIC 3147 | 8802981 | EM 05 | 11kV AC | Urban | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1289623 | 20190514UTD_01 | Tree on HV 28 Munro Av. Council tree o/s 32 Munro, white & red phase conductor repaired, Tree Branch caught fire within 1 metre of lines
744 | United 18/115 | United | 2019-05-13 | 0.596 | -37.8682 | 145.06 | 1889 MALVERN ROAD, MALVERN EAST VIC 3145 | 2317286 | K 13 | Low voltage AC (<1kV) | Urban | - connector / termination | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1291106 | 20190523UTD_01 | lis: 2317286 ipc connection caught fire and needs to be replaced 1889 malvern rd malvern east
745 | United 18/116 | United | 2019-05-17 | 0.86137 | -38.3753 | 144.774 | 31 MUNRO STREET, BLAIRGOWRIE VIC 3942 | 1304717 | STO21 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 1292812 | 20190523UTD_02 | replaced 3 phase folcb at pole end severely melted so lokely fire starts
746 | United 18/117 | United | 2019-06-03 | 0.7895 | -38.369 | 144.7712 | 403 MELBOURNE ROAD, BLAIRGOWRIE VIC 3942 | 1316285 | STO21 | Low voltage AC (<1kV) | Rural Short | - lamps (major road) | single phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1298656 | 20190702UTD_01 | At LIS # 1316285 there was a melted street light. needs replacement. street light isolated at the mains. See new TO # 1298672
747 | United 18/118 | United | 2019-06-06 | 0.38948 | -37.9395 | 145.1313 | 29 ROSEBANK AVENUE, CLAYTON SOUTH VIC 3169 | 629670 | SV 33 | 22kV AC | Urban | - fuse (powder filled) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1300030 | 20190704UTD_01 | crews have at rank rosebank - crew have replaced pff fuse at switch 810 caused by candling. LIS 0629670 Nomaly Feeder SV 33 but SV 20 on day of event
748 | United 18/119 | United | 2019-06-06 | 0.69575 | -38.3829 | 145.1703 | 46 SANDY POINT ROAD, SOMERS VIC 3927 | 1108920 | HGS21 | 22kV AC | Rural Short | - fuse (boric acid) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1300276 | 20190702UTD_02 | Centre phase (White) BA fuse unit damaged. F/Path side (Red phase) BA fuse blown. MT0513 LIS (1108920) is open and LLC's lifted on East side (fuse units). BA fuse had candled.
749 | United 18/120 | United | 2019-06-07 | 0.33293 | -38.395 | 144.8035 | 30 COORAMINTA ROAD, RYE VIC 3941 | 1305535 | STO21 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1300406 | 20190617UTD_01 | replaced 3ph FMB at lis # 1305535, Fire Report #6728, NST tested and left on
750 | United 18/121 | United | 2019-06-22 | 0.75397 | -37.9257 | 145.0352 | 94-106 PATTERSON ROAD, BENTLEIGH VIC 3204 | 1803554 | MR 14 | 22kV AC | Urban | - underground cable | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1305265 | 20190704UTD_03 | Cause: HV UGC steel box termination bushing failed at HV CHP in Patterson Rd corner North Ave (LIS# 1803554) c/t CH7638 PATTERSON N120 RAILWAY. (identified as not Cabus)
751 | United 18/122 | United | 2019-06-22 | 0.90486 | -37.7742 | 145.1478 | 8 FARRER COURT, DONCASTER EAST VIC 3109 | 7063437 | DC 02 | Low voltage AC (<1kV) | Urban | - underground cable | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1305363 | 20190704UTD_02 | lis: 7063437 - Crew isolated west cct out of s/s WOODLEA-GAUDION so that u/g crew can replace pillar out front off #8-#9 - Pillar Fire
752 | Powercor 18/19 | Powercor | 2018-04-07 | 03:52 | -37.41143132 | 144.59226608 | 124 Brougham Road, Mount Macedon 3441 | 32043129 | GSB014 | 22kV AC | Rural Short | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | INC-0002704 | 20180705PWA_01 | Customer reported wire down and grass fire at incident location and CFA attended to control 10m x 5m grass fire. Attending crew found a HV conductor had been brought down by a tree branch starting the fire. No injuries or property damage.
753 | Powercor 18/20 | Powercor | 2018-05-07 | 20:57 | -36.25063049 | 141.50053419 | 1860 Nhill-Yanac Road, Nhill | 32107074 | NHL031 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | INC-0002707 | 20180706PWA_01 | Vic Fire reported a transformer on fire at the incident location. On arrival the crew found the end of a 22kV strain crossarm had burned off and HV conductors were on the ground. There was no ground fire. no reported injuries or third party property damage.
754 | Powercor 18/21 | Powercor | 2018-08-07 | 21:55 | -34.77838000 | 142.65146000 | 3794B HATTAH-ROBINVALE ROAD, WEMEN 3549 | 30099965 | WMN013 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0002718 | 20180710PWA_01 | Customer reported a low conductor at the incident location. On arrival the crew found that a wooden intermediate cross-arm failed due to fire damage at a EDO fuse unit mounting position. conductor was adrift but remained suspended 4.0M above the ground. There was no ground fire, no reported injuries or third party property damage.
755 | Powercor 18/22 | Powercor | 2018-09-07 | 05:52 | -35.39086267 | 142.68413991 | Off Patchewollock - Sea Lake rd, Nyarrin | 30549570 | OYN005 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | INC-0004233 | 20190212PWA_02 | Following a line outage patrol found a pole fire at the incident location. There was no ground fire, no reported injuries or third party property damage
756 | Powercor 18/23 | Powercor | 2018-09-07 | 08:48 | -38.32014399 | 141.59648569 | 632 HENTY HIGHWAY, PORTLAND NORTH VIC 3305 | 33056439 | PLD004 | Low voltage AC (<1kV) | Rural Short | - luminaires (major road) | single phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | INC-0002711 | 20180712PWA_03 | Vic Fire reported a pole fire at the incident location. Upon arrival, the Powercor crew found that the street light caught fire at the incident location There was no ground fire, no reported injuries or third party property damage
757 | Powercor 18/24 | Powercor | 2018-09-07 | 03:10 | -34.24964943 | 142.20837013 | 3296 FOURTEENTH STREET, IRYMPLE VIC 3498 | 30098208 | RCT021 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0002719 | 20180710PWA_02 | Customer reported a low conductor and pole fire at the incident location. On arrival the crew found that a wooden intermediate cross-arm failed due to fire damage. There was no ground fire, no reported injuries or third party property damage.
758 | Powercor 18/25 | Powercor | 2018-12-07 | 09:12 | -38.25509991 | 141.62468009 | 10 SEGTNAN COURT HEATHMERE VIC 3305 (BOLWARRA) | 33204908 | PLD001 | Low voltage AC (<1kV) | Rural Long | - fuse (any other type) | single phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | INC-0004245 | 20190213PWA_02 | REC reported meter board fire due to burn fuse. There was no reported injuries
759 | Powercor 18/26 | Powercor | 2018-12-07 | 08:52 | -37.73599693 | 141.23970250 | 185 Uptons Road, Strathdownie | 32134589 | HTN002 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | INC-0002756 | 20180718PWA_06 | Customer reported Pole Fire at Myaring P43, HTN002. Crew attended and confirmed incident . There was no ground fire, no reported injuries or third party property damage.
760 | Powercor 18/27 | Powercor | 17/07/2018 | 10:40 | -38.33586304 | 143.60684439 | 2 Forest St Colac East | 32064073 | CLC003 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0002755 | 20180718PWA_05 | A Powercor contractor, Electrix, reported a P1 fault that was a pole fire at the incident location. Upon arrival, the Powercor crew found that the cross arm had been burnt through some time ago There was no ground fire, no reported injuries or third party property damage.
761 | Powercor 18/28 | Powercor | 17/07/2018 | 12:50 | -37.69976944 | 143.07487645 | 3399 Woorndoo Streantham Rd Streantham | 30356380 | ART033 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | INC-0002749 | 20180718PWA_01 | A passer-by advised a ground fire at the incident location. On arrival the Powercor crew found that a HV conductor lying on the ground. There was a ground fire, no reported injuries.
762 | Powercor 18/29 | Powercor | 20/07/2018 | 10:13 | -36.58119430 | 145.00326633 | 115 Moora Rd, Rushworth | 30127332 | SHP014 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | INC-0002779 | 20180723PWA_01 | Crew attended a reported supply outage. They found the HV EDO tube had candled and fallen to the ground. There was no ground fire, no reported injuries or third party property damage.
763 | Powercor 18/30 | Powercor | 20/07/2018 | 07:35 | -35.25506407 | 141.58778429 | 710 Boinka South Rd, Boinka | 32140466 | OYN001 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | INC-0002780 | 20180723PWA_02 | Customer reports outage and pole in paddock on ground. crew attended and found P35 Boinka Sth S/L on ground, burnt off at butt. There was no reports of injuries or third party property damage.
764 | Powercor 18/31 | Powercor | 22/07/2018 | 12:32 | -38.18116 | 144.570648 | O/S 14 Buccleugh St, Drysdale | 30065961 | DDL013 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0002783 | 20180723PWA_04 | A customer reported a pole fire at incident location. There was no ground fire, no reported injuries or third party property damage.
765 | Powercor 18/32 | Powercor | 28/07/2018 | 13:09 | -38.27265139 | 144.61929393 | 18 Nelson Rd, Pt Lonsdale 3225 | 33044427 | DDL012 | 22kV AC | Rural Short | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0002850 | 20180802PWA_01 | Customers reported to Powercor "dim lights and motor driven appliances struggling to work". When crews arrived they found a EDO fuse carrier had candled on pole type transformer at the incident location. No evidence of ground fire was found. No injuries or 3rd party property damage was reported.
766 | Powercor 18/33 | Powercor | 2018-04-08 | 15:55 | -38.37690879 | 142.46892477 | 312 Koroit St, Warrnambool | 30283657 | WBL004 | 22kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0002967 | 20180820PWA_02 | CFA reports a pole fire at the incident location. The crew identified a pole fire had occurred at switch pole 19B The site was safe and no ground fire, injuries or shocks were reported.
767 | Powercor 18/34 | Powercor | 2018-06-08 | 05:37 | -37.86059362 | 144.80030916 | 9 & 53 Slough Road Altona & surrounds ,VIC,3018, | 30141768 | AL011 | 11kV AC | Urban | - dropper / bridge | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0002871 | 20180807PWA_01 | A customer reported an explosion from power pole outside 9 Slough rd Altona. On arrival the crew found a possum had bridged across 11kv connections damaging cable termination. The fault current caused a HV conductor bridge to burn off nearby ( LIS 934164 53-65 Slough st)) falling particles ignited a grass fire at the base of the pole. Fault current damage was also sustained to islolators at pole ( Lis 1777) outside 2 Ajax rd altona, hot debris caused minor damage to a number of cars. There was no reported injuries.
768 | Powercor 18/35 | Powercor | 2018-10-08 | 11:11 | -34.31611439 | 142.18631761 | 147 Jacaranda St, Red cliffs | 31019705 | RCT023 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0002940 | 20180815PWA_03 | Customer reported conductor laying on crossarm, at incident location. A crew attended and found a previous crossarm fire had occurs at incident location There was no ground fire, no reported injuries or third party property damage.
769 | Powercor 18/36 | Powercor | 15/08/2018 | 01:53 | -37.44235538 | 144.60507472 | 212 Baringo Road, New Gisborne, 3438. south off this address in nature strip. | 33023842 | GSB012 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | INC-0002937 | 20180815PWA_02 | A Tree fell across conductors Between poles 9 and 10 of the water trust spur line. The conductors contacted the ground causing a 20 square metre grass fire. There were no reported injuries.
770 | Powercor 18/37 | Powercor | 19/08/2018 | 12:59 | -37.57985742 | 143.92401287 | 25 Stokes Road, Warrenheip | 32002534 | BATS-BAS2 | 66kV AC | Rural Long | - insulators | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | INC-0002968 | 20180820PWA_03 | Vic Fire reported sparking coming from pole, with broken insulator resting on the crossarm at the incident location . On arrival crew found that the centre phase 66kV insulator pin has sheared off at the "P" bracket, allowing the insulator with conductor attached to fall. The conductor fell and lay on the steel crossarm. The hanging insulator brushed the wood pole and burned the pole, requiring it to be replaced. There was no ground fire or any other damage caused by this incident.
771 | Powercor 18/38 | Powercor | 24/08/2018 | 09:23 | -34.18934098 | 142.14990775 | 168 Thirteenth st, Mildura | 32140356 | MDA032 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0004255 | 20190213PWA_05 | During patrol crew found burnt crossarm There was no ground fire, no reported injuries or third party property damage.
772 | Powercor 18/39 | Powercor | 2018-01-09 | 22:55 | -36.66834926 | 144.15614404 | 394 Vosti Rd Woodvale Vic 3556 | 33017991 | EHK024 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | within electric line construction area | 19.8 | No forecast | 0.1 | 1.98 | INC-0003056 | 20180903PWA_01 | CFA and landowner reported flames and smoke coming from pole. On arrival, crew found a junction box had melted and a small patch of burnt ground at the base of the pole, approx. 30cm x 30cm. There was no reported injuries or third party property damage.
773 | Powercor 18/40 | Powercor | 13/06/2019 | 0.33056 | -38.4618 | 142.9763 | 127 BROWNS ROAD, TIMBOON VIC 3268 | 33036205 | TRG003 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | INC-0007102 | 20190819PWA_06 | A customer reported a HV cable on the ground at the incident location. Upon arrival, a crew found that a large tree fell on to HV conductor and the conductor on the ground and a service line. An inspector was called as passible back fed HVI. However no damage or injuries found.
774 | Powercor 18/41 | Powercor | 2018-04-09 | 14:07 | -36.33303483 | 145.43177304 | Corner of Grahamvale & Northey Rd's Grahamvale 3631 | 30305074 | SHN024 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0003071 | 20180905PWA_02 | A pelican struck conductors, breaking conductors and initiating a small grass fire. There was no reported injuries or third party property damage.
775 | Powercor 18/42 | Powercor | 2018-07-09 | 23:00 | -37.28275197 | 142.93509007 | 83 High St Ararat | 30339108 | ART031 | Low voltage AC (<1kV) | Rural Short | - fuse (any other type) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0003115 | 20180911PWA_02 | Report received of fuse on meter panel was smoking and sparking which has since stopped. On arrival crew found meter board fuse had melted and evidence of burning on meter board. There was no ground fire, no reported injuries or third party property damage.
776 | Powercor 18/43 | Powercor | 2018-12-09 | 10:00 | -37.69902 | 143.558975 | 49 Linton-Naringhil Road, Linton.3360. | 30009044 | BAS021 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | INC-0003148 | 20180913PWA_02 | A tree fell down across conductors between Lintonpark P1 & P2. The conductor on the ground has caused grass and dead tree to ignite resulting in a small fire about 3m2 area burnt. There was no injuries reported.
777 | Powercor 18/44 | Powercor | 2018-12-09 | 05:30 | -37.7051 | 143.9809 | 6206 Midland Highway, Clarendon, 3352. | 31037826 | BAS022 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | INC-0003150 | 20180913PWA_01 | A new wooden pole was erected mid-span between Buninyong-P211 and P211A . During the night strong winds have pushed conductors against this pole (conductors had not yet been tied to insulators / pole undressed) resulting in pole catching fire. There was no ground fire and no injuries as a result of this incident.
778 | Powercor 18/45 | Powercor | 14/09/2018 | 18:17 | -37.65620324 | 144.46394920 | 100 Oconnell Road, Merrimu, 3340 | 33072519 | BMH006 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | INC-0003157 | 20180918PWA_01 | A passerby reported pole in front of this premise is on fire. Upon arrival the crew had found that the Pole Box/FOLCB opposite, 100 Oconnell Road, Merrimu, had overheated, causing the FOLCB to melt and burn away. The resultant hot melted plastic from the FOLCB above had fallen onto the ground below causing a small grass fire near the base of the pole approximately 50m² total area. There was no reported injuries or third party property damage.
779 | Powercor 18/46 | Powercor | 16/09/2018 | 20:13 | -38.32622583 | 144.32369113 | 45 Fischer Street Torquay | 32087132 | WPD032 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0003214 | 20180926PWA_01 | CFA communications reported a pole fire. Attending crew found that a pole mounted LV fuse box had overheated There was no ground fire, no reported injuries or third party property damage.
780 | Powercor 18/47 | Powercor | 18/09/2018 | 21:28 | -35.18596789 | 143.26389804 | Chinkapook - Nyah W, Nyrraby | 32155442 | SHL002 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | INC-0004266 | 20190213PWA_06 | During outage crew located a pole fire at pole 88 Manangatang line There was no ground fire, no reported injuries or third party property damage.
781 | Powercor 18/48 | Powercor | 18/09/2018 | 21:39 | -35.25154000 | 143.53665000 | 335 Tyntynder Central Rd, Tyntynder VIC 3586 | 32156894 | SHL004 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0003177 | 20180920PWA_03 | Vic-fire reported pole fire at incident location, upon arrival found that a cross-arm fire had commenced at the HV kingbolt position of an intermediate substation pole. The CFA extinguished the fire using an interrupted spray, stopping the fire prior to the cross-arm failing. There was no ground fire, no reported injuries or third party property damage.
782 | Powercor 18/49 | Powercor | 20/09/2018 | 19:15 | -36.75843542 | 144.26826556 | Corner of Don and Barnard Street BENDIGO (202 Don st ) | 30026909 | BET002 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0003231 | 20180927PWA_02 | Emergency services reported a pole fire at incident location. On arrival crew found overheated LV connection had ignited part of the pole top.. There was no ground fire, no reported injuries or third party property damage.
783 | Powercor 18/50 | Powercor | 23/09/2018 | 06:54 | -36.78065789 | 144.56728935 | 256 KNOWSLEY BARNADOWN ROAD, KNOWSLEY, VIC, 3551 | 30040888 | BGO023 | Low voltage AC (<1kV) | Rural Long | - fuse (any other type) | single phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | INC-0003247 | 20181002PWA_02 | Customer reported fire in meter box. On arrival crew found fire out and damage to meter board and fuse unit. There was no ground fire, no reported injuries or third party property damage.
784 | Powercor 18/51 | Powercor | 24/09/2018 | 08:37 | -37.8225 | 144.8344 | 19 Paw Paw Rd Brooklyn | 30117783 | BLT016 | 22kV AC | Urban | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0003241 | 20181001PWA_02 | Report from Fire services of pole fire and bin fire. There was also damage to a vehicle parked at the kerb. There was a ground fire (bin) . no reported injuries.
785 | Powercor 18/52 | Powercor | 28/09/2018 | 17:40 | -36.92647350 | 144.68757308 | 51 Chapmans Lane, Heathcote VIC 3523 | 33031625 | BGO023 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | INC-0003284 | 20181008PWA_02 | Customer reported supply interruption, upon arrival crew found that a EDO fuse tube had candled and burnt through. There was no ground fire, no reported injuries or third party property damage.
786 | Powercor 18/53 | Powercor | 2018-03-10 | 18:21 | -35.04164144 | 143.32383943 | 3566 Murray Valley Hwy, Piangil VIC 3596 | 32157328 | SHL002 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0003308 | 20181012PWA_01 | A passer-by reported arcing and some intermittent flame from a small branch blown into conductors at incident location. On arrival there was no evidence of ground fire, minor charring found on branch. There was no ground fire, no reported injuries or third party property damage.
787 | Powercor 18/54 | Powercor | 2018-04-10 | 18:34 | -37.68295474 | 144.58325150 | 318 HIGH STREET,MELTON,VIC,3337 | 30102707 | MLN023 | Low voltage AC (<1kV) | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0003321 | 20181015PWA_04 | Customer, from 298 High street Melton, reported a pole fire at the incident location. On arrival the crew found that an Low Voltage Insulated Piercing Connectors (IPC) had overheated resulting in burning of the IPC and the LV ABC bridge into the krone box. There was a small fire on the pole but had self-extinguished. There was no reported injuries or third party property damage.
788 | Powercor 18/55 | Powercor | 2018-05-10 | 10:15 | -37.8797646 | 144.733322 | 7 Chinook Way Point Cook 3030 | 34030537 | LV010 | Low voltage AC (<1kV) | Urban | - LV pillar | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0003278 | 20181005PWA_02 | Lend Lease employee reported a fire at the incident location, Upon arrival the crew found that the LV pillar partially burnt out. The fire was extinguished by the caller. The crew also observed that the pillar had been struck by a third party vehicle but no details are available. There was no ground fire, no reported injuries or third party property damage.
789 | Powercor 18/56 | Powercor | 2018-06-10 | 12:00 | -38.25295099 | 142.46596098 | 1351 WARRNAMBOOL-CARAMUT ROAD WINSLOW 3281 | 32198425 | KRT012 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0003282 | 20181008PWA_01 | Powercor received a report that a wire had been brought down by a truck. The attending crew found that a tip truck had contacted a HV line and had brought down the centre phase conductor.
790 | Powercor 18/57 | Powercor | 2018-07-10 | 11:07 | -37.943 | 144.674 | 400 K ROAD WERRIBEE SOUTH 3030 | 32171538 | WBE034 | 22kV AC | Rural Short | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0004530 | 20190613PWA_02 | HV Fuse candled and caught fire. Fire incident found during outage data review. No ground fire
791 | Powercor 18/58 | Powercor | 2018-08-10 | 09:43 | -37.92709600 | 144.15650041 | 482 Maude-She Oak Rd Maude | 30070761 | GL015 | 22kV AC | Rural Long | - pole (concrete) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0003290 | 20181009PWA_02 | An excavator hit power pole resulting clashing conductors in side the quarry near the incident location. Upon arrival the crew found that the broken conductors had fallen to the ground resulting in a small grass fire. CFA attended the site. There were no reported injuries or third party property damage.
792 | Powercor 18/59 | Powercor | 2018-08-10 | 13:31 | -37.76324822 | 144.62177495 | 231-239 Faulkners rd. Mount Cottrell 3024 | 32167519 | MLN011 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0003298 | 20181010PWA_01 | Customers at incident location reported loss of supply. On arrival a field crew found that a FSD had overheated and melted. Burning debris fell to ground and caused a small grass fire which self extinguished. There was no reported injuries or third party property damaged.
793 | Powercor 18/60 | Powercor | 2018-09-10 | 13:52 | -36.9476 | 141.6249 | 7332 Nhill-Harrow Rd, Miga Lake VIC 3409 | 32095476 | HSM004 | 12.7kV AC (SWER) | Rural Long | - fuse (EDO fuse) | single wire earth return (SWER) | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0004531 | 20190613PWA_03 | Candled EDO fuse (fire). Fire incident found during outage data review . No ground fire
794 | Powercor 18/61 | Powercor | 2018-09-10 | 19:39 | -35.24701225 | 143.47134948 | 171 GOODMAN ROAD, WOORINEN, VIC, 3589 | 32160058 | SHL004 | 22kV AC | Rural Short | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0003301 | 20181011PWA_01 | Vic fire reported a pole fire at incident location. The crossarm broke resulting in a small ground fire. There was no injuries or third party property damage.
795 | Powercor 18/62 | Powercor | 2018-10-10 | 14:46 | -36.14416189 | 145.54419106 | 690 Invergordon Rd Invergordon | 30150931 | NKA001 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0003329 | 20181016PWA_02 | Vic Fire reported a pole fire at the incident location. Upon arrival, the crew found that the substation pole ignited and burnt at bridging insulator. There was no ground fire, no reported injuries or third party property damage.
796 | Powercor 18/63 | Powercor | 2018-12-10 | 12:33 | -37.24809449 | 143.96003723 | 60 Stoney Rises Rd Smeaton VIC 3364. | 30000141 | BAN009 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0003311 | 20181012PWA_02 | An employ of Tuki Trout farm phoned in to report fire on the substation pole which supplies the trout farm. Crew attended to find a burnt out low voltage junction box, fire had self extinguished. There was no ground fire, no reported injuries or third party property damage.
797 | Powercor 18/64 | Powercor | 22/10/2018 | 12:32 | -37.84869800 | 144.78090000 | 60 - Harcourt Road, Altona, | 30236687 | LVN022 | 22kV AC | Urban | - overhead conductor (ABC) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0003373 | 20181023PWA_01 | A fault on the LVN22 feeder at 12:32 caused a feeder trip. A grass fire adjacent to pole LIS 994554 outside 70-72 Harcort Road, Altona was ignited when a high voltage ABC overhead cable (Non-metallic screened) faulted, then to fell onto the ground. There was no reported injuries or third party property damage.
798 | Powercor 18/65 | Powercor | 22/10/2018 | 12:32 | -37.84461341 | 144.78841066 | Kororoit Creek Rd Altona, Victoria (270 mtrs east of princes freeway) | 32173435 | LVN022 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0003374 | 20181023PWA_02 | An ABC conductor faulted and fell to ground outside 60 - Harcort Road, Altona. Secondary fault currents caused clashing of conductors adjacent to Kororoit creek rd which ignited two small grass fires on the nature strip. There was no reported injuries or third party property damage.
799 | Powercor 18/66 | Powercor | 30/10/2018 | 20:03 | -36.28133319 | 143.35581064 | Intersection of Watson Street and Back Street on St Arnaud Road, Charlton | 33015547 | CTN006 | 22kV AC | Rural Long | - crossarm (steel) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0003430 | 20181031PWA_03 | Vic fire reported small grass fire at incident location. On arrival crew found a bird has flashed over on ACR structure and fallen to ground igniting grass. there was no injuries or reported third party property damage
800 | Powercor 18/67 | Powercor | 31/10/2018 | 16:30 | -37.5737648 | 143.859512 | 617 Laurie st, Golden Point (Ballarat) | 32006305 | BAS023 | Low voltage AC (<1kV) | Rural Short | - underground cable | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0003441 | 20181102PWA_01 | Vic Fire reported wires sparking at the above address, on arrival the crew found a LV paper lead Cable head had failed, There was a small ground fire <1sqm, no reported injuries, or third party property damage.
801 | Powercor 18/68 | Powercor | 2018-01-11 | 15:02 | -37.75908209 | 144.80105961 | 273-275 Furlong Road, St Albans | 30115067 | SU012 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0003442 | 20181102PWA_02 | Powercor crews working only about 200m from the incident location heard a loud electrical noise and went to investigate. On arrival the crew found that a truck with a high load had contacted several communications cables in the street, with one cable flicking back over the 22kV HV overhead conductors. This then resulted in a small grassfire of approx. 10m2 on the nature strip. There were no reported injuries.
802 | Powercor 18/69 | Powercor | 2018-01-11 | 20:50 | -37.49718529 | 142.84656962 | Mortlake Ararat Road, near Malim Road, Rossbridge | 33049204 | ART033 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0003453 | 20181102PWA_04 | Vic Fire reported a grass fire at the incident location. On arrival the fault crew found that a bird had flashed over a 22kV insulator, attached to a steel crossarm on a concrete pole.
803 | Powercor 18/70 | Powercor | 2018-01-11 | 14:20 | -37.59870299 | 143.83131882 | 144 Grant Street, Sebastopol | 33003486 | BAS022 | Low voltage AC (<1kV) | Rural Long | - overhead conductor (ABC) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0003454 | 20181102PWA_05 | Following a report a fault crew attended the incident location. On arrival the crew found that Low Voltage flying bridges had failed causing sparks to drop into the grass on the edge of the road, igniting a small grass fire - in to order of 4 square meters. There were no injuries or any other damage. The fire had extinguished when the fault crew arrived.
804 | Powercor 18/71 | Powercor | 2018-01-11 | 17:16 | -37.34672745 | 143.40852017 | 450 Chute Waterloo Road, Waterloo | 30012734 | BAS011 | 12.7kV AC (SWER) | Rural Long | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0003445 | 20181102PWA_03 | Vic Fire reported a wire down and a grass fire at the incident location. On arrival the fault crew found that a cypress tree had fallen over HV conductors, which made contact with a post & wire fence, starting a grass fire - estimated at 4,000 square meters. The fire had been extinguished by the CFA when the fault crew arrived. There were no injuries or any other damage reported.
805 | Powercor 18/72 | Powercor | 2018-02-11 | 20:29 | -35.93294300 | 143.92402000 | 2221 LODDON VALLEY HWY - MACORNA | 31005685 | KGT003 | Earthing cable | Rural Long | - earth / earthing | single phase | Started in or originated from a distribution system | HBRA only | 1 | Severe | 2 | 2 | INC-0003478 | 20181108PWA_01 | A customer reported fire at base of pole. On arrival crew found that their was a small fire near the base of a SWER substation. There was no ground fire, no reported injuries or third party property damage.
806 | Powercor 18/73 | Powercor | 2018-06-11 | 06:39 | -34.59853500 | 142.78926000 | 32 Smith rd - Robinvale | 30095478 | RVL001 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0003484 | 20181109PWA_02 | Customers reported power failure. During patrol of line crew found a HV crossarm burnt off at incident location. There was no ground fire, no reported injuries or third party property damage.
807 | Powercor 18/74 | Powercor | 2018-06-11 | 09:48 | -37.54321073 | 143.85207689 | 3 Wood St, Ballarat | 30327257 | BAN013 | 22kV AC | Urban | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0003491 | 20181109PWA_05 | Vicfire reported a connection on fire at the incident location. On arrival the crew found that a HV insulated lead had contacted a surge diverter on the transformer, resulting in the lead catching fire. There was no ground fire, no reported injuries or third party property damage.
808 | Powercor 18/75 | Powercor | 2018-06-11 | 06:48 | -37.70086781 | 144.41674232 | 89 Kerrs Road Maddingley | 32175165 | BMH006 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0003488 | 20181109PWA_04 | Report received from a passerby of transformer fire on a pole. On arrival the fault crew found the centre 22kV crossarm had burnt through. There was no ground fire, no reported injuries or third party property damage..
809 | Powercor 18/76 | Powercor | 2018-09-11 | 07:50 | -37.29107456 | 144.51763630 | 22 Clerk Road, Carlsruhe, 3442. | 33108788 | WND023 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0003486 | 20181109PWA_03 | Vic fire attended this address and extinguished a fire on the pole and on the surrounding grass where burning debris had landed. Crew attended to find that the low voltage FOLCB had been burnt out,. There were no reported injuries.
810 | Powercor 18/77 | Powercor | 2018-09-11 | 11:00 | -38.28784818 | 144.33872223 | Blackgate Road Mount Duneed 3217 (near Surf Coast Road) | 32072179 | WPD022 | 22kV AC | Rural Short | - pole (wood) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0003495 | 20181112PWA_01 | Vic Fire reported wires down causing grass fire. On arrival at incident location crew found a vehicle registration No. YEU 948 had collided with LIS 33540 (Pole 6) knocking it down. A small grass fire started,
811 | Powercor 18/78 | Powercor | 2018-12-11 | 14:55 | -37.58316774 | 143.86438452 | Elsworth Street W, Golden Point | 33002388 | BAS013 | 22kV AC | Rural Short | - fuse (boric acid) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0003501 | 20181113PWA_01 | Powercor received a call from the CFA that a fire had started at the rear of the Soverign Hill complex by a Powercor Pole. A crew attended and determined that a bird had flashed over on a Boric Acid fuse unit. The bird fell to the ground starting a small ground fire (10 x 30 mtrs). There was no injuries or third party property damage.
812 | Powercor 18/79 | Powercor | 2018-12-11 | 19:17 | -38.20066 | 144.312775 | 179-193 COLAC ROAD GROVEDALE 3216 | 30068071 | WPD012 | 22kV AC | Urban | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0003503 | 20181113PWA_02 | CFA reported wire down and arcing and sparking. On arrival crew found that a HV ampac connection had over heated. Hot debris fell to ground resulting in a small grassfire (60m2)
813 | Powercor 18/80 | Powercor | 13/11/2018 | 08:52 | -37.23521021 | 142.20478758 | 6502 Heny Highway Glenisla | 30553863 | HSM002 | Earthing cable | Rural Long | - earth / earthing | single phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0004372 | 20190220PWA_03 | Customer reported Power pole smoking heavily at bottom of pole and burnt at top of pole. On arrival crew found SWER earthing was damaged. There was no ground fire, no reported injuries or third party property damage.
814 | Powercor 18/81 | Powercor | 13/11/2018 | 22:58 | -35.77806600 | 143.89248000 | 427 Old Kerang Rd, Kerang, VIC 3579 | 30025444 | KGT004 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very high | 1 | 1 | INC-0003537 | 20181119PWA_03 | Following on from a feeder operation to lockout a crew found a pole fire had occurred at the incident location. The crossarm had burnt through allowing the conductor to fall to ground. There was no ground fire, no reported injuries or third party property damage.
815 | Powercor 18/82 | Powercor | 13/11/2018 | 21:51 | -35.31009800 | 143.52459000 | 174 Bish Rd, Murrawee, VIC 3586 | 32161431 | SHL004 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0003535 | 20181119PWA_01 | Customer reported a pole fire at the incident location. Upon arrival the fault crew found that a 3 phase intermediate substation pole had a pole fire which burnt the intermediate crossarm. There was no ground fire, no reported injuries or third party property damage.
816 | Powercor 18/83 | Powercor | 13/11/2018 | 20:50 | -35.01621400 | 143.31255000 | 4686 MURRAY VALLEY HIGHWAY, Piangil VIC 3597 | 32157511 | BBD014 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very high | 1 | 1 | INC-0003536 | 20181119PWA_02 | Vicfire report pole fire near the incident location. Upon arrival fault crew found a pole fire had occurred, the pole had burnt internally. There was no ground fire, no reported injuries or third party property damage.
817 | Powercor 18/84 | Powercor | 14/11/2018 | 09:59 | -38.25075899 | 142.91831440 | 19 CEMETERY ROAD TERANG 3264 | 32058085 | TRG005 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0003610 | 20181129PWA_02 | Vic Fire reported a pole fire at the incident location. Upon arrival, the crew found that the LV junction box on the pole caught fire. There was no ground fire, no reported injuries or third party property damage.
818 | Powercor 18/85 | Powercor | 16/11/2018 | 03:19 | -37.06664960 | 143.89371157 | 3080 Pyrenees Highway Moolort 3465 | 30023598 | MRO007 | 22kV AC | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0003525 | 20181116PWA_01 | Vic Fire reported grass fire and wire down at incident location. Crew found that the centre phase HV copper conductor had broken mid span at sleeve. There was a small grass fire (520 sqm), no reported injuries or third party property damage.
819 | Powercor 18/86 | Powercor | 20/11/2018 | 15:10 | -36.09901948 | 145.39824563 | 1750 WALSHS BRIDGE ROAD NUMURKAH 3636. (Pole northeast of this property.) | 33087281 | NKA002 | 22kV AC | Rural Long | - pole (concrete) | three phase | Started by lightning striking a distribution system or a part of a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0003549 | 20181121PWA_01 | Vicfire reported grass fire under pole at the incident location. Grass fire has been extinguished. Powercor fault crew found lightning had struck the overhead 22kV line causing damage to the pole top assets, debris from the strike has fallen onto grass igniting a small fire. There was no reported injuries, no third party property damage.
820 | Powercor 18/87 | Powercor | 20/11/2018 | 14:04 | -36.19539968 | 144.91376988 | 7840 Murray Valley Hwy Koyuga 3622 | 30125489 | KYM-ECA2 | 66kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0003550 | 20181121PWA_02 | Vic Fire reported a grass fire at the incident location. Upon arrival, the fault crew found that the power pole top( LIS 26100) had been struck by lightning. The fallen debris caused small grass fire (10Sqm). There were no reported injuries or third party property damage.
821 | Powercor 18/88 | Powercor | 25/11/2018 | 07:24 | -38.29307251 | 143.16051599 | 527 Tesbury Road, Tesbury | 33036162 | CDN002 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0003611 | 20181129PWA_03 | Report received of pole fire at incident location. On arrival crew found burnt out FSD. There was no ground fire, no reported injuries or third party property damage.
822 | Powercor 18/89 | Powercor | 26/11/2018 | 11:48 | -36.0527 | 145.3499 | 1421 Boals Rd Numurkah | 30347324 | NKA006 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0003590 | 20181127PWA_01 | Vic Fire reported a grass fire at incident location. On arrival crew found wind blown fencing material had struck line causing fire. There were no injuries or third party property damage.
823 | Powercor 18/90 | Powercor | 29/11/2018 | 04:58 | -37.84962044 | 144.84401913 | 350 MILLERS ROAD ALTONA NORTH 3025 | 30116049 | BLTS-AL | 66kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0003609 | 20181129PWA_01 | Vic Fire reported pole on fire near the intersection of Millers Road and Kororoit Creek Road. On arrival the crew found that a pole fire at the base of the 66kV center phase bridging insulator on pole LIS 5414 had caused it to break of and fall onto the cross-arm causing a 66kV line reclose. There was no ground fire, no reported injuries or third party property damage.
824 | Powercor 18/91 | Powercor | 2018-01-12 | 15:47 | -38.33736491 | 143.35766156 | 2103 Princes Hwy, SWAN MARSH 3249 | 30046605 | CDN002 | Low voltage AC (<1kV) | Rural Long | - overhead service conductor (other) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within electric line construction area | 19.8 | Very high | 1 | 19.8 | INC-0003615 | 20181203PWA_01 | Vic Fire reported a grass fire at the above incident location. When crews arrived they found a OH Service wire was in contact (rubbing) with a branch. A small grass fire had started on road reserve (4x 55m). there was no injuries or property damage reported.
825 | Powercor 18/92 | Powercor | 2018-02-12 | 12:38 | -35.88844759 | 144.24956795 | 660 Kerang-Leitchville Road Leitchville VIC 3567 [300m West of Pipers Road Leitchville] | 33021808 | CHA005 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0003648 | 20181205PWA_01 | A CFA inspector reported that at an unknown date it appears a bird flashed over on concrete pole substation at the incident location. The bird fell to ground igniting road side grass. There was no reported injuries or third party property damage.
826 | Powercor 18/93 | Powercor | 2018-05-12 | 19:16 | -36.40046258 | 144.23008989 | 9 Hocking Road Dingee | 32040819 | EHK024 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0003664 | 20181206PWA_02 | Vic Fire Reports small grass fire caused by sparks from pole at incident location. On arrival crew found small ground fire caused by a burn out porcelain fuse box. There was no injuries or third party property damage.
827 | Powercor 18/94 | Powercor | 2018-06-12 | 16:04 | -38.26054680 | 144.52450366 | 37 PRESIDENTS AVENUE,OCEAN GROVE,VIC,3226 | 33042035 | DDL011 | 22kV AC | Rural Short | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0003678 | 20181210PWA_02 | VICFIRE reported transformer on fire at this address. Attending crew found that HV insulated leads had overheated. No ground fire.
828 | Powercor 18/95 | Powercor | 2018-06-12 | 16:19 | -37.92800585 | 144.64857638 | 215 Farm Road, Cocoroc, 3030 (Approx. 500m south of Princes Freeway) | 30143067 | WBE024 | 22kV AC | Urban | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0003687 | 20181210PWA_01 | Grass fire occurred within the Werribee Treatment Plant near HV Gas Switch. The resultant fault-current ruptured a connection on the incoming underground cable interface and a grass fire was ignited.
829 | Powercor 18/96 | Powercor | 2018-08-12 | 20:37 | -38.1712 | 144.3234 | 2 HARRISON COURT, HIGHTON ,VIC,3216 | 30225004 | WPD011 | Low voltage AC (<1kV) | Rural Short | - overhead service conductor (other) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0004532 | 20190613PWA_04 | Pole top fire due to service line failure. Incident found during outage data review. No ground fire
830 | Powercor 18/97 | Powercor | 2018-09-12 | 01:11 | -37.7219 | 144.8344 | 20 CHURCH STREET,KEILOR,VIC,3036 | 31023832 | SA002 | Low voltage AC (<1kV) | Rural Short | - overhead service conductor (other) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0004534 | 20190613PWA_05 | Tree fire due to tree rubbing on service line. Incident found in during outage data review. 1 sqm ground fire
831 | Powercor 18/98 | Powercor | 2018-09-12 | 15:19 | -36.0026 | 143.5456 | 119 SMITHS ROAD BARRAPORT WEST 3537 | 30554617 | CTN001 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started by lightning striking a distribution system or a part of a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0004537 | 20190613PWA_07 | Pole fire due to lightning strike. Found during outage data review. Ground fire 300 sqm
832 | Powercor 18/99 | Powercor | 2018-09-12 | 12:31 | -36.47103700 | 144.99594000 | 570 JOHNSON ROAD,STANHOPE,VIC,3623 | 30256538 | SHP021 | 22kV AC | Rural Long | - fuse (boric acid) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0003829 | 20190103PWA_06 | Customer reported a possible fire on pole at incident location. On arrival the crew found a boric acid fuse had burnt out and failed to operate correctly. There was no ground fire, no reported injuries or third party property damage.
833 | Powercor 18/100 | Powercor | 2018-10-12 | 17:47 | -34.2474 | 142.196 | 269 BELAR AVENUE IRYMPLE 3498 | 30099314 | RCT021 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0004540 | 20190613PWA_09 | Cross arm fire due to leakage current. Incident found during outage data review. No ground fire
834 | Powercor 18/101 | Powercor | 2018-11-12 | 16:07 | -37.12667616 | 142.99131807 | 1846 Bulgana Road, Bulgana | 32118131 | STL007 | 12.7kV AC (SWER) | Rural Long | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by lightning striking a distribution system or a part of a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0003736 | 20181213PWA_02 | Vic Fire reported a grass fire caused by a fallen SWER conductor at the incident location. On arrival the fault crew found that the pole had previously been struck by lightning, and was split at the top. A grass fire - estimated at 60 hectares by CFA personnel present at the incident location - was ignited by the fallen conductor. The fire was extinguished by the CFA. There was no reported injuries
835 | Powercor 18/102 | Powercor | 2018-11-12 | 18:30 | -37.07236424 | 143.00152303 | 668 Joel South Road, Joel South | 30086384 | STL007 | 12.7kV AC (SWER) | Rural Long | - fuse (EDO fuse) | single wire earth return (SWER) | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0003738 | 20181213PWA_03 | Vic Fire reported a small grass fire at the incident location. On arrival the fault crew found that an EDO had "hung Up" dropping hot material to the ground, igniting a grass fire approx. 6m x 25m in area There were no reported injuries.
836 | Powercor 18/103 | Powercor | 13/12/2018 | 16:45 | -38.0941 | 144.216 | 325 BOOLEY ROAD GHERINGHAP 3331 | 30323976 | GL015 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0004542 | 20190613PWA_11 | Candled EDO fuse (fire). Incident found during outage data review. No ground fire.
837 | Powercor 18/104 | Powercor | 13/12/2018 | 08:00 | -37.93085458 | 141.27605283 | 59 RIVERVIEW TERRACE DARTMOOR 3304. | 30089400 | PLD003 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0003727 | 20181213PWA_01 | Crew attended the incident site and found that a cross-arm fire had burnt through the cross-arm on the footpath side of the pole. The insulator and end of the cross-arm with high voltage conductor attached came to rest on the low voltage cross-arm. Possible high voltage injection to some customers to be confirmed. There were no reported injuries
838 | Powercor 18/105 | Powercor | 13/12/2018 | 19:16 | -36.62837501 | 142.631893166327 | Gibson Street, Rupanyup | 32096251 | STL006 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0003743 | 20181214PWA_01 | At approx. 19:10hrs on 13/12/18 the Glenorchy ACR P125 tripped to Lockout. The Powercor patrolled the line and found that a X-arm fire had occurred on Gibson Street Pole 2. There was no ground fire, no reported injuries or third party property damage.
839 | Powercor 18/106 | Powercor | 14/12/2018 | 15:33 | -36.0525 | 141.8397 | DIMBOOLA-RAINBOW ROAD JEPARIT 3423 | 32120285 | NHL016 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0004543 | 20190531PWA_06 | Report received of a cross arm fire due to leakage current. Incident found during outage data review. There was no ground fire, no reported injuries or third party property damage.
840 | Powercor 18/107 | Powercor | 14/12/2018 | 23:25 | -38.7297 | 143.3769 | 375 Blue Johanna Rd. Johanna | 33039953 | CLC006 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0004546 | 20190531PWA_05 | Report received of a Pole mounted fuse box fire. Incident found during outage data review. There was no ground fire, no reported injuries or third party property damage.
841 | Powercor 18/108 | Powercor | 16/12/2018 | 08:15 | -38.1466 | 144.3527 | 242 LATROBE TERRACE GEELONG WEST 3218 | 30069174 | GCY014 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0004548 | 20190613PWA_12 | Cross arm fire due to leakage current. Incident found during outage data review. No ground fire.
842 | Powercor 18/109 | Powercor | 16/12/2018 | 18:25 | -37.77405610 | 144.08363342 | 454 Morrisons-Elaine Rd, Morrisons 3334 | 30001236 | BAS022 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0003762 | 20181217PWA_02 | A report was received from a customer that there was a fuse box fire on the transformer pole at the above location. A Powercor crew attended and determined that the LV fuse box on Simpson Spur Pole 4 had caught fire and melted. A small section of the pole sustained minor burn damage. There was no ground fire, no reported injuries or third party property damage.
843 | Powercor 18/110 | Powercor | 17/12/2018 | 00:34 | -36.0715 | 142.341 | 111A QUICKS ROAD BRIM 3391 | 32090705 | HSM003 | 12.7kV AC (SWER) | Rural Long | - fuse (EDO fuse) | single wire earth return (SWER) | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0004413 | 20190613PWA_13 | Candled HV EDO Fuse (Fire) Fire incident was found during outage data review. No ground fire
844 | Powercor 18/111 | Powercor | 17/12/2018 | 13:40 | -36.16661265 | 144.57102966 | 355 WILLOW GROVE ROAD KOTTA 3565 | 33079969 | ECA012 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0003764 | 20181217PWA_04 | Customer phoned in to report a grass fire has started outside the front of her property, caused by falling debris from the pole. On arrival the crew found that a EDO HV Fuse unit became overheated and dropped hot debris onto the dry grass below igniting a ground fire. Fire area was around 3 x 150m There was no reported injuries.
845 | Powercor 18/112 | Powercor | 19/12/2018 | 04:02 | -38.06323000 | 144.37690787 | 43 FAIRBAIRN DRIVE, CORIO VIC 3214 | 31012734 | FNS012 | Low voltage AC (<1kV) | Rural Short | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0003803 | 20181221PWA_02 | CFA crew attending a house fire at #33 Fairbairn drive identified a second fire on a nearby pole. Attending crew found broken LV isolator. discussion with CFA fire investigator and review of AMI information confirmed that LV isolator fire was unrelated to house fire. House fire is being treated as suspicious and CFA supporting VICPOL forensic investigations
846 | Powercor 18/113 | Powercor | 20/12/2018 | 14:50 | -36.51927340 | 145.03236589 | 3587 MCEWEN ROAD WARANGA SHORES 3612 | 30127581 | SHP014 | Low voltage AC (<1kV) | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0003804 | 20181221PWA_01 | Vic-fire reports conductor down and grass fire at incident location. Crew attended to find that a low voltage termination cross-arm had broken There was a small ground fire, no reported injuries
847 | Powercor 18/114 | Powercor | 21/12/2018 | 13:50 | -36.76664988 | 144.26630259 | 54 Thistle St Golden Square Vic 3555 | 30239616 | BET008 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0003852 | 20190107PWA_02 | Vicfire reported transformer fire at incident location. On arrival Crew found that the low voltage fuse unit had failed. There was no ground fire, no property damage and no injuries
848 | Powercor 18/115 | Powercor | 24/12/2018 | 11:23 | -38.41933223 | 144.17008276 | 22 O’Donohue Road Anglesea 3230 | 32071083 | WPD021 | 22kV AC | Rural Short | - dropper / bridge | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0003814 | 20181224PWA_01 | Vic Fire reported transformer sparking, starting grass fire near Angahook - Lorne State Park - Fire brigade onsite - REF: 8763 - LIS 29929. Crew found a burnt HV dropper/lead had failed which started a small 5m2 grass fire, CFA attended, no property damage, no injuries.
849 | Powercor 18/116 | Powercor | 29/12/2018 | 09:53 | -36.31259900 | 145.42288000 | 116 Verney North Road, Congupna VIC 3633 | 33092637 | SHN011 | 22kV AC | Rural Long | - transformer (pole mounted) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0003817 | 20190102PWA_02 | Customer reported fire at 116 Verney North road, Congupna. Upon arrival the fault crew found that a bird had flashed over substation pole P30 SHTS-NKA #1. The bird fell to ground igniting a grass fire of approximately 10M x 50M in area, CFA attended and extinguished the ground fire. There were no reported injuries, minor fence post damage.
850 | Powercor 18/117 | Powercor | 30/12/2018 | 13:30 | -37.70346534 | 143.64321470 | 155 GALATEA ROAD NEWTOWN (BALLARAT) 3351 | 33002011 | BAS021 | 12.7kV AC (SWER) | Rural Long | - fuse (EDO fuse) | single wire earth return (SWER) | Started by lightning striking a distribution system or a part of a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0003941 | 20190115PWA_03 | Customer reported following lightning strike pole caught fire. There was no ground fire, no reported injuries or third party property damage
851 | Powercor 18/118 | Powercor | 30/12/2018 | 23:56 | -38.13815079 | 143.00488833 | 308 Harrington Road, Glenormiston North 3265 | 32054677 | TRG001 | 22kV AC | Rural Long | - dropper / bridge | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0003813 | 20190102PWA_01 | Vicfire reported wires down causing approximately 100m x 100m grass fire, a crew dispatched to investigate. Upon arrival to the incident location, the lineworker identified evidence of a grassfire and a HV lead had come loose and burnt away from the HV bushing on the pole Tx. Made safe for repairs to be made during daylight hours.
852 | Powercor 18/119 | Powercor | 30/12/2018 | 21:52 | -38.76068445 | 143.6718 | 22 GREAT OCEAN ROAD, APOLLO BAY VIC 3233 | 32062525 | CLC006 | Low voltage AC (<1kV) | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0003816 | 20190102PWA_03 | Vic Fire reports a pole fire at the incident location, On arrival, the crew finds bare LV conductor has broken off and is laying on the ground, across the highway. Burns to the grass at the base of the pole were reported.
853 | Powercor 18/120 | Powercor | 30/12/2018 | 09:30 | -36.12766863 | 142.45822105 | Lah East Road Lah | 32113994 | HSM003 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started by lightning striking a distribution system or a part of a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0003864 | 20190107PWA_12 | A customer reported that a pole had been hit by lightning and was on fire. On arrival crew found pole partially destroyed, had been hit by lightning . Pole had caught fire but fire was extinguished by rain. There was no ground fire, no reported injuries or third party property damage.
854 | Powercor 18/121 | Powercor | 30/12/2018 | 09:50 | -37.7701 | 143.6874 | 585 Derwent Jacks rd Berringa 3351 | 30272578 | BAS021 | 12.7kV AC (SWER) | Rural Long | - fuse (EDO fuse) | single wire earth return (SWER) | Started by lightning striking a distribution system or a part of a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0003865 | 20190107PWA_13 | Customer reported following a lightning strike there was a pole fire at the incident location. On arrival crew found EDO fuse hung up and fire extinguished by rain. There was no ground fire, no reported injuries or third party property damage.
855 | Powercor 18/122 | Powercor | 31/12/2018 | 12:45 | -38.1683 | 144.7159 | 12 First Ave, St Leonards | 32087947 | DDL013 | Low voltage AC (<1kV) | Rural Short | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0004415 | 20190613PWA_14 | Transformer LV isolator burnt off causing small burn marks at base of pole. Incident found during outage data review. Small ground fire 0.1 sqm
856 | Powercor 18/123 | Powercor | 31/12/2018 | 13:38 | -37.29701504 | 143.49984527 | 2154 Beaufort – Lexton Road Lexton Vic 3352 | 30011244 | BAN006 | Low voltage AC (<1kV) | Rural Long | - overhead service conductor (other) | single phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0003820 | 20190102PWA_04 | Vicfire reported a pole fire caused a grass fire at incident location. On arrival crew found that a neutral screen service had ruptured at the pole end had started a grass fire. There were no reported injuries
857 | Powercor 18/124 | Powercor | 2019-03-01 | 17:35 | -37.12469600 | 142.84611000 | 105 MOUNT VIEW ROAD GREAT WESTERN 3374 | 32116024 | ART031 | 12.7kV AC (SWER) | Rural Short | - transformer (pole mounted) | single wire earth return (SWER) | Started by lightning striking a distribution system or a part of a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very high | 1 | 4.6 | INC-0003847 | 20190104PWA_13 | Customer reported pole was sparking and this caused a ground fire of approximately 1m² in the vicinity of the base of the pole. On arrival crew found that the transformer had failed. There was no reported injuries or third party property damage
858 | Powercor 18/125 | Powercor | 2019-04-01 | 21:47 | -37.25317800 | 142.71992000 | 190 Pollands Rd Moyston 3377 | 32091855 | ART033 | 12.7kV AC (SWER) | Rural Long | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Severe | 2 | 9.2 | INC-0003854 | 20190107PWA_03 | Vic Fire reported conductors down and grass fire. On arrival crew found a SWER conductor had fallen to ground starting a small grass fire, There was no reported injuries
859 | Powercor 18/126 | Powercor | 2019-04-01 | 0.92986 | -36.4547 | 145.2033 | 170 GIRGARRE EAST ROAD,TATURA,VIC,3616 | 33088618 | MNA021 | 22kV AC | Rural Short | - fuse (boric acid) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Extreme | 3.5 | 0.7 | INC-0004644 | 20190613PWA_15 | Customer reports sparking from pole top. On arrival crew found that a boric acid fuse had hung up and was candling. There was no ground fire, no reported injuries or third party property damage. Event found during outage data review.
860 | Powercor 18/127 | Powercor | 2019-06-01 | 01:33 | -37.62341584 | 143.87891315 | 1815 Geelong Rd, Ht Helen 3350 | 33000502 | BAS013 | 22kV AC | Rural Short | - surge diverter | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0003948 | 20190116PWA_03 | On 6/1/19 at approx. 01:33 hrs a possum caused a flashover on the cable head structure on Buninyong Pole 89 (LIS 342). The possum fell to the ground and caused a small ground fire covering an area of approx. 3 sq metres. The CFA attended and extinguished the fire. There was no third party damage or injury.
861 | Powercor 18/128 | Powercor | 2019-06-01 | 11:36 | -37.50402700 | 143.93443000 | 227 Clarkes Rd Glen Park 3352 | 30015277 | BAN008 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0003860 | 20190107PWA_09 | Vic Fire reported at pole fire at the incident address. on arrival crew found that a FOLCB had burnt at the substation pole. There was no ground fire, no injuries or third party property damage.
862 | Powercor 18/129 | Powercor | 2019-07-01 | 15:22 | -37.67291027 | 141.96157846 | 368 Partridges Rd Hamilton | 32128531 | HTN006 | 12.7kV AC (SWER) | Rural Long | - transformer (pole mounted) | single wire earth return (SWER) | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0003871 | 20190108PWA_01 | A customer reported a bird made contact with line at the incident location causing a small grass fire. Upon arrival, crew found that a bird flashover on SWER substation pole resulting in a small fire surrounding the pole base. The grass fire caused a minor damage to the property fence. There was no damage to the pole base. There was no reported injuries.
863 | Powercor 18/130 | Powercor | 2019-07-01 | 17:54 | -36.69669000 | 142.22955000 | 39 Riverside Rd Dooen 3401 | 32091134 | HSM005 | 22kV AC | Rural Long | - surge diverter | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0003877 | 20190108PWA_04 | A crow caused a flashover at a Lightning Arrestor on a gas switch pole and this resulted in a small grass fire of 5m² at the base of the pole. There was no reported injuries or third party property damage.
864 | Powercor 18/131 | Powercor | 2019-09-01 | 20:15 | -37.48987400 | 144.02660000 | 970 Black Swamp Rd Bullarook 3352 | 32013164 | BAN008 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0003907 | 20190111PWA_01 | Powercor received a report from a customer advising while attending to a pump for stock water he found a nearby wooden pole with evidence of a fire. He believed it had occurred in the last two days, almost burnt through and cross arm barely holding on, wires very low. Supply is still on. There was no ground fire, no reported injuries or third party property damage.
865 | Powercor 18/132 | Powercor | 2019-09-01 | 12:04 | -38.17971213 | 142.42247515 | 16 Reeves Rd Woolsthorpe 3279 | 33101473 | KRT012 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0003950 | 20190116PWA_05 | A Powercor fault crew reported a candled EDO unit at the incident location. There was no ground fire, no reported injuries or third party property damage.
866 | Powercor 18/133 | Powercor | 2019-11-01 | 12:31 | -36.44396081 | 145.00903470 | cnr of Midland Hwy and Middle Rd Stanhope | 30142962 | SHP014 | Low voltage AC (<1kV) | Rural Long | - overhead service conductor (other) | single phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0003925 | 20190114PWA_01 | Vic fire reported a grass fire at the incident location. Upon arrival, Powercor crew found that there was a grass fire that was caused by a fallen service with its junction box across the road. The crew believed the service was pulled down by an unknown high load. There was no reported injuries
867 | Powercor 18/134 | Powercor | 2019-12-01 | 11:11 | -35.22847500 | 143.47774000 | OUTSIDE TAMERESK 1528 MURRAY VALLEY HIGHWAY - BEVERFORD | 32160477 | SHL004 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | INC-0003938 | 20190115PWA_02 | During a patrol of assets after a feeder operation the remains of a crossarm fire was found at the incident location. there was no ground fire, no reported injuries or third party property damage
868 | Powercor 18/135 | Powercor | 14/01/2019 | 18:45 | -34.16516900 | 142.13744000 | 38-42 FLORA AVENUA - MILDURA | 31034166 | MBN023 | 22kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0003956 | 20190118PWA_02 | Report received of pole fire at incident location. On arrival crew found a transformer had failed, causing burning to conduits, leads and pole. There was no ground fire, no reported injuries or third party property damage.
869 | Powercor 18/136 | Powercor | 14/01/2019 | 15:34 | -37.70523162 | 144.6021 | 100-128 Ferris Rd, Cobblebank, 3338 | 34015306 | MLN021 | Low voltage AC (<1kV) | Rural Short | - luminaires (minor road) | single phase | Started in or originated from a distribution system | HBRA only | 1 | Very high | 1 | 1 | INC-0004001 | 20190124PWA_06 | Report from Vicfire of street light pole smoking. On arrival crew advised that lantern had failed internally which had caused the lantern to smoke. There was no ground fire, no reported injuries or third party property damage.
870 | Powercor 18/137 | Powercor | 15/01/2019 | 21:45 | -36.34749700 | 145.42547000 | 240 FORD RD - GRAHAMVALE | 33096318 | SHN024 | Low voltage AC (<1kV) | Rural Short | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | INC-0003951 | 20190117PWA_01 | An IPC overheated at incident location. Hot particles caused a small fire at base of pole. There was no reported injuries or third party property damage.
871 | Powercor 18/138 | Powercor | 16/01/2019 | 17:55 | -38.06223487 | 142.35840073 | "Kareela", 292 Kooringal Rd, HAWKESDALE Vic 3287 | 30347516 | KRT013 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0003954 | 20190118PWA_01 | Vic Fire reported a grass fire due to a pole fire at the incident location. When crews arrived they found a small grass fire (10m x 20m) had been started at the base of a pole by a failed LV junction box. There was no reported injuries.
872 | Powercor 18/139 | Powercor | 17/01/2019 | 18:03 | -36.35356734 | 142.35178191 | Moloneys Rd, Btn Kranzs rd and Ailsa Wheat Rd, Wallup 3401 | 30081906 | HSM001 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Severe | 2 | 2 | INC-0003959 | 20190118PWA_05 | Vicfire reported a fire on a pole at the incident location. On arrival the crew found that a cross arm fire had occurred on a 22kV intermediate pole which caused the cross arm to break and the conductors to fall to the ground, resulting in a ground fire (Approx. 2000 sqm) on the road reserve. Protection operated. CFA attended. There were no reported shocks or injuries.
873 | Powercor 18/140 | Powercor | 18/01/2019 | 11:00 | -35.88866422 | 144.09171209 | 302 BORELLA ROAD MINCHA WEST 3568. | 30027998 | CHA006 | 22kV AC | Rural Long | - transformer (pole mounted) | three phase | Started by lightning striking a distribution system or a part of a distribution system | HBRA only | 1 | Very high | 1 | 1 | INC-0003960 | 20190118PWA_06 | Powercor crew were restoring supply when a transformer failed at this address causing a small grass fire. 1m by 3m. Transformer required replacement. There were no injuries due to this incident.
874 | Powercor 18/141 | Powercor | 19/01/2019 | 15:03 | -36.66533642 | 145.24619535 | 60 Old Dargalong School Wahring | 32192254 | MNA034 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | Very high | 1 | 1 | INC-0003964 | 20190121PWA_01 | CFA reported tree on conductors and ground fire underneath. On arrival crew identified that a large tree of some 35 metres in height had fallen breaking conductors and starting a small ground fire. There were no reported injuries.
875 | Powercor 18/142 | Powercor | 21/01/2019 | 15:56 | -38.31430681 | 142.42928982 | 420 CONNS LANE YANGERY 3283 | 32195757 | KRT013 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0003969 | 20190122PWA_01 | Emergency services reported a pole and ground fire . The attending crew found that a pole fire had occurred on pole 1 and a grass fire of some 6 by 20 metres had occurred on the roadside grass. No injuries or direct damage was noted.
876 | Powercor 18/143 | Powercor | 23/01/2019 | 09:03 | -38.716 | 143.7297 | 5750 GREAT OCEAN ROAD,PETTICOAT CREEK,VIC,3233 | 32062627 | CLC001 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0004643 | 20190531PWA_07 | Report from customer of pole fire . Possibly lighning strike but not confirmed. 22kv crossarm burnt of at one end. There was no ground fire, no reported injuries or third party property damage.
877 | Powercor 18/144 | Powercor | 24/01/2019 | 20:24 | -37.71292241 | 144.56356815 | 4 Hume Avenue, Melton South | 30111841 | MLN011 | Low voltage AC (<1kV) | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0004008 | 20190125PWA_02 | Resident reported that pole outside his house had exploded, showering sparks on to the nature strip below resulting in a small grass fire (approx. 1.5m2 in total). Upon arrival the fault crew found that the Aluminium conductor bridging in one of the LV transformer bus isolators at pole LIS-108994 had melted and burnt through. There was no reported injuries or third party injuries.
878 | Powercor 18/145 | Powercor | 24/01/2019 | 18:44 | -37.7497 | 144.7637 | 99 Fairfax Circuit, Albanvale | 30103829 | SU022 | Low voltage AC (<1kV) | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0004005 | 20190125PWA_01 | Resident reported they heard a loud bang from the pole and smoke coming from the pole outside their property, and that there was a fire at the bottom of the pole and grass. The residents extinguished the small grass fire (approx 1m2) in the nature stri. When the fault crew arrived they found that the red phase LV transformer bus fused isolator at pole LIS-014081 had burnt out at the copper to aluminium connector connecting the isolator to the overhead conductor. There were no reported injuries or third party property damage reported.
879 | Powercor 18/146 | Powercor | 25/01/2019 | 09:57 | -36.9704 | 141.0929 | 2067 Wimmera Highway, Apsley VIC, Australia. On north side of the Highway. | 32120393 | CHM011 | 22kV AC | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Severe | 2 | 2 | INC-0004009 | 20190125PWA_03 | A wooden termination cross-arm broke on Aspley P 2 202 the incident location causing conductor clashing and a low conductor across the Wimmera Highway. Debris falling to ground is believed to have ignited a grass fire (61,000m2 burnt) which started at this point. This fire was subsequently extinguished by the CFA. A large truck passing under the low conductor has snagged the low conductor causing it to break and fall to the ground. There was no reported injuries.
880 | Powercor 18/147 | Powercor | 25/01/2019 | 16:33 | -37.87057320 | 144.80555980 | 32 Kookaburra St, Altona | 32167630 | AL006 | Low voltage AC (<1kV) | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | INC-0004018 | 20190129PWA_04 | Report received from Vic fire of wire down, arching and sparking. Upon arrival the fault crew found the copper tail on the white phase bus fused LV isolator had burnt through due to corrosion. Some sparks were splashed on to the dry grass below, with a very small area of grass scorched. There was no reported injuries or third party property damage.
881 | Powercor 18/148 | Powercor | 26/01/2019 | 02:06 | -37.49631611 | 144.51690070 | 81 HAIRES ROAD BULLENGAROOK VIC 3437 | 32043180 | GSB011 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0004013 | 20190129PWA_01 | Vic Fire reported trees down over wires and caused grass fire at incident location. On arrival crew found tree through single phase 22kv conductors and small grass fire between P3 & P4 . CFA extinguished 5m x 35m grass fire. There was no reported injuries or third party property damage.
882 | Powercor 18/149 | Powercor | 27/01/2019 | 09:22 | -36.34309749 | 145.20885497 | 920 Lilford Road, Gillieston 3616 (near Mulcahy Road) | 30127687 | SHTS-KYM1 | 66kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0004017 | 20190129PWA_03 | Following a 66kv line trip to lockout a PAL crew found a crossarm fire at the incident location. Crew found at SHTS KYM No 1 66kV Line P164, the road side insulator burnt off the x-arm, dropped down and clashed with another phase, small grass fire approximately 300mm x 300mm. There was no reported injuries or third party property damage.
883 | Powercor 18/150 | Powercor | 28/01/2019 | 16:54 | -36.29917134 | 145.48516005 | 447 CONGUPNA EAST ROAD CONGUPNA VIC 3633 | 33090392 | SHN024 | 22kV AC | Rural Short | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0004324 | 20190218PWA_01 | Customer reported red glow from top of transformer pole. On arrival crew found EDO fuse hung up and glowing. CFA attended site. There was no ground fire, no reported injuries or third party property damage.
884 | Powercor 18/151 | Powercor | 29/01/2019 | 13:02 | -37.86545979 | 144.82670993 | 48 David St, Altona. | 32164804 | AL012 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0004084 | 20190204PWA_03 | MFB called to report a pole fire at the incident location. On arrival the crew found that an FOLCB box on the pole had caught fire and was destroyed. There were no reported injuries, ground fire or third party damage.
885 | Powercor 18/152 | Powercor | 30/01/2019 | 18:57 | -34.25145509 | 142.162 | 36 COORONG AVENUE,IRYMPLE,VIC,3498 | 30096208 | RCT021 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | INC-0004057 | 20190201PWA_01 | Customers reported wires down at incident location. On arrival crew found a tree stem had broken and brought down two conductors causing a small ground fire. The stem broke approximately 1.2 m above the ground prior to falling toward overhead conductors.
886 | Powercor 18/153 | Powercor | 30/01/2019 | 13:28 | -36.47180147 | 145.33402665 | 308 Pogue Rd Toolamba | 33090668 | MNA034 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0004042 | 20190131PWA_01 | Vic Fire reported a ground fire at a pole base at the incident location. On arrival, the Powercor crew found a conductor down and small ground fire that was caused by lightning. There were no reported injuries or third party property damage.
887 | Powercor 18/154 | Powercor | 2019-01-02 | 17:48 | -36.39910812 | 145.41182360 | 16-18 Poplar Avenue, Shepparton VIC 3630 | 32192567 | STN021 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0004083 | 20190204PWA_02 | Emergency services reported a POA fire at IGA in Poplar Avenue, Shepparton. Upon arrival crew found that POA did fail due to excessive heat & was likely to have commenced burning as there was evidence of soot on the adjacent veranda façade. The CFA extinguished the POA fire using chemical retardant prior to the fault crews arrival. There was no reported injuries.
888 | Powercor 18/155 | Powercor | 2019-03-02 | 14:26 | -37.82311282 | 144.80645669 | 62 Pipe road, Laverton , 3026 | 33075857 | LVN032 | Low voltage AC (<1kV) | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | INC-0004080 | 20190204PWA_01 | Mike from DIAMOND VALLEY PORK PTY LTD reported a truck has clipped the mains wire in street, wire now down on ground across driveway, wire sparking. Power to this property is still on. On arrival the crew found that a truck had hit an Optus Service Cable, this resulted in the Optus cable detaching from one of the poles and falling down to the ground across the driveway of #62 Pipe road, Laverton. The crew advised that most likely the Optus Service Cable flicked up into the LV Bare Mains, causing sparking on the LV conductors as they noticed some splash marks on the red phase & neutral conductors. The sparks and probably hot debris that fell to the ground started a small ground fire on the dry grass, the fire extinguished by itself. There were no reported injuries or third party property damage.
889 | Powercor 18/156 | Powercor | 2019-03-02 | 16:42 | -36.08560996 | 144.11462039 | Bendigo - Pyramid Rd, Pyramid Hill 3575 - 1.3kM north of Mitiamo - Kerang Rd. | 31004471 | CHA006 | 22kV AC | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very high | 1 | 1 | INC-0004094 | 20190205PWA_02 | Vicfire reported grass fire caused by Network assets at the incident location. Upon arrival crew found that the roadside phase conductor broken. A ground fire ignited at the incident location.
890 | Powercor 18/157 | Powercor | 2019-03-02 | 16:30 | -36.48952761 | 144.23022553 | Bendigo - Pyramid Rd, Raywood 3570 - 200M Sth of Newton Rd | 30151753 | EHK024 | 22kV AC | Rural Long | - insulators | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very high | 1 | 4.6 | INC-0004089 | 20190205PWA_01 | Crews were in process of locating a fault on feeder when a ground fire was located at a pole mounted capacitor at the incident location. CFA attended and extinguished the fire. There was no reported injuries or third party property damage.
891 | Powercor 18/158 | Powercor | 2019-04-02 | 16:42 | -36.31376800 | 145.20181000 | 630 Lancaster - Mooroopna Rd, Gillieston VIC 3616 | 32191858 | KYM003 | Low voltage AC (<1kV) | Rural Long | - overhead service conductor (other) | single phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0004106 | 20190206PWA_01 | Vicfire reported fire caused by network assets. Upon arrival the fault crew found that a truck hit grey twisted service cable crossing the road, the cable broke approximately 30cm from the supply pole end, prior to the LV fuses operating arcing has occurred between active's & neutral conductors & material ejected by the arcing commenced a ground fire emanating at base of pole at the incident location. The CFA attended and extinguished the grass fire. There was no reported injuries.
892 | Powercor 18/159 | Powercor | 2019-05-02 | 18:14 | -36.75141900 | 144.25610000 | 1 Jason Street, Long Gully VIC 3550 | 33012138 | BET001 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0004108 | 20190206PWA_02 | Vicfire reported a pole fire at the incident address. Upon arrival the Powercor fault crew found that a bird had flashed over on the HV between the centre phase disc string and the fuse unit bracket, damaging the glass disc string which required replacing. The bird fell to ground and ignited 2 small grass fires near the base of the pole. There was no reported injuries or third party property damage.
893 | Powercor 18/160 | Powercor | 2019-05-02 | 18:11 | -36.66016600 | 143.91507000 | 236 NEWBRIDGE-BRIDGEWATER ROAD, BRIDGEWATER VIC 3516 | 32039868 | BET001 | 22kV AC | Rural Long | - surge diverter | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0004111 | 20190206PWA_03 | Customer reported loud explosion and smoke on their substation pole at the incident location. Upon arrival Powercor fault crew found that a ABB surge diverter had ruptured ( Polymer type MVK20 ). Material ejected from the arcing resulted in a very small burnt area at the base of the pole, less than 0.2m square. The customer doused the ground with a pail of water which extinguished the smoldering material. There was no reported injuries or third party property damage
894 | Powercor 18/161 | Powercor | 2019-06-02 | 01:00 | -38.73200779 | 143.64882454 | 420 Tuxion Rd, Apollo Bay | 32062167 | CLC007 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0004115 | 20190206PWA_04 | Vic fire reported a pole fire at the incident location. On arrival the crew found that the SWER strain substation pole had burnt off in the area of the transformer, resulting in the top section of the pole including the transformer falling to the ground. A small grass fire resulted and was extinguished by the CFA. A small amount of oil was spilt from the transformer, however no oil entered any drains or waterways. There was no other reported third party damage.
895 | Powercor 18/162 | Powercor | 2019-06-02 | 21:30 | -37.08444800 | 143.94589000 | 2613 Pyrenees Hwy, Moolort VIC 3465 | 30017086 | MRO007 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0004159 | 20190208PWA_03 | Vicfire reported pole fire at the incident location. Upon arrival crew found that a pole fire had occurred on a 66/22/LV pole, Carisbrook 144A. Pole fire occurred at position #3 crossarm kingbolt, but involved the LV crossarm also at the kingbolt position. All conductors remained aloft. No ground fire, 3rd party damage or injury transpired.
896 | Powercor 18/163 | Powercor | 2019-07-02 | 13:46 | -38.3134 | 143.3245 | 2317 PRINCES HIGHWAY (near Craigs Lane) STONYFORD VIC 3260 | 31009370 | CDN002 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | within electric line construction area | 19.8 | High | 0.5 | 9.9 | INC-0004154 | 20190208PWA_01 | Customer reported Transformer on pole has blown, making a "cooking noise" before it went off and is now quite dark and damaged at incident location. On arrival crew found one fuse blown and one hung up. There was a small fire at the base of the pole (1 sq metre). The fire was extinguished by the customer There was no reported injuries or third party property damage.
897 | Powercor 18/164 | Powercor | 2019-09-02 | 15:09 | -35.05598228 | 142.87709548 | On Mallee Highway west of the MANANGATANG TOWNSHIP SIGN | 32154472 | OYN003 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very high | 1 | 1 | INC-0004196 | 20190211PWA_03 | Report received from Vic Fire of wires down and grass fire at incident location. On arrival crew found the end burnt off a crossarm and a small grass fire (20 sq m) There was no reported injuries or third party property damage.
898 | Powercor 18/165 | Powercor | 2019-09-02 | 23:59 | -38.22399239 | 144.25018507 | 255 Reservoir Road, Waurn Ponds | 33046494 | WPD011 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very high | 1 | 4.6 | INC-0004182 | 20190211PWA_01 | During a fault patrol a crew found a conductor on the ground at the incident location. There was a small ground fire (30sq m). There was no reported injuries or third party property damage.
899 | Powercor 18/166 | Powercor | 2019-09-02 | 18:56 | -38.08390696 | 144.42237806 | 480 A Avalon Road, Avalon | 30242888 | FNS032 | Earthing cable | Rural Short | - earth / earthing | single phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | Very high | 1 | 1 | INC-0004215 | 20190212PWA_01 | CFA reported a pole fire at the above location. The crew attended and noticed the HV earth and the LV cable had been cut off at ground level and above head height on the pole. The cutting of the earth had started the pole fire. The fire was contained to the pole with no ground fire. CFA attended.
900 | Powercor 18/167 | Powercor | 2019-10-02 | 11:17 | -38.5662 | 142.8599 | Lot 67B Old Peterborough Road, Peterborough | 30251713 | WBL012 | 22kV AC | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0004192 | 20190211PWA_02 | CFA called regarding a grass fire at the above location involving our assets. The crew attended and found conductor damage due to a bird strike. conductor fell to ground causing a small ground fire. The fire was approximately 50M X 30M. There was no reported injuries.
901 | Powercor 18/168 | Powercor | 14/02/2019 | 11:06 | -36.3098 | 145.6283 | 30 SUTHERLAND ROAD COSGROVE 363 | 30129547 | STN024 | 12.7kV AC (SWER) | Rural Long | - fuse (boric acid) | single wire earth return (SWER) | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0004291 | 20190214PWA_07 | A passer-by reported a ground fire at the incident location. Upon arrival, the Powercor crew found that the HV fuse hung-up and approx. 2150Ssqm grass had been burnt and extinguished by the CFA. There was no reported injuries.
902 | Powercor 18/169 | Powercor | 14/02/2019 | 23:37 | -38.1491607529005 | 144.358660253967 | 126 RYRIE STREET, GEELONG VIC 3220 | 30266203 | GCY021 | Low voltage AC (<1kV) | Urban | - fuse (any other type) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0004320 | 20190215PWA_02 | REC for Restaurant owner advised that premises had part supply. Attending crew found burnt wooden meter board and fuse carrier.
903 | Powercor 18/170 | Powercor | 15/02/2019 | 10:30 | -37.45033262 | 144.01599994 | 151 MYERS ROAD DEAN 3363. | 32008548 | BAN008 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0004319 | 20190215PWA_01 | Property owner advised pole on fire at incident address. Crew attended to find pole top and conductors on ground. Pole burnt through at the cross-arm strap bolt. No ground fire and no reported injuries.
904 | Powercor 18/171 | Powercor | 16/02/2019 | 13:35 | -38.02914501 | 144.41890807 | 87 Archimedes Ave, Lara. | 32085956 | FNS022 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0004442 | 20190226PWA_02 | Vicfire reported a pole fire at the incident location. On arrival the crew found that a 3 phase Fused mains box had overheated resulting in melted debris falling to the ground. Due to green vegetation and bare earth at the base of the pole, the melted debris did not result in a ground fire. There were no reported injuries or third party damage.
905 | Powercor 18/172 | Powercor | 16/02/2019 | 00:26 | -38.5681 | 142.8596 | Paddock off Old Peterborough Rd, 2.5km East of Great Ocean Rd. | 30251712 | WBL012 | 22kV AC | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0004342 | 20190219PWA_01 | A Powercor Fault crew patrolling following an outage, discovered a dead swan in a paddock, beside a downed HV conductor. The conductor falling on the ground resulted in two small grassfires of approx. 600m2 total in size on private property. The fire self extinguished, due to dewy conditions. There were no reported injuries or other third party damage.
906 | Powercor 18/173 | Powercor | 17/02/2019 | 04:06 | -37.43206412 | 143.37846324 | 11 stuart st Beaufort 3373 | 33005424 | BAS011 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0004449 | 20190226PWA_05 | Following report from supply interruption crew found an EDO fuse fuse had candled before falling to the ground. There was no ground fire, no reported injuries or third party property damage.
907 | Powercor 18/174 | Powercor | 22/02/2019 | 14:20 | -38.44761892 | 143.72564100 | 390 Dewings Bridge Rd, Gerangamete, Victoria. | 33039445 | CLC013 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0004405 | 20190225PWA_01 | Vic-fire report fire under pole at incident location, caused by HV Fuse unit. On arrival crew found a burnt grass patch which had been caused by a crow which had flashed over on the center phase HV fuse unit. There was no reported injuries.
908 | Powercor 18/175 | Powercor | 23/02/2019 | 00:26 | -38.26978679 | 144.35033083 | 750 HORSESHOE BEND ROAD, MOUNT DUNEED VIC 3217 | 33041574 | WPD024 | 22kV AC | Rural Short | - insulators | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0004411 | 20190225PWA_02 | Vic Fire reported a grass fire start due to an animal fault at the incident location. When crews arrived they found a possum fault on a HV concrete anchor pole had started a grass fire (50m x 20m) mainly in the road reserve and onto farm land. The fire was extinguished by CFA crews. No injury, or 3rd party property damage other than superficial burning to some farm boundary fence posts and railings.
909 | Powercor 18/176 | Powercor | 25/02/2019 | 20:41 | -37.91173204 | 141.78380465 | 94 N Wallacedale Rd, BRANXHOLME 3302 (approx 900m east of Henty Hwy) | 31017267 | HTN002 | 22kV AC | Rural Long | - fuse (boric acid) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very high | 1 | 4.6 | INC-0004434 | 20190226PWA_01 | Customer reported a transformer fire and CFA in attendance at incident site. When crews arrived they found a HV Boric Acid fuse had "hung up. This resulted in a small grass fire (40m x 2m) along the road reserve that was extinguished by the CFA. No injuries or property damage reported
910 | Powercor 18/177 | Powercor | 25/02/2019 | 18:49 | -37.67281920 | 144.58751187 | 21 Kurunjang Drive, Kurunjang 3337 | 31025469 | MLN012 | Low voltage AC (<1kV) | Rural Short | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0004448 | 20190226PWA_04 | MFB Comms reported burnt wire, started a grass fire. brigade onsite On arrival the PCA Faults Crew have advised that a burnt out Blue Phase LV Isolator, Cu to Al D-Loop connection has overheated and caused sparks to fall onto the grassed area below. The resultant hot sparks above had fallen onto the ground/grassed nature strip below causing a small grass fire near the base of the pole (1m x5m). There was no reported injury or shocks as a result of this incident.
911 | Powercor 18/178 | Powercor | 25/02/2019 | 10:57 | -36.2738 | 144.5388 | 21 ALFRED CRESCENT,LOCKINGTON,VIC,3563 | 33085689 | SHP012 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0004477 | 20190227PWA_04 | Vic Fire reported a pole fire and smoke coming from just above the transformer at the incident location. Upon arrival the crew found the centre phase fuse hung up asa result of a bird flashover. There was no ground fire, no reported injuries or third party property damage.
912 | Powercor 18/179 | Powercor | 26/02/2019 | 20:37 | -38.41957828 | 143.83721486 | Murroon Rd (250m sth of Barholme Rd), PENNYROYAL 3235 | 30260049 | WIN011 | 22kV AC | Rural Long | - dropper / bridge | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0004462 | 20190227PWA_01 | CFA reported grass fire at incident location and requested Powercor attendance to check equipment as possible ignition source. When crews arrived they inspected the Regulator structure at P159 CLC-LRN line and found evidence of a hot spot on the center phase lead to the top of the disconnect switch on the south side of the pole. Molten PVC tubing was found on the ground. A grass fire of 30m2 had burnt along the road reserve and into private paddock and was extinguished by CFA crews. No injuries or property damage reported
913 | Powercor 18/180 | Powercor | 27/02/2019 | 18:51 | -37.85926126 | 144.69908237 | 42 Evrah Drive, Hoppers Crossing 3029 | 33072797 | LV009 | Low voltage AC (<1kV) | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0004496 | 20190228PWA_03 | PCA Faults Crew attended a fault call have advised that a burnt out Blue Phase Cu to Al D-Loop connection at incident location has overheated and caused sparks to fall onto the dry grassed area below. This has caused a small grass fire near the base of the pole. There was no reported injury or shocks as a result of this incident.
914 | Powercor 18/181 | Powercor | 27/02/2019 | 18:13 | -34.48499867 | 142.36342717 | Crown land opposite 2768 Kulkyne Way Nangiloc | 32149834 | RCT013 | Low voltage AC (<1kV) | Rural Short | - overhead conductor (insulated) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0004490 | 20190228PWA_02 | CFA called reporting grass fire at incident location. On arrival crew found fire of approx. 1000 m2 and part of the burnt area was under our pole. Insulation between D clamp and isolator had melted on LV cables, fallen debris ignited grass below. CFA and State Forest Management crews in attendance. There were no injuries or third party property damage.
915 | Powercor 18/182 | Powercor | 28/02/2019 | 14:41 | -35.67693435 | 143.40267487 | 4235 Lalbert–Kerang Road, Lalbert 3542 | 30019603 | SHL001 | 12.7kV AC (SWER) | Rural Long | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any other thing forming part of or coming into contact with a distribution system | HBRA only | 1 | Very high | 1 | 1 | INC-0004557 | 20190304PWA_02 | Report of wire has blown into conductors started fire at incident location. Crew found that a Willy Willy had blown some old tangled fencing wire onto the SWER overhead conductor. There was a ground fire of approx. 8000 sq m, there was no reported injuries, no asset damage.
916 | Powercor 18/183 | Powercor | 2019-01-03 | 20:18 | -36.48164682 | 145.2413 | 765 Dhurringile Road Tatura 3616 (corner Toolamba-Rushworth Road) | 33097279 | MNA021 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0004560 | 20190304PWA_03 | Reports received of small grass fire. On arrival crew found a limb had fallen through conductors between poles 9 & 10 at incident location. Disturbance to Conductors caused a small grass fire between poles 6 & 7. There were no reported injuries or third party property damage.
917 | Powercor 18/184 | Powercor | 2019-01-03 | 09:25 | -37.97242176 | 144.34854716 | 1225 BACCHUS MARSH ROAD,ANAKIE,VIC,3213 | 30228255 | FNS011 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | HBRA only | 1 | Very high | 1 | 1 | INC-0004574 | 20190305PWA_01 | CIVILEX VICTORIA reports while completing road works, an excavator in travelling mode has contacted an overhead conductor causing it to break and fall to ground. On arrival crew found Excavator hit line at driveway of 1225 Bacchus Marsh Road Anakie between LIS 986123 and LIS 986124. One conductor has fallen , there are burn marks at 7 individual sites where small fires started mostly spots. The fires were upstream caused by backfeed. There were no reported injuries
918 | Powercor 18/185 | Powercor | 2019-03-03 | 02:59 | -38.08191472 | 144.34109062 | 13 REDFEARN COURT, CORIO VIC 3214 | 30071844 | CRO013 | Low voltage AC (<1kV) | Rural Short | - underground service cable (other) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | INC-0004556 | 20190304PWA_01 | customer reported no supply and pole on fire. Attending crew found fused mains box on pole had overheated, burnt service cables and charred pole.
919 | Powercor 18/186 | Powercor | 2019-04-03 | 11:01 | -36.34701865 | 144.79579479 | 115 Gibson Road, Nanneella,3561, VIC, Australia. | 30121480 | KYM001 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0004562 | 20190304PWA_05 | Vicfire reported pole fire at incident location. On arrival the crew found that the pole mounted junction box had overheated and melted, Debris from this had fallen to ground and started a ground fire approximately 3m by 50m. Superficial damage to fencing posts. There was no reported injuries.
920 | Powercor 18/187 | Powercor | 2019-04-03 | 10:45 | -37.04151166 | 141.28734067 | 63 POWERS CREEK ROAD EDENHOPE 3318 | 33053008 | CHM011 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0004582 | 20190305PWA_03 | A report was received that bird has flashed over the HV EDO unit at the pole at the incident location. The bird fell to ground on fire and ignited a ground fire near the pole 20m by 60m ((1200m2). Fire extinguished by the CFA. There was no report of injury or third party property damage.
921 | Powercor 18/188 | Powercor | 2019-05-03 | 07:02 | -38.49477428 | 143.88839212 | 335 Benwerrin-Mt Sabine Rd Benwerrine | 33045906 | CLC005 | 22kV AC | Rural Short | - surge diverter | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0004594 | 20190305PWA_05 | CFA reported a fire at the incident location. Upon arrival, the Powercor crew found that a lightning arrestor on sub pole, CLC - LRN 217, had been damaged. There was a ground fire, no reported injuries.
922 | Powercor 18/189 | Powercor | 2019-06-03 | 00:51 | -38.14999813 | 144.33693454 | 88 Aphrasia street Newtown | 30074160 | GL022 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0004617 | 20190306PWA_05 | Emergency services report that cross-arm had burnt and insulator had fallen into conductors below. Attending crew found that a cross arm fire had occurred and high voltage injection damage was apparent
923 | Powercor 18/190 | Powercor | 2019-07-03 | 14:00 | -38.25994988 | 142.92604029 | COBDEN-TERANG ROAD TERANG 3264. 200meters south of Bend Road | 30043677 | TRG003 | 22kV AC | Rural Long | - surge diverter | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0004642 | 20190308PWA_02 | Report received of a bird flashover at the incident location. On arrival the crew found that a bird had caused a flashover between surge arrestor and its base. The bird fell to ground to ground starting a small grass fire. CFA extinquished the fire. There was no reported injuries.
924 | Powercor 18/191 | Powercor | 2019-08-03 | 18:50 | -37.72617287 | 141.98881075 | 377 Glenelg Hwy, Hamilton, 3300 | 32139027 | HTN006 | 22kV AC | Rural Long | - transformer (pole mounted) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0004656 | 20190312PWA_03 | CFA reported a transformer had started a grass fire at the incident location. On arrival the crew found an area 20x12m had been burnt. Wire was found on the transformer possibly from a bird attempting to build a nest. There were no reported injuries.
925 | Powercor 18/192 | Powercor | 2019-09-03 | 12:50 | -37.7363 | 144.7975 | 216 BIGGS STREET, ST ALBANS VIC 3021 | 30232994 | SA009 | 22kV AC | Urban | - overhead conductor (ABC) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0004653 | 20190312PWA_01 | Calls received from residents to report an outage in the area, with wires down and grass fire in Biggs St, St Albans. Upon arrival the fault crew found that a HV ABC had broken mid span and come to ground on the nature strip below, resulting in a grass fire on the nature strip as well as the grass within the front yard of unit 1 of 216 Biggs St. There was no reported injuries.
926 | Powercor 18/193 | Powercor | 2019-10-03 | 16:23 | -36.72604500 | 144.50466000 | 163 MCCORMICKS ROAD, FOSTERVILLE VIC 3551 | 33019088 | EHK031 | 22kV AC | Rural Short | - surge diverter | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0004655 | 20190312PWA_02 | Fosterville mine reported a grass fire coinciding with a part supply failure. Upon arrival the crew found that the transformer mounted porcelain surge diverter had failed & subsequently started a small ground fire of approximately 2M x 1M in size. The mine staff extinguished the fire, no injuries or 3rd party damage reported,
927 | Powercor 18/194 | Powercor | 2019-10-03 | 06:42 | -36.04282041 | 141.03192921 | TAYLORS ROAD, TELOPEA DOWNS VIC 3420 | 32121232 | NHL031 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0004662 | 20190312PWA_04 | Crew reported a fire at the incident location. Following a patrol the crew found that a pole fire had occurred on a 12.7kV pole, resulting in a ground fire (approx. 50 sqm) on private property. There were no reported injuries.
928 | Powercor 18/195 | Powercor | 15/03/2019 | 20:18 | -38.1809 | 144.348 | 97 FRANCIS STREET, BELMONT VIC 3216 | 30268132 | GLE012 | 22kV AC | Urban | - pole (wood) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0006829 | 20190528PWA_01 | Report received of possum flashover which in turn ignited pole top There was no ground fire, no reported injuries or third party property damage.
929 | Powercor 18/196 | Powercor | 16/03/2019 | 12:35 | -37.80992593 | 142.10834742 | 647 Yatchaw Road, Yatchaw | 30092292 | HTN003 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0004715 | 20190318PWA_01 | Bird flashed over on Yatchaw Rd P27E S/Stn, it came to ground and resulted in a ground fire in the road reserve of approximately 20 M X 100 M.
930 | Powercor 18/197 | Powercor | 16/03/2019 | 12:27 | -36.3879 | 145.4267 | 130-160 Benalla Rd, Shepparton VIC 3630 | 31033732 | STN021 | 22kV AC | Rural Short | - dropper / bridge | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0004716 | 20190702PWA_05 | Customer from "good guys warehouse" reported transformer fire at the incident location. Upon arrival crew found that a frond from an adjacent palm tree was making contact with the HV transformer dropper of "Zurcas 2E" substation, this caused the frond to burn due to the contact with the HV. 1 HV fuse operated at Zurcas 2E. No ground fire, injury or 3rd party damage transpired .
931 | Powercor 18/198 | Powercor | 18/03/2019 | 03:37 | -37.87958395 | 144.77411021 | Corner of Hastie court and May Avenue. Altona Meadows 3028 | 33076190 | LV003 | Low voltage AC (<1kV) | Rural Short | - overhead conductor (ABC) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0004732 | 20190320PWA_02 | Vic fire reported a pole fire at the incident location. On arrival the crew found that a connection on to LV ABC conductors had burnt at the pole . Small pieces of debris had landed on the ground below. There were no reported injuries or third party damage.
932 | Powercor 18/199 | Powercor | 19/03/2019 | 00:00 | -36.35209121 | 144.65627828 | 310 Diggora Road, Rochester | 33081172 | SHP012 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0006126 | 20190322PWA_01 | A customer reported that when they turned off their irrigation pump on Tuesday (19th March) the power pole started sparking and arcing, made a loud bang, and started a small grassfire. This was not reported to Powercor until Thursday (21st March). On arrival the crew found a porcelain fuse box on the substation pole had overheated and dropped hot debris to the ground resulting in a small grassfire of approx. 10m x 16m= 160m2 in size. There were no reported injuries or third party damage.
933 | Powercor 18/200 | Powercor | 20/03/2019 | 00:25 | -38.15373389 | 144.36613587 | 200 Myres Street, Geelong (Cnr block, pole in Swanston Street) | 17171688 | GCY024 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0004731 | 20190320PWA_01 | Following a report of a pole fire on arrival the crew found the top crossarm burnt off on outer phase. There was no ground fire, no reported injuries or third party property damage.
934 | Powercor 18/201 | Powercor | 23/03/2019 | 07:46 | -36.40213700 | 145.13202000 | 525 BYRNESIDE-KYABRAM ROAD, MERRIGUM VIC 3618 | 33094346 | SHP014 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0006177 | 20190327PWA_01 | A powercor crew responding to an outage identified that High voltage fuses had mal-operated and there had been a small ground fire at the base of the pole.
935 | Powercor 18/202 | Powercor | 23/03/2019 | 08:56 | -38.34637469 | 144.29754630 | 33 DUNKEITH AVENUE,JAN JUC,VIC,3228 | 30070945 | WPD032 | 22kV AC | Rural Short | - fuse (Fault Tamer) | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0006214 | 20190329PWA_02 | Customers reported intermittent supply. Attending crew found that fault tamer fuse had burnt in half, with the top section of the fuse carrier falling to the ground.
936 | Powercor 18/203 | Powercor | 23/03/2019 | 10:17 | -36.7172 | 144.3496 | GOLF COURSE ROAD, WELLSFORD VIC 3551 | 30026717 | EHK022 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very high | 1 | 4.6 | INC-0006458 | 20190416PWA_07 | Report received of a pole fire at incident location. On arrival crew found a crossarm with the end burnt off . There was no ground fire, no reported injuries or third party property damage.
937 | Powercor 18/204 | Powercor | 24/03/2019 | 11:44 | -38.28259846 | 144.61484358 | 135-137 POINT LONSDALE ROAD, POINT LONSDALE VIC 3225 | 31012844 | DDL012 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0006158 | 20190325PWA_02 | Passerby reports burnt cross- arm on pole 11924. Attending crew found end had burnt off from lower HV cross-arm on pole. No HVI identified
938 | Powercor 18/205 | Powercor | 24/03/2019 | 11:20 | -37.90806370 | 144.66147987 | Burke St. Werribee, along the side of No 31 Wedge St | 33071159 | WBE024 | 22kV AC | Urban | - transformer (pole mounted) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0006170 | 20190326PWA_02 | customers reported smoke coming from a power pole (LIS 204796) on the north side of Burke St Werribee A Powercor crew attended the site and noted that a 300kVA pole mounted substation (Burke Wedge 22 03 1751) had faulted
939 | Powercor 18/206 | Powercor | 24/03/2019 | 22:27 | -38.46571580 | 144.08123563 | 3 WERONA ROAD FAIRHAVEN 3231 | 30060390 | WPD014 | Low voltage AC (<1kV) | Rural Short | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0006221 | 20190329PWA_03 | Customer reported transformer on fire. Attending crew found Fuse switch disconnector had overheated
940 | Powercor 18/207 | Powercor | 24/03/2019 | 10:19 | -34.3113 | 142.1659 | CNR BOOBOOK AVE AND WESTCLIFFS AVE - redcliffs | 32146224 | RCT023 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0006247 | 20190401PWA_01 | Report received of a pole fire at the incident location. On arrival crew found that the top of the pole and crossarm had been burnt. There was no ground fire, no reported injuries or third party property damage.
941 | Powercor 18/208 | Powercor | 24/03/2019 | 02:48 | -34.2396 | 142.1755 | 2172 FIFTEENTH STREET IRYMPLE 3498 | 31021116 | RCT021 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0006823 | 20190527PWA_02 | Vic fire reported pole fire at incident location
942 | Powercor 18/209 | Powercor | 24/03/2019 | 10:14 | -34.972 | 143.2939 | 5235 MURRAY VALLEY HIGHWAY NATYA 3597 | 33067603 | BBD014 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0006358 | 20190408PWA_09 | Customer reported pole fire at incident location. On arrival crew found top of pole had been burnt off at king bolt location There was no ground fire, no reported injuries or third party property damage.
943 | Powercor 18/210 | Powercor | 28/03/2019 | 20:54 | -36.7321 | 141.1823 | 367 Mimimay Frances Road, Minimay | 33054660 | HSM004 | 12.7kV AC (SWER) | Rural Long | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any other thing forming part of or coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0006248 | 20190329PWA_05 | A B Double tip truck, while unloading gypsum fertilizer on a farming property, made contact with overhead SWER conductor; bringing the conductor to the ground. The truck was driving forward with the tipper up, and the driver did not check for clearance from the overhead SWER conductor. The electrical discharge through the truck ignited a grass fire on this property - burning an area approx. 50m x 10m There were no injuries to the truck driver or any other damage caused by this incident.
944 | Powercor 18/211 | Powercor | 29/03/2019 | 11:34 | -35.955 | 145.61 | 6515 Benalla-Tocumwal Road (C371) YARROWEYAH VIC 3644 (Near corner Churchill Road & Lonergan Road) | 30326765 | CME015 | 22kV AC | Rural Short | - fuse (EDO fuse) | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | INC-0006250 | 20190329PWA_04 | Customer reported lightning has struck power pole out the front of property. Crew found lightning had damaged an EDO fuse unit and started a 100m x 20m grass fire, no reported injuries or property damage.
945 | Powercor 18/212 | Powercor | 29/03/2019 | 14:17 | -37.5705 | 143.7427 | 98 Sago Hill Road Bunkers Hill 3352 (Near Greenhalghs Road) | 30282752 | BAS011 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very high | 1 | 4.6 | INC-0006253 | 20190402PWA_01 | Vicfire reported wire down and a grass fire at the incident location. Crew found a tree had fallen and damaged a bare overhead conductor.
946 | Powercor 18/213 | Powercor | 29/03/2019 | 18:33 | -38.1149 | 144.3543 | Cnr Mackey St & Princes Hwy, Geelong. | 31012241 | GB031 | 22kV AC | Urban | - overhead conductor (bare; steel) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0006254 | 20190402PWA_02 | Vicfire called to report a pole hit by lightning, conductors down and a grass fire at the incident location. On arrival the crew found that a cross-arm fire had occurred on the 66kV cross arm, causing the 66kV conductors to fall on the 22kV conductors, which subsequently resulted in one phase of the 22kV falling to the ground. The 22kV conductor that fell, landed across the Princes Highway blocking the road, and also fell across the Geelong-Melbourne Railway causing the trains to be stopped. A small ground fire was ignited at the base of the pole.
947 | Powercor 18/214 | Powercor | 29/03/2019 | 21:29 | -37.8561 | 144.808 | 20-24 AJAX ROAD, ALTONA VIC 3018 | 30108857 | AL011 | 11kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0006256 | 20190402PWA_03 | Vic fire reported a pole fire at incident location. On arrival the crew found a crossarm burnt on one end. There was no ground fire, no reported injuries or third party property damage.
948 | Powercor 18/215 | Powercor | 30/03/2019 | 18:24 | -36.2547 | 144.9987 | Allot 79A Finlay Rd Tongala | 33091308 | KYM004 | 22kV AC | Rural Long | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0006258 | 20190402PWA_05 | A PAL crew returning from another fault found CFA in attendance at a small grass fire at the incident location. On arrival crew found a HV isolator appears to have flashed. There were no reported injuries or third party property damage.
949 | Powercor 18/216 | Powercor | 31/03/2019 | 13:36 | -35.3126 | 141.3017 | 174 GUNAMALARY ROAD, COWANGIE VIC 3506 | 32151897 | OYN001 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0006259 | 20190402PWA_06 | CFA reported pole fire on Gunamalary Rd. On arrival crew found that a HV cross arm had burnt through at the kingbolt. The centre phase insulator was on the ground. A Ground fire had occurred, there were no reported injuries or third party damage.
950 | Powercor 18/217 | Powercor | 31/03/2019 | 08:15 | -35.0702 | 143.3354 | 28 HANKINSON LANE PIANGIL 3597 | 32162865 | SHL002 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0006825 | 20190527PWA_03 | Report of pole fire at incident location
951 | Powercor 18/218 | Powercor | 31/03/2019 | 15:06 | -34.7185 | 143.1496 | TOWER 13 MURRAY VALLEY HIGHWAY BOUNDARY BEND VIC 3599 | 32143607 | BBD021 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0006826 | 20190527PWA_04 | Pole fire found at incident location
952 | Powercor 18/219 | Powercor | 31/03/2019 | 11:39 | -35.1398 | 142.0249 | 21 Glen St Walpeup | 30097832 | OYN001 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0006355 | 20190408PWA_08 | Reports of pole fire, crew arrived and CFA and police in attendance. HV cross-arm had burnt out and HV conductors were on LV cross arm. Crew checked and HV conductors have not made contact with LV conductors and no reports of HV injection. No ground fire. No injuries. No third party damage.
953 | Powercor 18/220 | Powercor | 2019-03-04 | 13:10 | -35.2547 | 141.1078 | MALLEE HIGHWAY CARINA 3512 | 32153602 | OYN001 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0007291 | 20190701PWA_04 | Following report from customer a pole fire was found at the incident location. On arrival crew found end burnt of crossarm and conductor hanging low across paddock. There was no ground fire, no reported injuries or third party property damage.
954 | Powercor 18/221 | Powercor | 2019-05-04 | 19:39 | -35.2868 | 141.0811 | 1047 NGALLO ROAD,CARINA,VIC,3512 | 31021367 | OYN001 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very high | 1 | 1 | INC-0006349 | 20190408PWA_06 | Customer reported wire down in the paddock, wire is only 8 foot off the ground at 1047 Ngallo Road, wire is resting on top of a poly tank and goes over the gateway. Crew found Carina P26 Burnt and broken cross arm There was no ground fire, no property damage and no injuries.
955 | Powercor 18/222 | Powercor | 2019-05-04 | 14:15 | -38.2876 | 141.5173 | 359 Foleys Rd, Gorae West. | 32128662 | PLD003 | 12.7kV AC (SWER) | Rural Long | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | Very high | 1 | 1 | INC-0006346 | 20190408PWA_03 | Vicfire advised of grass fire caused by a large plantation gum tree falling across conductors. On arrival crew found that a large gum tree had fallen across SWER conductors causing a grass fire There was no reported injuries
956 | Powercor 18/223 | Powercor | 2019-07-04 | 12:27 | -35.9238 | 144.2065 | Peaces Road corner Mansfield Bridge Road Leitchville | 31038390 | CHA005 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0006344 | 20190408PWA_02 | Report of pole fire and ground fire at incident location. Crew found a pole fire had started a 1 acre grass fire, no property damage, no injuries.
957 | Powercor 18/224 | Powercor | 2019-08-04 | 14:22 | -37.3913 | 144.0575 | 475 Telegraph Road Mount Prospect 3364 | 31001430 | BAN008 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0006365 | 20190409PWA_02 | Vicfire reported lines down, grass fire caused by lines down, wires sparking at incident location. Crew found a broken xarm and a broken conductor There was a ground fire of 2 x 30m2,, no injuries, no property damage.
958 | Powercor 18/225 | Powercor | 2019-08-04 | 20:35 | -38.1616 | 144.3445 | 406 Pakington St, NEWTOWN (sth of Rutland St) | 32087669 | GL022 | 22kV AC | Urban | - pole (wood) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0006367 | 20190409PWA_04 | Powercor received a report from Vic FIre of an explosion and pole on fire in Pakington St. When crews arrived they found a possum had shorted across the HV switch. This resulted in some grass igniting on the pole which had grown up the pole along the earth cable and behind the possum guard approx. 1.5m above ground level. This was also the location of the end of the HV switch handle and it appears that an arc had occurred been the switch handle and possum guard. There was no ground fire, no reported injuries or third party property damage.
959 | Powercor 18/226 | Powercor | 2019-09-04 | 03:02 | -35.7683 | 142.0542 | 22 Byrne Street,, Yapeet | 32123038 | NHL015 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0006364 | 20190409PWA_01 | Powercor received a report from the CFA of a Pole Fire at 222 Byrne Street Yapeet. A Powercor crew attended at determined that a Pole Fire had occurred on Jeparit Pole 627. The X-arm had burnt through at the X-arm strap bolt and one of the HV conductor had come to rest on a LV conductor on the x-arm below. There was no ground fire or reported injuries.
960 | Powercor 18/227 | Powercor | 2019-09-04 | 01:13 | -36.6027 | 143.9429 | 27 Main Street Bridgewater | 30028650 | BET001 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0006366 | 20190409PWA_03 | Vic Fire reported pole on fire, sparks everywhere. Crew found pole fire/burnt HV strain xarm, no ground fire, no property damage, no injuri
961 | Powercor 18/228 | Powercor | 2019-09-04 | 15:04 | -35.1589 | 141.0413 | 246 Simon Road Panitya Vic 3512 (near Mickan Road) | 32146042 | OYN001 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0006370 | 20190410PWA_01 | Customer advised fuse down on pole located on Panitya North Rd. Crew found SWER pole had burnt down 2m from top, There was a small stubble fire , no reported injuries.
962 | Powercor 18/229 | Powercor | 2019-11-04 | 18:14 | -34.2055 | 142.1482 | 359 San Mateo Avenue Mildura | 33063508 | MDA034 | 22kV AC | Urban | - crossarm (steel) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0006431 | 20190412PWA_03 | A Sparking Transformer was reported by customers. Sparks reaching ground and started a grass fire. Three magpies flashed over at the top of the substation pole. CFA Attended small scorched area where magpies fell. There was no reported injuries or third party property damage.
963 | Powercor 18/230 | Powercor | 2019-11-04 | 07:50 | -36.4998 | 142.568 | 548 MINYIP-COROMBY ROAD, MINYIP VIC 3392 | 32112021 | STL006 | 12.7kV AC (SWER) | Rural Long | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0006395 | 20190411PWA_03 | CFA Brigade reported as per police, pole fire, Cnr Robbins Rd & Coromby-Minyip Rd Minyip, top of pole on fire, Brigade enroute. Due to a pole fire the crew found live SWER conductor hanging approximately 3.6m above road and railway line There was a small ground fire: 50m x 30m = 1,500m2, no property damage, no injuries.
964 | Powercor 18/231 | Powercor | 15/04/2019 | 15:59 | -36.3752 | 145.3992 | outside 29 Welsford Street Shepparton | 30259528 | SHN023 | Low voltage AC (<1kV) | Urban | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0006638 | 20190506PWA_03 | Powercor crew responding to a fault found a LV Fused Gang Operated Fused dis-connector switch [FSD] had burnt out
965 | Powercor 18/232 | Powercor | 15/04/2019 | 11:40 | -37.5552 | 143.8973 | 32 Water St, Brown Hill | 30283126 | BAN015 | Low voltage AC (<1kV) | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0006444 | 20190416PWA_01 | A crew investigating an outage found that an unknown vehicle had contacted a communications cable above Water St, The force of the impact caused the communications cable to contact the overhead LV conductors. This resulted in hot debris falling to the ground, starting a small grass fire. There was no reported injuries or third party property damage.
966 | Powercor 18/233 | Powercor | 16/04/2019 | 09:32 | -38.1456 | 143.6297 | 1992 Colac Ballarat Road, Beeac | 30052273 | CLC003 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very high | 1 | 4.6 | INC-0006478 | 20190418PWA_02 | A customer called concerned about a tree branch that had fallen onto the High Voltage conductors and started a fire. On arrival the crew found that a tree branch had fallen and contacted the HV conductors and then onto the ground. This caused a ground fire of approx. 750m2. The CFA did not notify Powercor of the fire at the time of their attendance. There were no reported injuries.
967 | Powercor 18/234 | Powercor | 21/04/2019 | 05:34 | -38.6004 | 143.0012 | 2520 Cobden-Port Campbell Rd, Port Campbell 3269 | 32056227 | TRG003 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0006649 | 20190507PWA_02 | CFA reported pole fire at incident location. On arrival crew found bird nest material in FOLCB had caught fire and melted the box and conductor insulation. Melted plastic fell to the ground but did not start a fire.
968 | Powercor 18/235 | Powercor | 21/04/2019 | 18:31 | -36.4669 | 145.2778 | 690 Craven Rd, Tatura VIC 3616 | 30133198 | MNA034 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0006650 | 20190507PWA_03 | Vic Fire report a pole fire at the incident location. Upon arrival the fault crew found that a 3 phase intermediate pole had ignited.
969 | Powercor 18/236 | Powercor | 21/04/2019 | 12:39 | -35.2325 | 141.0208 | OUYEN HIGHWAY CARINA VIC 3512 | 31021260 | OYN001 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0007294 | 20190701PWA_05 | Customer reported low conductors and pole fire. On arrival crew found crossarm burnt in half. There was no ground fire, no reported injuries or third party property damage.
970 | Powercor 18/237 | Powercor | 23/04/2019 | 14:37 | -34.1678 | 142.0658 | 149 Commercial Street, Merbein VIC 3505 | 32151664 | MBN031 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0006652 | 20190507PWA_05 | Vic Fire reported a pole fire at the incident location. Upon arrival crew found that an intermediate crossarm had burnt through at the kingbolt, dropping down onto the LV cross arm below
971 | Powercor 18/238 | Powercor | 23/04/2019 | 15:34 | -34.2358 | 142.1713 | 2135 Fifteenth St Irymple | 30099579 | MDA023 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0006653 | 20190507PWA_06 | A pole fire reported at the incident location. The attending crew found the HV strain cross-arm had burnt
972 | Powercor 18/239 | Powercor | 23/04/2019 | 14:29 | -34.251 | 142.0831 | 3420 Deakin Av Mildura | 30098768 | MBN032 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | INC-0006654 | 20190507PWA_07 | Vic Fire reported a pole fire at the incident location, attending crew found HV cross-ram had burnt
973 | Powercor 18/240 | Powercor | 23/04/2019 | 12:13 | -34.2319 | 142.1848 | 685 Irymple Av Irymple | 30558650 | RCT011 | 22kV AC | Rural Short | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0006648 | 20190507PWA_01 | Vic Fire reported a pole fire at the incident location. Upon arrival, the crew found that the pole top burnt through and fell onto LV
974 | Powercor 18/241 | Powercor | 23/04/2019 | 12:08 | -34.1927 | 142.1498 | 16 Princess St Mildura | 32149824 | MDA033 | 22kV AC | Urban | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0006525 | 20190424PWA_01 | A pole fire reported at the incident location. Upon arrival, that the crew found HV cross arm burnt through. There were no injuries or ground fire. HVI damage was reported.
975 | Powercor 18/242 | Powercor | 23/04/2019 | 14:28 | -34.2113 | 142.1806 | 396-402 SANDILONG AVENUE IRYMPLE 3498 | 30100024 | MDA024 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0006526 | 20190424PWA_02 | pole fire reported at the incident location. Upon arrival, that the crew found HV cross arm bunt through. There were no injuries or ground fire. HVI reported.
976 | Powercor 18/243 | Powercor | 23/04/2019 | 22:40 | -34.2417 | 142.1035 | 3219 SAN MATEO AVENUE MILDURA 3500 | 32146495 | MBN032 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0006527 | 20190424PWA_03 | A pole fire reported at the incident location. HVI was found . There were no injuries or ground fire.
977 | Powercor 18/244 | Powercor | 23/04/2019 | 11:39 | -34.4274 | 142.3492 | BLAKE ROAD, IRAAK VIC 3494 | 30098951 | RCT014 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0007296 | 20190701PWA_06 | Customer reports pole fire at incident location. On arrival crew found termination crossarm burnt There was no ground fire, no reported injuries or third party property damage.
978 | Powercor 18/245 | Powercor | 24/04/2019 | 16:45 | -34.2716 | 142.162 | 264 Coorong Ave, Irymple VIC 3498 | 32148573 | RCT021 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0006661 | 20190508PWA_01 | Customer reported wire down at the incident location. Upon arrival crew found that a Tee Off cross-arm burnt off at eye bolt position. Supply remained on as the conductor remained aloft suspended by the bridging cable.
979 | Powercor 18/246 | Powercor | 24/04/2019 | 13:58 | -34.464 | 142.3414 | 73 Sculthorpe Road, Nangiloc VIC 3494 | 32144798 | RCT013 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0006655 | 20190507PWA_08 | Customer reported broken cross arm at incident location. Upon arrival crew found that a intermediate cross arm burnt through at the kingbolt, the cross arm straps kept the conductors aloft.
980 | Powercor 18/247 | Powercor | 26/04/2019 | 09:02 | -37.0594 | 144.2086 | 29 RICHARDS ROAD, CASTLEMAINE VIC 3450 | 32045602 | BETS-CMN | 66kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0006663 | 20190508PWA_02 | Vic Fire reported a pole fire at the incident location. Upon arrival, the fault crew found 66kV cross arm ignited.
981 | Powercor 18/248 | Powercor | 26/04/2019 | 10:18 | -38.067 | 144.359 | 214 Baccush Marsh Service Rd Corio | 32073948 | FNS011 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0006664 | 20190508PWA_03 | Vic Fire reported a pole fire at the service road of this incident location. The attended crew made the site safe and repairs arranged
982 | Powercor 18/249 | Powercor | 26/04/2019 | 15:58 | -36.2574 | 145.351 | CNR MEDLAND RD AND ALDINGA DVE - BUNBARTHA | 33097110 | SHN011 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0006551 | 20190429PWA_03 | Customer advised that tree fell across bare overhead mains and reported smoking from wire/tree. Attending crew found A tree had fallen directly across all three phases and tree had caught fire. There were small fires where the conductors had been brought to ground.
983 | Powercor 18/250 | Powercor | 26/04/2019 | 13:37 | -36.2675 | 144.2321 | BENDIGO-PYRAMID ROAD, MITIAMO VIC 3573 | 31005276 | CHA006 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0006548 | 20190429PWA_01 | Vic Fire reported a pole fire at the incident location. A fault crew found that the cross arm burnt through and fallen debris caused a ground fire approx. 7*100 Sqm area.
984 | Powercor 18/251 | Powercor | 26/04/2019 | 00:45 | -38.3859 | 142.4916 | 74 Barkly st Warrnambool, vic 3280 | 30544142 | WBL008 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0007299 | 20190701PWA_08 | Call from customer reporting pole fire outside 74 barkly st. No ground fire, no injuries or third party property damage.
985 | Powercor 18/252 | Powercor | 26/04/2019 | 16:18 | -34.2258 | 142.0934 | 3171 ONTARIO AVENUE MILDURA 3500 | 30099184 | MBN032 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0007314 | 20190702PWA_04 | Report received of a pole fire at incident location. There was no ground fire, no reported injuries or third party property damage.
986 | Powercor 18/253 | Powercor | 2019-01-05 | 06:01 | -34.4477 | 142.3355 | 2351 KULKYNE WAY, IRAAK VIC 3494 | 30096877 | RCT013 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very high | 1 | 1 | INC-0006913 | 20190514PWA_03 | Vic fire reported a pole fire. The attending crew found that a cross arm had burnt at the king bolt position.
987 | Powercor 18/254 | Powercor | 2019-01-05 | 04:30 | -35.241 | 143.4719 | Cnr ray and heslop rd (outsie 68 heslop rd - beverford). | 32161041 | SHL004 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0006914 | 20190603PWA_02 | Customer reported a pole fire at the incident location. On arrival crew reported end burnt of wooden crossarm. There was no ground fire, no reported injuries or third party property damage.
988 | Powercor 18/255 | Powercor | 2019-01-05 | 05:47 | -35.725 | 142.3616 | 39 TOOLE STREET, HOPETOUN VIC 3396 | 32098179 | HSM003 | Low voltage AC (<1kV) | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0006665 | 20190508PWA_04 | Vic Fire reported a pole fire at the incident location. On arrival the fault crew found that an LV crossarm had burned through on a HV / LV 2 way tee off pole. The Powercor pole was also burned at the kingbolt location.
989 | Powercor 18/256 | Powercor | 2019-01-05 | 06:17 | -35.3287 | 143.5566 | 9 KING STREET, SWAN HILL VIC 3585 | 32161090 | SHL004 | 22kV AC | Rural Short | - overhead conductor (insulated) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0006610 | 20190503PWA_01 | Powercor received an alarm indicating that a high voltage automatic circuit recloser had opened. The attending crew found that a pole top fire had occurred which destroyed the top of a pole and dislodged overhead conductors. The crew indicated that the fire may have ignited in the vicinity of the low voltage cross-arm supporting isolators and an LV underground cable. No ground fire.
990 | Powercor 18/257 | Powercor | 2019-01-05 | 09:10 | -36.1406 | 144.7598 | 121 OGILVIE AVENUE ECHUCA 3564 | 30121458 | ECA001 | 22kV AC | Rural Short | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0006572 | 20190501PWA_05 | Emergency services report pole fire O/S 121 OGILVIE AVENUE ECHUCA Powercor crew attended site to find the lowest high voltage cross-arm had burnt thru on the king bolt, conductors fell onto low voltage circuit below
991 | Powercor 18/258 | Powercor | 2019-01-05 | 10:55 | -37.9286 | 141.847 | 597 WALLACEDALE-BYADUK ROAD WALLACEDALE 3303 | 30087598 | HTN002 | 12.7kV AC (SWER) | Rural Long | - earth / earthing | single wire earth return (SWER) | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0006574 | 20190501PWA_06 | customer reports earth is burning where it meets the pole. Crew attended site to find SWER earth getting very hot near base of pole. Appears to have ignited a small grass fire about 0.5m2.
992 | Powercor 18/259 | Powercor | 2019-01-05 | 12:30 | -36.2547 | 145.0319 | 617 MCEWEN ROAD WYUNA 3620 southwest of property. | 31027332 | KYM004 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0006593 | 20190502PWA_01 | Customer reported loud bang and power went out. Crew attended site to find broken HV cross-arm on Harris P5, with a flash over and pole fire on Tongala East -P79
993 | Powercor 18/260 | Powercor | 2019-01-05 | 06:54 | -35.9203 | 144.2188 | 130 PEACES ROAD LEITCHVILLE VIC 3567 | 32033752 | CHA005 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0007209 | 20190627PWA_03 | Report of pole fire at incident location. There was no ground fire, no reported injuries or third party property damage.
994 | Powercor 18/261 | Powercor | 2019-02-05 | 00:07 | -34.3024 | 142.1424 | 436 myall street,cardross,vic,3496 | 30095563 | MDA023 | 22kV AC | Rural Short | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0006915 | 20190603PWA_03 | Vic fire reported a pole fire at the incident location. On arrival the crew found that a pole fire had occurred resulting in the pole being burnt between the HV and LV crossarms. There was no ground fire, no reported injuries or third party property damage.
995 | Powercor 18/262 | Powercor | 2019-02-05 | 06:29 | -34.2846 | 141.6612 | HARDS LANE - WERRIMULL VIC 3496 | 30283808 | MBN031 | 12.7kV AC (SWER) | Rural Short | - pole (wood) | single wire earth return (SWER) | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0006688 | 20190510PWA_07 | Vicfire reported a pole fire in Hards lane, the attending crew found the top of the pole had burnt and signs of burning on the ground.
996 | Powercor 18/263 | Powercor | 2019-07-05 | 18:46 | -35.3373 | 141.108 | 901 CARINA SOUTH ROAD, CARINA VIC 3512 | 32154757 | OYN001 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very high | 1 | 1 | INC-0006683 | 20190510PWA_05 | Customer reported pole fire in paddock. On arrival crew found pole was burning on the inside and on the tee-off cross arm
997 | Powercor 18/264 | Powercor | 13/05/2019 | 08:40 | -38.1706 | 144.3423 | BELMONT PRIMARY SCHOOL, 51 MT PLEASANT ROAD, BELMONT VIC 3216 | 31010963 | GCY023 | Low voltage AC (<1kV) | Urban | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0006707 | 20190514PWA_06 | Belmont Primary School advises top of pole is on fire, pole is located directly at front of the school and at school crossing. Powercor crew arrived to find a fuse switch disconnect (FSD) device had overheated and caught fire. The Fire brigade had extinguished the fire prior to the crew attending.
998 | Powercor 18/265 | Powercor | 13/05/2019 | 12:31 | -35.5008 | 142.7171 | MYALL ROAD LASCELLES 3487 | 32159145 | OYN005 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0006706 | 20190514PWA_05 | Customer reported pole in paddock has burnt to the ground in past 24 hours, not currently on fire, paddock is on Mitchell road between where it meets Myall School Bus Road and Sea Lake-Lascelles Road. Crew found SWER pole had been burnt due to pole fire, minor ground fire damage around where pole was.
999 | Powercor 18/266 | Powercor | 18/05/2019 | 17:30 | -35.82 | 144.1938 | 119 COHUNA-MCMILLANS ROAD, COHUNA VIC 3568 | 33019552 | CHA006 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0006771 | 20190521PWA_01 | Emergency services reported wire down and ground fire at the incident location. Upon arrival fault crew found that road side 22kV conductor failed approximately 20M from pole 41 Greens Rd. The downed conductor caused localised burning of grass in the immediate vicinity of where it came to rest, approximately 2.0M in burnt area comprised of small patches.
1000 | Powercor 18/267 | Powercor | 19/05/2019 | 18:17 | -36.2764 | 145.4113 | 185 Zeerust Rd, Zeerust VIC 3634 | 33093329 | SHN011 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0006950 | 20190605PWA_05 | CFA reported transformer fire at the incident location. Upon arrival crew found that a LV fuse box had melted and candled due to excessive hea. No ground fire resulted or any other 3 party damage.
1001 | Powercor 18/268 | Powercor | 21/05/2019 | 19:01 | -37.3521 | 144.1423 | 5 Macadam St, Daylesford | 31001630 | BAN011 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0006885 | 20190531PWA_02 | CFA reported reported a fire on a pole at the incident location. On arrival, the crew found that a connection in a pole mounted LV fuse box had overheated, causing the box to melt and catch fire. There was no ground fire. There were no reported injuries or third party property damages.
1002 | Powercor 18/269 | Powercor | 27/05/2019 | 21:52 | -37.7086 | 144.7881 | 1A BOBBORA COURT TAYLORS LAKES 3038 | 17978879 | SA003 | Low voltage AC (<1kV) | Urban | - transformer (kiosk mounted) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0006832 | 20190528PWA_04 | Customers and Fire Brigade reported BOBBORA-ADMIRALS 300kVA Kiosk on fire. LV switchboard end of the kiosk was burnt out internally. Fire brigade extinguished the fire. There was no ground fire, no reported injuries or third party property damage.
1003 | Powercor 18/270 | Powercor | 27/05/2019 | 22:57 | -38.3865 | 142.4928 | 58 BARKLY STREET WARRNAMBOOL 3280 | 32194380 | WBL008 | 22kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0006830 | 20190528PWA_02 | CFA Comms reported pole fire. Attending crew found pole top had burnt above HV strain cross arm and would require replacement in daylight. no customers impacted
1004 | Powercor 18/271 | Powercor | 27/05/2019 | 21:49 | -37.3557 | 144.7218 | 278 KNOX ROAD ROMSEY 3434 | 31006494 | WND012 | 22kV AC | Rural Long | - transformer (pole mounted) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0007230 | 20190628PWA_01 | Transformer failed and caught fire CFA attended There was no ground fire, no reported injuries or third party property damage.
1005 | Powercor 18/272 | Powercor | 29/05/2019 | 09:00 | -38.4884 | 142.7011 | 784 CHILDERS COVE ROAD THE COVE 3268 | 33105330 | WBL012 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0006890 | 20190531PWA_03 | Vic Fire reports a pole fire at 784 Childers Cove Rd The Cove. Crew attended to find that EDO fuse on 22kV substation had mal-operated.
1006 | Powercor 18/273 | Powercor | 30/05/2019 | 03:34 | -38.1247 | 144.6645 | 122 SIMSON STREET,PORTARLINGTON,VIC,3223 | 32070815 | DDL013 | Low voltage AC (<1kV) | Rural Short | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0006992 | 20190606PWA_08 | Vicfire reported a pole fire. Attending crew found that a LV switch disconnector had failed There was no ground fire , no reported injuries or third party property damage.
1007 | Powercor 18/274 | Powercor | 31/05/2019 | 08:49 | -36.3226 | 145.1639 | Ground water Pump site, Davies Rd, Lancaster | 30222670 | KYM003 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0006997 | 20190606PWA_10 | Following a report of the HV fuse down at the incident location, crews attended and found that lightning had struck the HV OH conductors mid-span. Insulation was burnt from a section of LV transformer leads adjacent to the FOLCB . A birds nest inside the FOLCB was scorched - refer image There was no ground fire, no reported injuries.
1008 | Powercor 18/275 | Powercor | 31/05/2019 | 06:53 | -36.4151 | 141.6602 | Winiam Rd, near the corner of D Manns Rd, Nhill 3418 | 32122897 | NHL015 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0007009 | 20190607PWA_01 | Vic fire reported a pole fire at the incident location. On arrival the crew found minor burning of the wooden pole top. The conductor stayed in position until crews arrived to perform repairs. There were no reported injuries, and no ground fire.
1009 | Powercor 18/276 | Powercor | 2019-03-06 | 18:41 | -37.84 | 144.8439 | 22 Cooper Avenue, Altona North | 32164659 | AL002 | Low voltage AC (<1kV) | Urban | - transformer (pole mounted) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0007019 | 20190607PWA_04 | MFB reported a transformer was on fire. Upon arrival the fault crew found a melted red phase LV bushing a 300kVA pole sub. The fire self extinguished according to the MFB. The fire was contained to the area immediately surrounding the LV bushing and transformer tank on the pole itself. There was no ground fire to report. No reports of shock, injury or third party damage.
1010 | Powercor 18/277 | Powercor | 2019-04-06 | 11:20 | -37.827 | 144.7713 | 255 Dohertys Rd Laverton North | 30114188 | LVN021 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0007021 | 20190607PWA_05 | Vic Fire reported a transformer on fire at the incident location. Upon arrival a Powercor crew found that a service termination box on a Pole Substation had melted. There was no ground fire, no reported injuries or third party property damage.
1011 | Powercor 18/278 | Powercor | 2019-05-06 | 04:50 | -36.661 | 142.1168 | Bedderson rd Vectis, | 32090809 | HSM006 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | INC-0006967 | 20190606PWA_01 | Customer reported loss of supply and wire down near their place, on arrival the work crew found a pole fire had occurred resulting in the top of the pole burning off and the conductors fell to the ground. There was a small ground fire 1m sq. There was no reported injuries.
1012 | Powercor 18/279 | Powercor | 2019-06-06 | 10:32 | -38.4111 | 144.1849 | 14 Minifie Avenue, Anglesea | 33043992 | WPD021 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0007029 | 20190607PWA_07 | Emergency Services reported a pole fire and a grass fire at the incident location. On arrival the crew found that a 3 phase FOLCB had overheated and dropped hot debris to the ground, resulting in a small ground fire of less than 1 metre square at the base of the pole. There were no reported injuries.
1013 | Powercor 18/280 | Powercor | 2019-08-06 | 19:15 | -38.271 | 144.5192 | 45 Osborne Street, Ocean Grove | 30233688 | DDL023 | Low voltage AC (<1kV) | Rural Short | - overhead service conductor (other) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0007044 | 20190611PWA_01 | Crew were dispatched to incident following reports transformer and pole were on fire. The fire brigade were also enroute. Upon arrival, the crew identified a 2 wire neutral screened service to 45 Osborne St had burnt at the pole junction box. The wire fell to the ground causing 1m2 of grass to burn. There was no reported injuries.
1014 | Powercor 18/281 | Powercor | 2019-08-06 | 17:43 | -37.7207 | 144.8383 | 662 OLD CALDER HIGHWAY,KEILOR,VIC,3036 | 33073634 | SA002 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0007073 | 20190612PWA_02 | MFB and a customer reported conductors and a transformer on fire. Pole located outside a row of townhouses near intersection of Flora street and Calder Highway. They advised it was a small fire and still currently on supply. CFA have been called. On arrival the Powercor crew found that the connections in a krone box had overheated and the box melted. The small fire extinguished by itself. There was no ground fire, no reported injuries or third party property damage.
1015 | Powercor 18/282 | Powercor | 16/06/2019 | 00:24 | -35.2959 | 143.454 | 25 Woorinen-Goschen Road Woorinen South, Victoria | 30259059 | SHL004 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | INC-0007112 | 20190617PWA_01 | VIC Fire reported pole fire, possible junction box, brigade en route. Crew found remains of a burnt fuse box. There was no ground fire, no pole fire just light black stain from smoke and spatter. There was no reported injuries or third party property damage.
1016 | Powercor 18/283 | Powercor | 18/06/2019 | 08:44 | -37.7682 | 144.4399 | 3573 Geelong - Bacchus Marsh Rd, Parwan Vic | 32163946 | BMH006 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | INC-0007183 | 20190624PWA_04 | An employee reported a fire on a pole at the incident location. On arrival the crew found that a cross arm fire had occurred on a 22kV pole which burnt the cross arm only. There was no ground fire. There were no reported injuries or third party property damages.
1017 | Powercor 18/284 | Powercor | 22/06/2019 | 17:03 | -38.0739 | 144.309 | 110 Evans Rd, Lovely Banks 3213 | 31011781 | CRO022 | Low voltage AC (<1kV) | Urban | - overhead service conductor (other) | single phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | INC-0007177 | 20190624PWA_01 | Vicfire & customer reported a pole fire at the incident location. When crews arrived they found a FOLCB located on the pole had caught on fire. Molten plastic and hot debris had dropped into the cable guard below resulting in a secondary fire start to the enclosed customer conduit and cable. No ground fire start found or injuries reported.
1018 | Powercor 18/285 | Powercor | 26/06/2019 | 05:36 | -37.9119 | 144.6673 | 28 Nangiloc Crescent, Werribee 3030 | 60071893 | WBE024 | Low voltage AC (<1kV) | Urban | - LV pillar | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0007204 | 20190627PWA_02 | Vic Fire reported pillar on fire, On arrival crew found LV pillar had been on fire which was extinguished by CFA. No reported injuries or third party property damage.
1019 | Powercor 18/286 | Powercor | 29/06/2019 | 00:16 | -37.6664 | 143.6739 | 180 Browns Rd Scarsdale 3351 | 30005437 | BAS021 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | INC-0007322 | 20190703PWA_01 | VicFire reported a pole fire. On arrival the fault crew found a melted FOLCB at incident location. There was no ground fire, no reported injuries or third party property damage.
1020 | Powercor 18/287 | Powercor | 26/11/2018 | 0.53819 | -37.7409 | 144.701 | 699 NEALE ROAD, DEANSIDE VIC 3336 | 31023328 | MLN021 | Low voltage AC (<1kV) | Rural Short | - overhead service conductor (other) | single phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0003718 | 20181212PWA_02 | A customer reported a cable pulled out from the pole and also the meter board at the incident location. The attended crew found that the service had been vandalised and cut off from both pole end and the meter board. There also appears to be potential sign of fire at the pole end adjacent to FOLCB. There was no injuries reported.
1021 | Powercor 18/288 | Powercor | 2019-07-06 | 0.65903 | -38.2142 | 143.5453 | 115 WARRION HILL ROAD WARRION VIC 3249 | 30054866 | CLC003 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | INC-0007481 | 20190717PWA_03 | Hung up fuse reported by customer
1022 | Powercor 18/289 | Powercor | 25/04/2019 | 0.53889 | -35.1213 | 142.0199 | 139 LOWAN TANK ROAD - WALPEUP, VIC, 3507 | 32147524 | OYN001 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0006550 | 20190429PWA_02 | Cross arm fire due to leakage current.
1023 | Powercor 18/290 | Powercor | 28/01/2019 | 0.56181 | -36.6795 | 142.3032 | 37 Field Days Road, Longerenong | 33047656 | HSM003 | Low voltage AC (<1kV) | Rural Long | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | INC-0004015 | 20190129PWA_02 | Vic Fire reported a grass fire at the incident location. On arrival the fault crew found that a crossarm on a private pole had broken allowing the open wire low voltage / service conductors to clash, dropping hot material to the ground, igniting a grass fire approx. 15 hectares in area. Failure on private line caused secondary failure at LV isols on our system and this secondary failure caused grass fire.
1024 | Powercor 18/291 | Powercor | 2019-01-02 | 0.37014 | -36.0505 | 143.1709 | 308 Denneys Rd, Wycheproof VIC 3527 | 32027183 | CTN001 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | INC-0007642 | 20190730PWA_05 | Report received of HV crossarm burnt off. There was no ground fire.
1025 | Powercor 18/292 | Powercor | 2019-01-04 | 0.40972 | -35.0266 | 142.7464 | Mallee HWY, Manangatang 3546 | 30099720 | OYN003 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | INC-0007643 | 20190730PWA_06 | Report from customer of burn crossarm and conductors hanging low.
1026 | Jamena 18/19 | Jamena | 18/08/2018 | 0.65935 | -37.7781 | 144.8604 | 31 LACY STREET BRAYBROOK | A127303 | BY15 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 168375 | 20180905JEM_01 | Small branch, from a council responsible tree, broke during high winds and failed onto 2 phasaes of HV conductor
1027 | Jamena 18/20 | Jamena | 2018-01-09 | 0.059028 | -37.85797 | 144.902069 | 10 THE STRAND WILLIAMSTOWN | A024432 | NT04 | Low voltage AC (<1kV) | Urban | - luminaires (major road) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 168981 | 20180907JEM_01 | Public lighting lantern fire
1028 | Jamena 18/21 | Jamena | 2018-05-09 | 0.045139 | -37.7503 | 145.016083 | 35 VICTORIA STREET PRESTON | A078208 | EP37 | Low voltage AC (<1kV) | Urban | - luminaires (major road) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 169116 | 20181009JEM_01 | Public lighting lantern fire
1029 | Jamena 18/22 | Jamena | 2018-11-09 | 0.6375 | -37.7963 | 144.9317 | 167 EASTWOOD STREET KENSINGTON | A030298 | WMTSFT1 | 66kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | PM10285287 | 20190819JEM_01 | Pole top fire
1030 | Jamena 18/23 | Jamena | 2018-07-11 | 0.82708 | -37.7411 | 144.9637 | 135A BELL STREET COBURG | A111280 | CS03 | Low voltage AC (<1kV) | Urban | - luminaires (major road) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | PM10286835 | 20190819JEM_02 | Public lighting lantern fire
1031 | Jamena 18/24 | Jamena | 2018-06-12 | 0.73976 | -37.7833 | 144.9278 | 2 DOVER STREET FLEMINGTON | A028095 | FT11 | 11kV AC | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 173522 | 20181206JEM_01 | Fire at pole top due to cable termintaion failure
1032 | Jamena 18/25 | Jamena | 25/12/2018 | 0.23108 | -37.7124 | 145.0228 | 144 BOLDREWOOD PARADE RESERVOIR | A034511 | TT0-011 | Low voltage AC (<1kV) | Urban | - luminaires (major road) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | PM10288106 | 20190819JEM_03 | Public lighting lantern fire
1033 | Jamena 18/26 | Jamena | 25/01/2019 | 0.71101 | -37.7795 | 144.8785 | 60 EMU ROAD MAIDSTONE | A151624 | BY14 | 22kV AC | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 175477 | 20190126JEM_01 | Small grass fire
1034 | Jamena 18/27 | Jamena | 2019-07-02 | 0.025868 | -37.7439 | 145.0356 | 207 LIBERTY PARADE, HEIDELBERG WEST | A039071 | TTSEP | 66kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | PM10289147 | 20190819JEM_04 | Pole top fire
1035 | Jamena 18/28 | Jamena | 2019-07-02 | 0.91777 | -37.5891 | 144.7428 | 108 BROOK ST SUNBURY | A005293 | KTSSBY | 66kV AC | Rural Short | - connector / termination | three phase | Started by lightning striking a distribution system or a part of a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 176116 | 20190207JEM_05 | Small grass fire due to lighting strike
1036 | Jamena 18/29 | Jamena | 2019-06-03 | 0.74091 | -37.8188 | 144.8595 | 1 HARDIE ROAD YARRAVILLE | A030064 | FW13 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 177682 | 20190403JEM_01 | Pole top fire
1037 | Jamena 18/30 | Jamena | 19/03/2019 | 0.82986 | -37.6483 | 144.9423 | 25 FODEN AVENUE CAMPBELLFIELD | A080873 | ST12 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 178234 | 20190319JEM_01 | Small grass fire due to vehicle impact
1038 | Jamena 18/31 | Jamena | 25/03/2019 | 0.62388 | -37.6582 | 144.9706 | 65 METROLINK CIRCUIT CAMPBELLFIELD | A090085 | ST13 | Low voltage AC (<1kV) | Urban | - underground service cable (commercial / industrial) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | PM10290642 | 20190325JEM_05 | Small grass fire due to vadalism (copper theft)
1039 | Jamena 18/32 | Jamena | 29/03/2019 | 0.66236 | -37.6739 | 144.8986 | 1 SHIRRA PLACE ATTWOOD | A040004 | BD07 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | PM10290870 | 20190330JEM_01 | A branch, from a Jemena responsible tree, broke during high winds and failed onto HV resulting in failed burnt through conductor and a consequent minor grass fire.
1040 | Jamena 18/33 | Jamena | 29/03/2019 | 0.89583 | -37.804 | 144.8699 | 3A INDWE ST WEST FOOTSCRAY | A052410 | TH11 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 178847 | 20190402JEM_01 | Pole top fire
1041 | Jamena 18/34 | Jamena | 2019-10-04 | 0.17647 | -37.7705 | 145.0552 | 34 YORK AVENUE IVANHOE EAST | A016819 | HB14 | Low voltage AC (<1kV) | Urban | - fuse (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 179232 | 20190410JEM_01 | Small grass fire due to LV fused switch failure
1042 | Jamena 18/35 | Jamena | 2019-10-04 | 0.54456 | -37.8354 | 144.8865 | 91-119 CRAIG STREET SPOTSWOOD | A059706 | NT16 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 179262 | 20190411JEM_01 | Pole top fire
1043 | Jamena 18/36 | Jamena | 16/04/2019 | 0.38819 | -37.595 | 144.9211 | 1 WATFORD CRESCENT CRAIGIEBURN | A026749 | ST33 | 22kV AC | Urban | - dropper / bridge | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 179498 | 20190416JEM_01 | Small grass fire due to bird strike
1044 | Jamena 18/37 | Jamena | 25/06/2019 | 0.80124 | -37.7516 | 144.9785 | 129 RENNIE STREET COBURG | A073199 | CS09 | Low voltage AC (<1kV) | Urban | - fuse (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 182256 | 20190625JEM_01 | LV fused switch burnt out
1045 | CitiPower 18/19 | CitiPower | 2018-08-07 | 18:25 | -37.81279500 | 145.09298335 | 33-35 Banool Road, Balwyn, VIC, Australia | 30176489 | WD031 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0002725 | 20180711PWA_01 | Police and MFB reported a pole fire at the above incident location. On arrival, the crew found that a Fuse Switch Disconnect (FSD) unit overheated and caught on fire. Melted pieces fell onto the grass nature strip. There was no ground fire, no reported injuries or third party property damage.
1046 | CitiPower 18/20 | CitiPower | 19/07/2018 | 08:44 | -37.81380586 | 145.02985239 | 135 Barkers Rd, Kew | 30178382 | Q010 | 11kV AC | Urban | - crossarm (wood) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0002769 | 20180720PWA_01 | Customer reports fire on pole. Crew attended and found tree branch had struck the HV insulator at P05E Barker Denmark, breaking a disc insulator. This resulted in leakage current flowing to the wood crossarm starting a crossarm fire. No shock, injuries or ground fire start.
1047 | CitiPower 18/21 | CitiPower | 16/08/2018 | 18:45 | -37.79486262 | 144.97964260 | 96 Westgarth Street, Fitzroy, 3065. | 30170306 | CW011 | Low voltage AC (<1kV) | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0002957 | 20180817PWA_01 | A Local resident advised loud explosion on black box attached to pole across the street, then small fire started on the pole. Crew attended to find a small fire burning on an overheated IPC. There was no ground fire, no reported injuries or third party property damage.
1048 | CitiPower 18/22 | CitiPower | 13/09/2018 | 08:52 | -37.8227844 | 145.0057 | 88 Fraser St, Richmond. | 30189149 | NR003 | Low voltage AC (<1kV) | Urban | - fuse (any other type) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | INC-0003146 | 20180913PWA_03 | MFB reported house fire at meter board. Powercor crew requested to attend. Crew found meter board had caught fire. There were no reported injuries.
1049 | CitiPower 18/23 | CitiPower | 2018-09-10 | 11:38 | -37.84503653 | 144.94765196 | 83 DANKS STREET,ALBERT PARK,VIC,3206 | 30172683 | AP003 | 11kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0004529 | 20190613PWA_01 | Cross-arm fire due to leakage current. Fire incident found during review of outage data for fire incidents. No ground fire
1050 | CitiPower 18/24 | CitiPower | 2018-07-11 | 16:40 | -37.8111 | 144.9676 | Cnr of 234 Russell St and Belman Pl Melbourne 3000 | 35415217 | WA035 | Low voltage AC (<1kV) | CBD | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0003483 | 20181109PWA_01 | Multiple customers reported power outages on Belman Pl. On arrival it was found that a service box on a building wall had caught fire. There was no reported injuries or third party property damage.
1051 | CitiPower 18/25 | CitiPower | 2019-01-01 | 03:35 | -37.83234023 | 145.02876878 | 10 Scotsburn Street, Hawthorn | 30202117 | CL036 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0003835 | 20190104PWA_03 | VicFire called the CitiPower Report Room to advise of a pole fire at 10 Scotsburn St, Hawthorn. On arrival the CitiPower overhead faults crew found an FOLCB and LV cable to 10 Scotburn St, Hawthorn to have heat damage causing it to fall to the ground. The crew observe charring marks on the ground of approx. 1sqm. There was no reported injuries or third party property damage.
1052 | CitiPower 18/26 | CitiPower | 24/01/2019 | 15:01 | -37.78349991 | 145.09188909 | 2 Joy St Balwyn North | 30185720 | WD011 | Low voltage AC (<1kV) | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0004010 | 20190125PWA_04 | CP received a report of supply interruption and fire at the incident location. On arrival the crew found that an IPC connector and blue phase isolator had burnt out. Debris from isolator fell to ground causing a small fire at the base of the pole. There was no reported injuries or third party property damage.
1053 | CitiPower 18/27 | CitiPower | 25/02/2019 | 17:52 | -37.86814000 | 145.01303000 | 557 Inkerman Road, Caulfield North, VIC, 3161 | 30261573 | EL011 | Low voltage AC (<1kV) | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0004447 | 20190226PWA_03 | A passer-by reported ground fire on the ground at the above incident location. On arrival, the crew found an Low Voltage (LV) overhead conductor tie had broken due to faulty Insulation Piercing Connector (IPC) overheating and melted the LV tie conductor. The melted plastic IPC fell onto the ground and caused ground fire of approximately 20sqm. There was no third party damaged and no reported injuries.
1054 | CitiPower 18/28 | CitiPower | 28/02/2019 | 15:21 | -37.83079773 | 145.09015448 | Corner of Durham Rd and Dome St Surrey Hills | 30187129 | RD006 | Low voltage AC (<1kV) | Urban | - overhead conductor (bare; copper) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0004522 | 20190301PWA_01 | Police reported that there were wires down at the incident location. When Citipower crew attended they found out that 3 wires were brought down by a tree branch on corner of Durham Rd and Dome St Surrey Hills. There was a small fire (4m x 1m), on the side walk. No other damages or injuries.
1055 | CitiPower 18/29 | CitiPower | 2019-06-03 | 01:13 | -37.86794797 | 145.03069605 | 701 Dandenong Road Malvern | 30203328 | AR007 | 11kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0004641 | 20190308PWA_01 | Citipower received an alarm indicating a feeder protection operation had occurred. It was found that a HV cross-arm had burnt allowing HV conductors to fall onto traction system passing underneath.
1056 | CitiPower 18/30 | CitiPower | 18/03/2019 | 12:07 | -37.81511907 | 144.96119119 | 433 Bourke St Melbourne 3000 | 33111907 | LQ003 | Low voltage AC (<1kV) | CBD | - switch (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | INC-0004725 | 20190319PWA_01 | Vic Fire reported a possible fire in an indoor substation at the incident location. Upon arrival the CitiPower crew found that the LV panel board ignited. The fire was extinguished by Fire Brigade. There was no reported injuries.
1057 | CitiPower 18/31 | CitiPower | 24/03/2019 | 15:39 | -37.8073 | 145.0651 | 29 GORDON STREET, BALWYN VIC 3103 | 30356235 | L001 | 11kV AC | Urban | - overhead conductor (bare; copper) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | INC-0006159 | 20190325PWA_03 | MFB reported fire in the vicinity of Cnr King and Gordon St Balwyn. Attending crews found high winds caused tree limb to fall across hv and lv near pole 863057 HVI damage was identified. An overheated connection was also found on pole 14139 , with a small fire also being reported at the base of this pole.
1058 | CitiPower 18/32 | CitiPower | 21/11/2018 | 0.68194 | -37.8297 | 144.939 | 39 Bertie St. Port Melbourne | 30205968 | MG014 | 11kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | INC-0007632 | 20190730PWA_01 | 11kV pole top fire.
1059 | Ausnet 18/19 | Ausnet | 2018-02-07 | 43283.7685 | -37.8158 | 145.3053 | 144 COLCHESTER ROAD, BAYSWATER NORTH VIC 3153 | 1208636 | CYN13 | Low voltage AC (<1kV) | URBAN | - luminaires (minor road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | E0025486 | 20190827SPN_03 | Street light has failed. Cause of failure unknown. Investigation conducted but inconclusive and unable to determine cause of failure.
1060 | Ausnet 18/20 | Ausnet | 2018-02-07 | 43283.7764 | -37.8481 | 145.2864 | 364 DORSET ROAD, BORONIA VIC 3155 | 5625975 | BWR22 | Low voltage AC (<1kV) | URBAN | - luminaires (major road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | E0004367 | 20181112SPN_04 | Street light head caught fire. Cause of failure unknown
1061 | Ausnet 18/21 | Ausnet | 2018-07-07 | 43288.7889 | -38.5175 | 145.7975 | 770 OUTTRIM-LEONGATHA ROAD, OUTTRIM VIC 3951 | 596635 | LGA23 | Low voltage AC (<1kV) | RURAL LONG | - connection box | single phase | Otherwise started by a distribution system | HBRA only | 1 | NO FORECAST | 0.1 | 0.1 | 234278 | 20180821SPN_01 | LV fuse box melted on pole LIS 596635 (cause unknown) resulting in small ground fire in the vacinity
1062 | Ausnet 18/22 | Ausnet | 2018-08-07 | 43289.9062 | -37.8314 | 145.2692 | 334-338 BAYSWATER ROAD, BAYSWATER NORTH VIC 3153 | 1201602 | BWR23 | Low voltage AC (<1kV) | URBAN | - luminaires (major road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | 234286 | 20190827SPN_01 | P/L fire on pole LIS1201602. P/L removed and replaced with new. Cause of failure unknown, Investigation inconclusive and did not determine cause of fire.
1063 | Ausnet 18/23 | Ausnet | 2018-12-07 | 43293.8467 | -38.2538 | 146.4745 | 440 FIRMINS LANE, HAZELWOOD NORTH VIC 3840 | 2615217 | TGN23 | 22kV AC | RURAL SHORT | - insulators | three phase | Otherwise started by a distribution system | HBRA only | 1 | NO FORECAST | 0.1 | 0.1 | 234390 | 20180713SPN_01 | Fault crew called to fault and small fire at Firmins lane Hazelwood. XLPE leads have been rubbing together at the gas switch causing one phase to rub through resulting in a fault to the earth screed of the other phase. Shutdown organised for a construction crew to replace the leads on TN099 and restore supply.
1064 | Ausnet 18/24 | Ausnet | 17/07/2018 | 43298.5999 | -37.5121 | 145.4257 | 220 CASTELLA ROAD, CASTELLA VIC 3777 | 1400651 | KLK11 | Low voltage AC (<1kV) | RURAL LONG | - transformer (pole mounted) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within electric line construction area | 19.8 | NO FORECAST | 0.1 | 1.98 | 234509 | 20180926SPN_01 | Tree branch that had been blown onto the LV bushings of the pole type substation. Supply was not interrupted and all fuses were still in. The fire did not cause any major damage to the customers property majority of the fire was contained within road reserve. The pole while it did have scorch marks on it from the fire appeared to just be cosmetic damage and nothing majorly structural. The tree branch had broken off due to the high winds that had occurred during that day. Fire observed in the area (approx. 30x8m).
1065 | Ausnet 18/25 | Ausnet | 19/07/2018 | 43300.8807 | -38.1516 | 146.7882 | 17 PRINCE STREET, ROSEDALE VIC 3847 | 5643756 | TGN41 | Low voltage AC (<1kV) | RURAL LONG | - luminaires (major road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | 234530 | 20190827SPN_04 | P/L fitting has failed and melted. on pole. Failed P/L fitting removed and replaced with new. Cause of failure unknown. Investigation conducted but inconclusive and unable to determine cause of failure.
1066 | Ausnet 18/26 | Ausnet | 2018-01-08 | 43313.3653 | -37.8604 | 145.377 | 1 WOOLRICH ROAD, OLINDA VIC 3788 | 1309467 | SFS1 | Low voltage AC (<1kV) | RURAL SHORT | - connection box | single phase | Otherwise started by a distribution system | within electric line construction area | 19.8 | NO FORECAST | 0.1 | 1.98 | 234714 | 20180809SPN_02 | The customer was fed via an old private underground service from pole LIS 1309467 which fed directly into their installation. Loose connections in the fused mains box resulted in pole fire only and no ground fire was present. Fault crew replaced the failed fused mains box with a new FOLCB. Burn marks on the pole and small pieces of plastic on the ground from the burnt out fused mains box but no evidence of ground fire.
1067 | Ausnet 18/27 | Ausnet | 2018-02-08 | 43314.0194 | -38.1241 | 145.8454 | 33 HEARN STREET, DROUIN VIC 3818 | 2704071 | WGL21 | Low voltage AC (<1kV) | RURAL LONG | - lamps (minor road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | 234718 | 20180809SPN_04 | DOA attended the site in daylight hours. Light had not been fixed and there were very small burn marks on the ground with bits of melted plastic in the vicinity of the burnt areas. Unable to determine cause of street light failure.
1068 | Ausnet 18/28 | Ausnet | 2018-03-08 | 43315.5979 | -37.6034 | 145.0948 | 1410 PLENTY ROAD, MERNDA VIC 3754 | 917511 | DRN12 | Low voltage AC (<1kV) | URBAN | - transformer (any other type) | single phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | NO FORECAST | 0.1 | 0.1 | 234756 | 20180808SPN_03 | The cap bank was installed and testing completed by AusNet testers. Installation was then livened, LV fuses closed before crew heard the Sec VT arcing and smoke observed just before the VT caught fire and self extinguished. Testers confirmed all the equipment was wired correctly and it appears to be equipment failure.
1069 | Ausnet 18/29 | Ausnet | 2018-04-08 | 43316.7875 | -37.6512 | 145.0165 | 130 COOPER STREET, EPPING VIC 3076 | 5658165 | EPG23 | Low voltage AC (<1kV) | URBAN | - luminaires (major road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | 234761 | 20180808SPN_02 | DAO arrived on site to find evidence of a burnt out 150w Street light. The street light was burnt from the top of the structure indicating faulty wiring rather than a blown globe. The light structure itself extends over the road so there was no ground fire to report. The fire was contained to the top of the pole. Fault crew had already attended site the night before but light had not been repaired/replaced as crew did not have spare 150W available at the time.
1070 | Ausnet 18/30 | Ausnet | 2018-05-08 | 43317.8417 | -37.7661 | 145.2396 | 34 CROYDON ROAD, CROYDON VIC 3136 | 1203025 | RWN31 | 22kV AC | RURAL SHORT | - earth / earthing | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | NO FORECAST | 0.1 | 0.46 | 234762 | 20180806SPN_01 | A possum short circuited the 22kV overhead conductor to earth on a steel X-arm on a concrete Substation pole. The short circuit caused the LV earth to be damaged at ground level where it was in contact with the earthed concrete pole. There was a small grass fire at the base of the pole of approximately 2 square metres, the fire did not spread, The pole is located in the road reserve, no property was damaged. The Substation that was affected is “Wonga P3 Colman” LIS # 1203025. The attending Fault crew were in the process of repairing damaged LV earth from the possum which caused a short circuit from conductor to steel X-arm on a concrete Substation pole when LEI arrived at site. Attending LEI inspected 3 affected properties along Croydon Rd Warrandyte South and found no evidence of HV injection. Control Room notified customers OK to return to supply upon completion of repairs.
1071 | Ausnet 18/31 | Ausnet | 2018-07-08 | 43319.9542 | -38.4722 | 145.949 | 43 TURNER STREET, LEONGATHA VIC 3953 | 2005194 | LGA22 | Low voltage AC (<1kV) | RURAL SHORT | - luminaires (major road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | 234792 | 20180808SPN_01 | Attending Fault crew found that the Active was disconnected and the it caught fire in head of light as a result of arching from moisture believed to be in the ballast.
1072 | Ausnet 18/32 | Ausnet | 15/08/2018 | 43327.0833 | -38.6435 | 146.4924 | 50 CLARK ROAD, HEDLEY VIC 3967 | 573608 | FTR12 | 22kV AC | RURAL LONG | - overhead conductor (bare; steel) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | NO FORECAST | 0.1 | 0.1 | 234867 | 20180820SPN_06 | Tree fell over line causing conductor to break and fall to ground igniting fire in span between poles LIS573608 and LIS2608426. Fire at t/off pole LIS2608424 from suspected conductor clashing as a result of tree twisting crossarm.
1073 | Ausnet 18/33 | Ausnet | 15/08/2018 | 43327.375 | -38.2818 | 146.1988 | 206 SAVIGES ROAD, THORPDALE VIC 3835 | 2203664 | MOE21 | 22kV AC | RURAL SHORT | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | NO FORECAST | 0.1 | 0.46 | 235039 | 20180827SPN_01 | Tree fell into and brought down overhead conductors starting a small ground fire.
1074 | Ausnet 18/34 | Ausnet | 20/08/2018 | 43332.4493 | -37.8672 | 145.2361 | 309 STUD ROAD, WANTIRNA SOUTH VIC 3152 | 1224715 | BRA21 | Low voltage AC (<1kV) | URBAN | - luminaires (major road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | 234965 | 20180820SPN_01 | Internal light fitting fault. It would appear that the top cover dropped off some time ago leaving the internal control gear and wires exposed, causing the wiring to deteriorate and the PE base to fill up with water, Over time this caused a short to the body of the lantern livening up the concrete pole.
1075 | Ausnet 18/35 | Ausnet | 28/08/2018 | 43340.4174 | -37.8043 | 147.4904 | 85 WINDMILL LANE, LINDENOW VIC 3865 | 1608131 | BDL44 | Low voltage AC (<1kV) | RURAL LONG | - connection box | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | E0004360 | 20181109SPN_05 | Crew attended site and found LV Krone box had melted and a small burnt area was evident at the base of the pole. Fire was out when crew arrived. Isolated supply and replaced Krone box.
1076 | Ausnet 18/36 | Ausnet | 29/08/2018 | 43341.7736 | -37.6982 | 145.1618 | 40 LEANE DRIVE, ELTHAM VIC 3095 | 5645776 | ELM15 | 22kV AC | RURAL SHORT | - transformer (kiosk mounted) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | E0003348 | 20181116SPN_03 | Kiosk transformer failed as a result of failed/damaged connections leading to insulation heating up and subsequently catching fire.
1077 | Ausnet 18/37 | Ausnet | 30/08/2018 | 43342.7479 | -38.1994 | 146.5255 | 19 GARIBALDI STREET, TRARALGON VIC 3844 | 2603531 | TGN43 | Low voltage AC (<1kV) | URBAN | - connection box | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | 235112 | 20180903SPN_06 | The middle phase of the FSD unit has overheated and melted. Cause could not be determined. Melted plastic observed at the base of the pole but no evidence of fire
1078 | Ausnet 18/38 | Ausnet | 2018-03-10 | 43376.7097 | -38.0703 | 145.4941 | RACECOURSE ROAD, PAKENHAM VIC 3810 | 503172 | PHM21 | 22kV AC | URBAN | - arc suppresion coil | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0002634 | 20181005SPN_01 | Whilst closing the No. 2 Cap Bank and it's No2 Step Switch, the cap bank CT failured resulting in fire at the cap bank tripping both the CB and Step Switch on Earth Fault. Asset failure report not available
1079 | Ausnet 18/39 | Ausnet | 19/10/2018 | 43392.4549 | -37.8792 | 147.9875 | 17 CHURCH STREET, LAKES ENTRANCE VIC 3909 | 1901962 | BDL41 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0003359 | 20181113SPN_01 | Blown EDO fuse appears to have been candling. No fire
1080 | Ausnet 18/40 | Ausnet | 19/10/2018 | 43392.8844 | -37.6828 | 145.0196 | 48 HEYINGTON AVENUE, THOMASTOWN VIC 3074 | 910335 | TT5 | 22kV AC | URBAN | - switch (any other type) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0004496 | 20181112SPN_02 | Investigation conducted but inconclusive, cause of fire unknown and no failed assets involved. Feeder re-close occurred and VicFire reported a pole fire spreading to trees. Fault crew dispatched and, upon arrival, identified scorch marks on the ground near switch pole LIS910335. Fire fighters on site and informed fault crew there was an explosion at the pole followed by a small fire on the ground. No signs of any animal or vegetation in the vicinity that could be attributed to the failure. Pole and switch inspected and no visible damage or cause identified that would account for the fire.
1081 | Ausnet 18/41 | Ausnet | 22/10/2018 | 43395.5625 | -37.5431 | 144.9786 | 910 DONNYBROOK ROAD, DONNYBROOK VIC 3064 | 932480 | KLO14 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0003461 | 20181113SPN_02 | Fault crew believe conductor may have been hit by an excavator resulting in a mid span break of the O/H conductors and one fuse operating and another candling. 10m of conductor was replaced on the phase that fell to the ground and the other phase was repaired using a splice. There are no reported injuries or damage and the ground clearance of the O/H conductor was deemed to be sufficient/compliant. Details of the excavator and the operator are not available as the excavator had left the site prior to the fault crew arriving.
1082 | Ausnet 18/42 | Ausnet | 24/10/2018 | 43397.6404 | -37.8771 | 145.3994 | 26 BAYNES PARK ROAD, MONBULK VIC 3793 | 1321322 | BGE11 | Low voltage AC (<1kV) | RURAL SHORT | - connection box | three phase | Otherwise started by a distribution system | within electric line construction area | 19.8 | LOW-MODERATE | 0.2 | 3.96 | E0004372 | 20181109SPN_04 | FOLCB has failed internally possibly as a result of poor neutral connections. Failed FOLCB removed and replaced with new, damaged dropper cables replaced and re-terminated.
1083 | Ausnet 18/43 | Ausnet | 31/10/2018 | 43404.5278 | -37.6996 | 145.1027 | 1 KALPARRIN AVENUE, GREENSBOROUGH VIC 3088 | 903803 | WT5 | Low voltage AC (<1kV) | URBAN | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0004005 | 20181101SPN_01 | Unknown truck contacted and brought down O/H LV lines resulting in ground fire. Truck and driver details unknown and not available. It is not known what the truck was doing when it contacted the O/H conductor
1084 | Ausnet 18/44 | Ausnet | 2018-01-11 | 43405.3361 | -38.6126 | 146.6594 | RANKIN STREET, ALBERTON VIC 3971 | 2608518 | FTR23 | Low voltage AC (<1kV) | RURAL LONG | - connection box | three phase | Otherwise started by a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | E0004070 | 20190827SPN_02 | Fused Mains box has burnt and melted on pole LIS2608518. Investigation conducted but inconclusive, unable to determine cause of failure.
1085 | Ausnet 18/45 | Ausnet | 2018-02-11 | 43406.0833 | -37.4024 | 144.977 | 11 NEMOYA COURT, WALLAN VIC 3756 | 912718 | KLO24 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | E0004097 | 20181107SPN_01 | Candled HV EDO fuse
1086 | Ausnet 18/46 | Ausnet | 2018-04-11 | 43408.7497 | -38.0451 | 147.0314 | BENELONG, 90 HOLTS LANE, BUNDALAGUAH VIC 3851 | 2500388 | SLE32 | 22kV AC | RURAL SHORT | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0004173 | 20181107SPN_03 | Tree stump visible when site attended for investigation but tree was missing from site. Remaining debris from the tree indicates it had fallen over towards the HV line in between CAM's 2500389 and 2500388, making contact with the OH conductors. Single tree failure impacted line. Fire started, burnt road reserve edge and up to an irrigation ditch, linear strip. [Tree and all debris had been cleared up prior to inspection].
1087 | Ausnet 18/47 | Ausnet | 2018-06-11 | 43410.6618 | -37.7976 | 145.2396 | 17 PANFIELD AVENUE, RINGWOOD VIC 3134 | 1209065 | RWN33 | Low voltage AC (<1kV) | URBAN | - connection box | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0004241 | 20190110SPN_01 | Krone box had melted and caused burnt plastic to fall onto the ground. No damage to any customers property and no ground fire present. All damage was caused in road reserve. Fire was cause by a fault in the Krone box due to severe weather and rain earlier on during the day
1088 | Ausnet 18/48 | Ausnet | 2018-07-11 | 43411.7188 | -38.6354 | 146.1125 | 778 WHITELAWS TRACK, BUFFALO VIC 3958 | 2024579 | FTR21 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0004292 | 20181205SPN_02 | Candling fuse.
1089 | Ausnet 18/49 | Ausnet | 2018-08-11 | 43412.4688 | -37.8253 | 147.5781 | 320 DOCKERTYS ROAD, WY YUNG VIC 3875 | 1603550 | BDL44 | Low voltage AC (<1kV) | RURAL LONG | - connection box | two phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0004423 | 20181109SPN_02 | Degradation of Krone Box
1090 | Ausnet 18/50 | Ausnet | 2018-08-11 | 43412.5861 | -36.9374 | 145.4195 | 644 PONKEEN CREEK ROAD, TARCOMBE VIC 3666 | 3902809 | BN1 | 12.7kV AC (SWER) | RURAL LONG | - fuse (EDO fuse) | single wire earth return (SWER) | Started by lightning striking a distribution system or a part of a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0004540 | 20181116SPN_01 | The EDO fuse operation was triggered by lightning in the area. The hung up of the fuse is due to accumulation of dry mud at the bottom of the fuse by insect/wasp. When the fuse link blows the tension is unable to be released causing the spring and the tube to hang up.
1091 | Ausnet 18/51 | Ausnet | 2018-09-11 | 43413.9333 | -38.0221 | 146.6694 | 2439 TRARALGON-MAFFRA ROAD, COWWARR VIC 3857 | 2601800 | TGN31 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0004494 | 20181112SPN_01 | Candling EDO fuse
1092 | Ausnet 18/52 | Ausnet | 15/11/2018 | 43419.573 | -37.9222 | 145.4756 | 3 UPPER GRIEVE ROAD, AVONSLEIGH VIC 3782 | 420243 | BGE22 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0004784 | 20181115SPN_01 | candling EDO fuse. No ground fire.
1093 | Ausnet 18/53 | Ausnet | 16/11/2018 | 43420.9139 | -38.1973 | 146.5253 | 45 LAFAYETTE STREET, TRARALGON VIC 3844 | 2603888 | TGN43 | Low voltage AC (<1kV) | URBAN | - luminaires (minor road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0004855 | 20181205SPN_03 | This is an older public light where the igniter or starter has failed causing a head fire. Failed head has been removed and replaced it with new.
1094 | Ausnet 18/54 | Ausnet | 2018-01-12 | 43435.9896 | -38.0169 | 145.3182 | 56 RYELANDS DRIVE, NARRE WARREN VIC 3805 | 5693444 | NRN13 | Low voltage AC (<1kV) | URBAN | - luminaires (minor road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | E0006173 | 20181214SPN_05 | Cause of street light failure not known. Light fitting replaced. Street light head fire only and no ground fire present
1095 | Ausnet 18/55 | Ausnet | 2018-02-12 | 43436.4444 | -37.7454 | 145.2623 | 1-11 WALKER ROAD, WONGA PARK VIC 3115 | 1203478 | CPK11 | 22kV AC | URBAN | - overhead conductor (bare; all aluminium conductor) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0005618 | 20181205SPN_01 | Branch blew out of tall Eucalyptus on opposite side of road approx. 10m away and landed on lines. A very small fire started below.
1096 | Ausnet 18/56 | Ausnet | 2018-03-12 | 43437.6167 | -36.8749 | 145.6136 | 1589 EUROA-MANSFIELD ROAD, GOORAM VIC 3666 | 3904896 | BN1 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0005715 | 20181205SPN_04 | Candling BA fuse on s/stn.
1097 | Ausnet 18/57 | Ausnet | 2018-05-12 | 43439.2951 | -36.3555 | 146.2965 | 59 RANGEVIEW AVENUE, WANGARATTA VIC 3677 | 5107251 | WN4 | 22kV AC | RURAL SHORT | - fuse (powder filled) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0005799 | 20181205SPN_06 | Candled HV EDO Fuse on s/stn pole. No evidence of ground fire
1098 | Ausnet 18/58 | Ausnet | 2018-07-12 | 43441.6823 | -37.0499 | 146.0807 | 173-175 HIGH STREET, MANSFIELD VIC 3722 | 3916716 | MSD4 | Low voltage AC (<1kV) | RURAL LONG | - overhead service conductor (residential) | two phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0006056 | 20181210SPN_01 | branch of an adjacent red gum outside clearance broke and fell through overhead service, bringing conductors to ground amongst grassy area. The limb also glanced service pole 3916716 and decked a service line resulting in a ground fire. Red gums are known for limb-shedding/bifurcation. In this event the red gum was 6 meters away from the insulated service line when the branch failed at the point of attachment. There are no externally visible signs of decay so this failure could not have been predicted. Pole inspected and cleared for service. Push test passed before the overhead service line replaced the following day. The pole has no outstanding maintenance items.
1099 | Ausnet 18/59 | Ausnet | 2018-09-12 | 43443.5111 | -38.1078 | 145.8502 | 180 MAIN NEERIM ROAD, DROUIN VIC 3818 | 2717457 | WGL21 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0006073 | 20181210SPN_02 | Candling HV fuse on pole s/stn.
1100 | Ausnet 18/60 | Ausnet | 2018-11-12 | 43445.1657 | -37.6588 | 145.5022 | 45 MCGRETTONS ROAD, HEALESVILLE VIC 3777 | 1403502 | LDL23 | Low voltage AC (<1kV) | RURAL LONG | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0006156 | 20181214SPN_02 | Large pine (DBH over 1m) has failed in ground falling across road and contacting and bringing down O/H HV and LV conductors resulting in a ground fire is approx. 0.5sqm in size. Fire occurred in road reserve and did not do any damage to any residential property. No one was injured in this event. Fire was out on arrival. Evidence of decay on line side of roots but only visible post failure. Other trees in row appear in good health. Small grass fire at base of pole. Grass fairly green with low fuel load. Fire burnt dead tufts of oat grass Line repaired and supply restored.
1101 | Ausnet 18/61 | Ausnet | 2018-12-12 | 43446.6965 | -37.6696 | 145.1365 | 49 HILLMARTIN LANE, DIAMOND CREEK VIC 3089 | 926857 | ELM12 | Low voltage AC (<1kV) | URBAN | - underground service cable (residential) | two phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0006263 | 20181214SPN_04 | Cause of fire was poor connection of tape on the active. Due to the dry nature of the area this resulted in a fire starting.
1102 | Ausnet 18/62 | Ausnet | 13/12/2018 | 43447.5604 | -38.091 | 145.7791 | 60 PRINCES WAY, LONGWARRY NORTH VIC 3816 | 2708577 | WGL12 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0006347 | 20181214SPN_01 | Candling due to suspected moisture ingress/weathering
1103 | Ausnet 18/63 | Ausnet | 13/12/2018 | 43447.8639 | -36.1342 | 147.0087 | BONEGILLA MIGRANT CENTRE, 82 BONEGILLA ROAD, BONEGILLA VIC 3691 | 5209671 | WOTS25 | 22kV AC | RURAL SHORT | - fuse (boric acid) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0006377 | 20181214SPN_03 | SUSPECTED LIGHTNING STRIKE
1104 | Ausnet 18/64 | Ausnet | 14/12/2018 | 43448.3979 | -38.0945 | 145.7267 | 33 ABECKETT ROAD, BUNYIP VIC 3815 | 522029 | WGL12 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0006409 | 20181219SPN_01 | Unable to establish root cause
1105 | Ausnet 18/65 | Ausnet | 17/12/2018 | 43451.2736 | -38.3145 | 145.9088 | 172 FERNDALE-STRZELECKI ROAD, FERNDALE VIC 3821 | 2005124 | LGA24 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0007026 | 20190111SPN_05 | Candled EDO fuse. Replaced fuse and restored supply.
1106 | Ausnet 18/66 | Ausnet | 17/12/2018 | 43451.441 | -38.5155 | 145.9827 | 275 NERRENA HALL ROAD, NERRENA VIC 3953 | 2001171 | LGA14 | 12.7kV AC (SWER) | RURAL LONG | - fuse (EDO fuse) | single wire earth return (SWER) | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0006540 | 20181218SPN_01 | Animal induced - Possum on line
1107 | Ausnet 18/67 | Ausnet | 18/12/2018 | 43452.0563 | -36.3206 | 146.8991 | 16 FLYNNS LANE, OSBORNES FLAT VIC 3691 | 5626316 | WOTS11 | 12.7kV AC (SWER) | RURAL LONG | - fuse (any other type) | single wire earth return (SWER) | Otherwise started by a distribution system | within electric line construction area | 19.8 | LOW-MODERATE | 0.2 | 3.96 | E0006713 | 20181218SPN_02 | Degraded internal connection. It appears the striker pin did not operate to let the Boric Acid fuse fall out.
1108 | Ausnet 18/68 | Ausnet | 18/12/2018 | 43452.25 | -36.3902 | 146.5241 | 32 DICKENS ROAD, EVERTON UPPER VIC 3678 | 4501721 | WN5 | 12.7kV AC (SWER) | RURAL LONG | - fuse (boric acid) | single wire earth return (SWER) | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0006717 | 20181218SPN_03 | HV fuse candled. It appears the striker pin may not have operated to drop the Boric Acid fuse out. There was no evidence of ground fire.
1109 | Ausnet 18/69 | Ausnet | 19/12/2018 | 43453.8139 | -37.7048 | 145.1603 | 66 BEARD STREET, ELTHAM VIC 3095 | 918697 | ELM13 | Low voltage AC (<1kV) | URBAN | - pole (wood) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0006823 | 20181220SPN_01 | white phase fused isol appears to have burnt at the 'U' bolt resulting in a small fire at base of pole
1110 | Ausnet 18/70 | Ausnet | 20/12/2018 | 43454.7188 | -36.2294 | 146.4197 | 168 ROBBINS ROAD, BORALMA VIC 3682 | 5105160 | WN3 | 12.7kV AC (SWER) | RURAL LONG | - fuse (EDO fuse) | single wire earth return (SWER) | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0006941 | 20181221SPN_01 | Suspected damage due to weather - lightning
1111 | Ausnet 18/71 | Ausnet | 22/12/2018 | 43456.7532 | -37.2094 | 145.2368 | 775 KING PARROT CREEK ROAD, STRATH CREEK VIC 3658 | 4704598 | SMR14 | 22kV AC | RURAL LONG | - insulators | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0007046 | 20190110SPN_03 | Animal/bird - magpie caused grass fire
1112 | Ausnet 18/72 | Ausnet | 27/12/2018 | 43461.8569 | -37.703 | 145.1641 | 1320 MAIN ROAD, ELTHAM VIC 3095 | 928838 | ELM13 | Low voltage AC (<1kV) | URBAN | - connection box | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | VERY HIGH | 1 | 0.2 | E0007097 | 20190111SPN_03 | FOLCB on Pole LIS928838 had caught fire and subsequently melted. There was no structural damage to the pole, only slight cosmetic damage where the fire had scorched it. As a result of the fire the remains of the FOLCB had melted and fell onto the ground in scattered pieces. There was a small ground fire as a consequence approx. 20cm by 10cm in length. The cause of the fire was not load related as the overhead service was still in tact (2x25mm O/H service. It appears as though the fire had started via a loose connection and high humidity which led to a spark ignited inside the FOLCB. No damage to the customers property occurred. All damage was located in road reserve.
1113 | Ausnet 18/73 | Ausnet | 29/12/2018 | 43463.845 | -38.1945 | 146.5448 | 14 PETERKIN STREET, TRARALGON VIC 3844 | 2604877 | TGN42 | 22kV AC | URBAN | - connector / termination | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | E0007157 | 20190111SPN_07 | Suspected drizzle rain after the hot and dry days caused possum proofing to catch fire.
1114 | Ausnet 18/74 | Ausnet | 29/12/2018 | 43463.8896 | -38.1646 | 145.9073 | 27 CAMELOT COURT, WARRAGUL VIC 3820 | 2720623 | WGL11 | 22kV AC | RURAL SHORT | - fuse (boric acid) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | E0007156 | 20190111SPN_06 | Fault Crew attended and found a magpie had shorted across the BA Unit causing the fuse to candle. Crew removed the bird and replaced the fuse.
1115 | Ausnet 18/75 | Ausnet | 2019-04-01 | 43469.625 | -37.6997 | 145.1588 | 55 ZIG ZAG ROAD, ELTHAM VIC 3095 | 918744 | ELM15 | 22kV AC | RURAL SHORT | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | SEVERE | 2 | 0.4 | E0007238 | 20190111SPN_09 | A small branch appears to have broken from the upper canopy of the tree and contacted o/h conductors. The branch appears to have smouldered on the lines and fallen to the ground which may have started a small grass fire. The tree in question was a Council owned Eucalyptus situated 4m beside the nearest conductor in LBRA Declared (Council responsibility). A very small branch failed due to strong winds and landed on the HV conductors and the resultant smouldering is believed to be the cause of a 2m sq ground fire.
1116 | Ausnet 18/76 | Ausnet | 2019-05-01 | 43470.9776 | -38.5258 | 146.5983 | 437 BOLGERS ROAD, DEVON NORTH VIC 3971 | 2624660 | FTR12 | 22kV AC | RURAL LONG | - fuse (boric acid) | three phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0007243 | 20190108SPN_02 | fuse candling
1117 | Ausnet 18/77 | Ausnet | 2019-09-01 | 43474.6257 | -38.1178 | 145.2674 | 39-45 CYRIL BEECHEY LANE, CRANBOURNE VIC 3977 | 509840 | CRE32 | 22kV AC | URBAN | - insulators | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0007571 | 20190111SPN_04 | Suspected 22kV insulator tracking through a pole stay rod resulting in pole top fire and failure of HV Strain structure, No evidence of ground fire.
1118 | Ausnet 18/78 | Ausnet | 2019-10-01 | 43475.7097 | -37.4799 | 145.2745 | 14 MARGARET STREET, KINGLAKE WEST VIC 3757 | 1411055 | KLK21 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0007627 | 20190111SPN_02 | 22kV EDO fuse is suspected to have hung-up and candled. There was no evidence of ground fire
1119 | Ausnet 18/79 | Ausnet | 2019-12-01 | 43477.7653 | -38.1856 | 145.6623 | 5 HUMPHRIES ROAD, CATANI VIC 3981 | 513501 | LLG11 | 22kV AC | RURAL SHORT | - overhead conductor (bare; steel) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0007738 | 20190115SPN_03 | Tractor contacted single phase 22kV O/H conductors between Cam Poles #513501 & # 513508 while moving bales of hay across his paddock. 2 small grass fires resulted (which was put out by the customer) measuring 1.5x1.5m and 1mx1m (6.25m sq total) Upon investigation, the height of the HV conductors where incident occurred was approximately 4.5m. No fuses or recloses occurred when tractor came into contact with HV. There was no damage to customer’s tractor or property other than the small grass fire on his land. Conductors repaired and restrung to approx. 6.3m to provide additional ground clearance
1120 | Ausnet 18/80 | Ausnet | 13/01/2019 | 43478.8889 | -36.2588 | 147.0923 | MURRAY VALLEY HIGHWAY, HUON 3695 | 5214084 | WOTS13 | 22kV AC | RURAL LONG | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | VERY HIGH | 1 | 4.6 | E0007830 | 20190114SPN_01 | Found 2 dead magpies at base of pole and center phase isolator from switch #601495 for the tee off conductors had part of the top shed of porcelain missing and flash marks evident.
1121 | Ausnet 18/81 | Ausnet | 15/01/2019 | 43480.6493 | -37.857 | 146.9927 | 47 MORGANS ROAD, BOISDALE VIC 3860 | 2513039 | MFA21 | Low voltage AC (<1kV) | RURAL LONG | - switch (disconnector/isolator) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | VERY HIGH | 1 | 0.2 | E0007916 | 20190115SPN_06 | Degraded hot connection
1122 | Ausnet 18/82 | Ausnet | 16/01/2019 | 43481.6326 | -38.4527 | 145.7395 | 490 ANDERSONS INLET ROAD, BENA VIC 3946 | 2008210 | LGA23 | 22kV AC | RURAL LONG | - pole (wood) | three phase | Otherwise started by a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | E0008129 | 20190117SPN_01 | The tie on the insulator has failed, possibly due to a lightning strike based on evidence of black charring on the insulator. The conductor has dropped and come in to contact with the pole, burning through the pole causing the top section to fail and fall to ground resulting in a small grass fire.
1123 | Ausnet 18/83 | Ausnet | 16/01/2019 | 43481.9201 | -38.0266 | 145.6039 | 40 MORTIMER ROAD, TYNONG NORTH VIC 3813 | 524311 | PHM33 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | E0008495 | 20190125SPN_01 | crew arrived on site to find a candled EDO fuse. Fuse was replaced and supply restored
1124 | Ausnet 18/84 | Ausnet | 17/01/2019 | 43482.4486 | -36.969 | 147.6045 | 895 OMEO VALLEY ROAD, OMEO VIC 3898 | 1605874 | BDL8 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | three phase | Started by lightning striking a distribution system or a part of a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0008180 | 20190117SPN_03 | Most probable cause is lightning strike (as indicated by evidence found on site i.e. black patches on concrete pole and exit marks etc.).
1125 | Ausnet 18/85 | Ausnet | 21/01/2019 | 43486.2188 | -37.7003 | 145.0974 | 14 Glamis st, Greensborough | 903905 | WT5 | 22kV AC | URBAN | - pole (wood) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | E0008305 | 20190121SPN_01 | MFB reported an explosion from pole and small fire on ground next to base of sub pole. Fire extinguished before fault crew arrived. Investigation conducted and no damage or fault could be identified that could be attributed to the reported fire. Investigation inconclusive and no cause found.
1126 | Ausnet 18/86 | Ausnet | 21/01/2019 | 43486.7646 | -37.669 | 145.162 | 1 LUSCOMBE DRIVE, DIAMOND CREEK VIC 3089 | 926985 | ELM15 | Low voltage AC (<1kV) | RURAL SHORT | - connection box | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | E0008397 | 20190122SPN_01 | The sheeting on the leads coming out from the supply transformer to the TX ISOL’s Krone box was melted and the spillage of the plastic fell to ground. Possible Overloaded TX / TX leads or loose terminals in the TX ISOL Krone box.
1127 | Ausnet 18/87 | Ausnet | 24/01/2019 | 43489.8042 | -37.886 | 145.37 | DANDENONG RANGES NATIONAL PARK, 70 MONBULK ROAD, SHERBROOKE VIC 3789 | 1305203 | BGE11 | Low voltage AC (<1kV) | RURAL SHORT | - overhead conductor (ABC) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within electric line construction area | 19.8 | VERY HIGH | 1 | 19.8 | E0008623 | 20190125SPN_03 | A branch has broken off a very large healthy Mt Ash tree contacting and bringing down 2 bays of LV ABC as it fell to ground resulting in a small 1m x 1m square fire. The tree was not identified as being hazardous
1128 | Ausnet 18/88 | Ausnet | 25/01/2019 | 43490.6424 | -38.1786 | 146.2761 | 21 DINWOODIE DRIVE, NEWBOROUGH VIC 3825 | 2207877 | MOE31 | 22kV AC | RURAL LONG | - fuse (powder filled) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | SEVERE | 2 | 0.4 | E0008722 | 20190125SPN_05 | Candled fuse. Fuse replaced and supply restored
1129 | Ausnet 18/89 | Ausnet | 26/01/2019 | 43491.941 | -37.8006 | 145.3294 | 214 CAMBRIDGE ROAD, KILSYTH VIC 3137 | 1001084 | CYN33 | 22kV AC | URBAN | - automatic circuit recloser (ACR) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | E0008754 | 20190130SPN_02 | Line Crews found Possum had got on top of ACR LD070. Charring between on pole approx.1m between ACR. Scorched earth at base of ACR and burnt shrubs outside the property approx. 1.5m long x 250mm wide. MFB put out small fire in shrubs next to the property fence prior to the fault crew's arrival. Fault crew made safe and carried out repairs
1130 | Ausnet 18/90 | Ausnet | 27/01/2019 | 43492.1251 | -36.274 | 147.0575 | 334 GENTLE ROAD, GUNDOWRING VIC 3691 | 5201242 | WOTS11 | Low voltage AC (<1kV) | RURAL LONG | - overhead service conductor (residential) | two phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0008757 | 20190128SPN_01 | Customer drawing 40 amps of load regularly. Appears connections in FOLCB on pole have dried and deteriorated resulting in the failure of the box
1131 | Ausnet 18/91 | Ausnet | 28/01/2019 | 43493.4146 | -37.8784 | 147.9582 | KALIMNA HOTEL, 21 KALIMNA JETTY ROAD, KALIMNA VIC 3909 | 1901592 | BDL6 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0008761 | 20190130SPN_04 | Candled EDO fuse, no evidence of ground fire. Fuse replaced.
1132 | Ausnet 18/92 | Ausnet | 29/01/2019 | 43494.9563 | -37.3642 | 145.0327 | 23 MCDONALD DRIVE, WANDONG VIC 3758 | 928497 | KMS12 | Low voltage AC (<1kV) | RURAL SHORT | - switch (disconnector/isolator) | two phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | VERY HIGH | 1 | 4.6 | E0008870 | 20190131SPN_01 | FOLCB on pole failed and burnt resulting in a ground fire at the base of the pole. Cause of FOLCB failure unknown. Fault truck attended, replaced FOLCB and restored supply
1133 | Ausnet 18/93 | Ausnet | 30/01/2019 | 43495.6611 | -36.334 | 145.9633 | 2346 BENALLA-YARRAWONGA ROAD, DEVENISH VIC 3726 | 3903372 | BN2 | 12.7kV AC (SWER) | RURAL LONG | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by lightning striking a distribution system or a part of a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0009020 | 20190204SPN_05 | Lightning brought down HV wires which resulted in multiple fire starts on the ground
1134 | Ausnet 18/94 | Ausnet | 31/01/2019 | 43496.2299 | -38.275 | 145.5729 | 280 MCDONALDS TRACK, LANG LANG VIC 3984 | 514128 | LLG12 | 22kV AC | RURAL SHORT | - fuse (boric acid) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0009016 | 20190131SPN_03 | Candling HV fuse. Fuse replaced and supply restored. No evidence of ground fire
1135 | Ausnet 18/95 | Ausnet | 31/01/2019 | 43496.2306 | -38.1727 | 145.7805 | 130 LYE AND DIXON ROAD, RIPPLEBROOK VIC 3818 | 2703396 | WGL11 | 22kV AC | RURAL SHORT | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | E0009015 | 20190131SPN_02 | Tree impact - Caused by hazardous tree branch failure which was outside the clearance space. Eucalyptus ovata on western side of conductors located approximately 18m from the nearest conductor and approximately 80m from pole 2703397. Tree has evidence of branch failure from pest infestation in the branch attachment point (borer and ants). Refer to photos. The span was last inspected on the 24th of May 2018 and cleared on the 24th of January 2019.
1136 | Ausnet 18/96 | Ausnet | 2019-01-02 | 43497.5417 | -37.0655 | 146.1466 | 615 MT BULLER ROAD, MANSFIELD VIC 3722 | 3917428 | MSD1 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0009249 | 20190219SPN_02 | EDO HV Fuse candling. There had been lightning in the area prior to the event. When the crew arrived they checked the LV volts which were fluctuating and it was noticed one of the HV fuses had candled. Fuse tube was replaced and supply restored. There was no fire or burn marks at the base of the pole.
1137 | Ausnet 18/97 | Ausnet | 2019-01-02 | 43497.5542 | -37.7563 | 145.3532 | 13 MARKET STREET, LILYDALE VIC 3140 | 1008581 | LDL12 | 22kV AC | URBAN | - pole (wood) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | E0010602 | 20190218SPN_01 | Bird made contact with exposed HV conductor at the Cable Head Pole resulting in scorch marks on ground 0.1m square where the bird fell to ground
1138 | Ausnet 18/98 | Ausnet | 2019-01-02 | 43497.7931 | -38.6999 | 146.047 | 225 CORNWALLS ROAD, FISH CREEK VIC 3959 | 2023994 | FTR22 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | E0009270 | 20190204SPN_02 | Customer contacted AusNet advising they had fluctuating volts, fault crew was dispatched and, upon arrival, found a candling ELF fuse tube. Fuse replaced and supply restored. No evidence of ground fire
1139 | Ausnet 18/99 | Ausnet | 2019-02-02 | 43498.9535 | -37.2512 | 144.9184 | 100 CAMPASPE ROAD, WILLOWMAVIN VIC 3764 | 4702628 | KMS11 | 12.7kV AC (SWER) | RURAL SHORT | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within electric line construction area | 19.8 | VERY HIGH | 1 | 19.8 | E0009278 | 20190204SPN_01 | insulator make DIA (Dalton Insulators Australia) manufacture year 1980 broke due to crack around the conductor groove. The crack was caused by cement growth.
1140 | Ausnet 18/100 | Ausnet | 2019-03-02 | 43499.2931 | -37.6996 | 145.1813 | 46 INGRAMS ROAD, RESEARCH VIC 3095 | 919354 | ELM13 | 22kV AC | URBAN | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | SEVERE | 2 | 0.4 | E0009283 | 20190212SPN_03 | Possum on HV conductor, caught fire and fell to ground resulting in small fire (2m x 3m) at pole of pole
1141 | Ausnet 18/101 | Ausnet | 2019-03-02 | 43499.7806 | -37.602 | 145.2828 | 10 WILMA GROVE, ST ANDREWS VIC 3761 | 920541 | DRN23 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | HBRA only | 1 | SEVERE | 2 | 2 | E0009287 | 20190212SPN_04 | candling HV fuse resulting in small ground fire
1142 | Ausnet 18/102 | Ausnet | 2019-05-02 | 43501.5243 | -38.4459 | 145.7542 | 50 JAMES ROAD, BENA VIC 3946 | 2007971 | LGA23 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | E0009466 | 20190207SPN_01 | Candled fuse and no evidence of ground fire. Fuse replaced
1143 | Ausnet 18/103 | Ausnet | 2019-06-02 | 43502.3007 | -38.3519 | 146.3824 | 610 JUMBUK ROAD, YINNAR SOUTH VIC 3869 | 2614576 | MWT31 | 22kV AC | RURAL SHORT | - overhead conductor (bare; steel) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0009546 | 20190207SPN_03 | Hazardous tree branch which was outside the clearance space: Bifurcated, Semi Mature Euc sp (H16m, DBH 700mm), has faulted at a point 1.7m from ground level and fallen onto HV conductors. Point of failure was on rear side of leader (non-line side/Sth side of line side leader), where Fungal Fruiting Body was present at site of previous failure. This would not have been visible from a span assessment. Decay and build up of soil present in center of the leader (deadwood), at the site of the Fruiting Body and down to ground level. Please refer to attached photos.
1144 | Ausnet 18/104 | Ausnet | 2019-06-02 | 43502.5417 | -37.6893 | 145.1008 | 17 COROWA CRESCENT, GREENSBOROUGH VIC 3088 | 5720978 | WT13 | Low voltage AC (<1kV) | URBAN | - LV pillar | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | E0009621 | 20190213SPN_03 | LV supply pillar in customer's front yard has failed internally resulting in a small shrub, adjacent to the pillar, being burnt, No damage to customer property. Pillar appears to have failed due to age (approx. 40 years old)
1145 | Ausnet 18/105 | Ausnet | 2019-06-02 | 43502.5521 | -38.0173 | 145.9736 | 18 MACKINTOSH ROAD, NEERIM SOUTH VIC 3831 | 2700235 | WGL24 | 22kV AC | RURAL LONG | - transformer (pole mounted) | single phase | Started by any other thing forming part of or coming into contact with a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0009630 | 20190828SPN_01 | Crew arrived and found the grass beneath the transformer was burnt, but no fire was present when crew arrived. Transformer had a slow oil leak from the HV bushing and had failed but attending crew advised the fire did not start from the transformer. Investigation conducted but exact cause of fire inconclusive. Attending crew advised civil works had taken place in the vicinity and the grass fire may have been caused by the circuit breaker on pole.
1146 | Ausnet 18/106 | Ausnet | 2019-07-02 | 43503.65 | -38.1099 | 145.4863 | 990 KOO WEE RUP ROAD, PAKENHAM VIC 3810 | 515966 | PHM22 | 22kV AC | RURAL SHORT | - underground cable | three phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0009793 | 20190213SPN_04 | HV cable on Blue phase of cable head pole has failed and burnt resulting in a ground fire. The insulation on the blue phase dropper appears to have degraded resulting in failure and subsequent fire.
1147 | Ausnet 18/107 | Ausnet | 2019-07-02 | 43503.8806 | -37.9827 | 145.3192 | 165 ROBINSON RD, NARRE WARREN NORTH VIC 3804 | 519932 | LYD14 | 22kV AC | RURAL SHORT | - surge diverter | three phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0009795 | 20190213SPN_05 | Surge Diverter on Blue phase of cablehead pole appears to have failed resulting in small ground fire approx. 1m sq.
1148 | Ausnet 18/108 | Ausnet | 2019-08-02 | 43504.8118 | -37.7585 | 145.4304 | 8A MAURICE ROAD, GRUYERE VIC 3770 | 1002281 | LDL23 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0009921 | 20190211SPN_04 | Candled EDO HV fuse following bird contacting O/H HV conductors. No damaged to AusNet assets and no evidence of ground fire
1149 | Ausnet 18/109 | Ausnet | 2019-09-02 | 43505.7139 | -38.8324 | 146.1326 | 11 TRELAWNY AVENUE, SANDY POINT VIC 3959 | 2021646 | FTR22 | Low voltage AC (<1kV) | RURAL SHORT | - connection box | three phase | Otherwise started by a distribution system | HBRA only | 1 | VERY HIGH | 1 | 1 | E0009927 | 20190211SPN_03 | Pole mounted Fused Mains Box has failed and melted resulting in pole fire. Cause of failure unknown. No evidence of ground fire
1150 | Ausnet 18/110 | Ausnet | 2019-10-02 | 43506.3201 | -37.7367 | 145.1723 | 1 KEARNEY LANE, TEMPLESTOWE VIC 3106 | 1207946 | ELM34 | 22kV AC | URBAN | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0009935 | 20190211SPN_02 | Candled EDO fuse and no evidence of ground fire. Suspect fault occurred during previous lightning storm. Replaced EDO tube and restored supply.
1151 | Ausnet 18/111 | Ausnet | 2019-11-02 | 43507.7153 | -37.3761 | 145.2762 | 2583 WHITTLESEA-YEA ROAD, FLOWERDALE VIC 3658 | 4707366 | SMR14 | 22kV AC | RURAL LONG | - overhead conductor (ABC) | three phase | Otherwise started by a distribution system | within electric line construction area | 19.8 | HIGH | 0.5 | 9.9 | E0010152 | 20190212SPN_01 | Cable insulation degradation due to age.
1152 | Ausnet 18/112 | Ausnet | 2019-12-02 | 43508.4653 | -37.7895 | 145.2831 | 3 SURREY ROAD W, CROYDON VIC 3136 | 1215701 | CPK21 | 22kV AC | URBAN | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | E0010178 | 20190213SPN_06 | Truck believed to have contacted O/H communications cable causing them to contact O/H HV conductors. Investigator found no evidence of fire or damage to Distribution assets
1153 | Ausnet 18/113 | Ausnet | 2019-12-02 | 43508.7688 | -36.8749 | 145.6136 | 1589 EUROA-MANSFIELD ROAD, GOORAM VIC 3666 | 3904896 | BN1 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | VERY HIGH | 1 | 4.6 | E0010281 | 20190213SPN_01 | Candling HV fuse
1154 | Ausnet 18/114 | Ausnet | 17/02/2019 | 43513.4549 | -38.297 | 146.1345 | 411 CHILDERS-THORPDALE ROAD, THORPDALE VIC 3835 | 2207436 | MOE32 | 22kV AC | RURAL SHORT | - overhead conductor (bare; steel) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0010807 | 20190218SPN_03 | Rusted 3/12 Steel conductor broke mid span at the steel sleeve between poles LIS2207435 and LIS2207436 resulting in a small ground fire. Only one conductor of the 3phase circuit broke. One dead cow found in the vacinity of the wood pole.
1155 | Ausnet 18/115 | Ausnet | 18/02/2019 | 43514.0708 | -36.4216 | 146.5801 | 379 DIFFEY ROAD, EVERTON VIC 3678 | 4508817 | WN5 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | VERY HIGH | 1 | 4.6 | E0010821 | 20190218SPN_02 | Candled HV fuse
1156 | Ausnet 18/116 | Ausnet | 18/02/2019 | 43514.5278 | -37.8854 | 145.4119 | 136 MOXHAMS ROAD, MONBULK VIC 3793 | 1304701 | BGE24 | 22kV AC | RURAL SHORT | - fuse (boric acid) | three phase | Otherwise started by a distribution system | within electric line construction area | 19.8 | HIGH | 0.5 | 9.9 | E0011130 | 20190220SPN_01 | Candling HV fuse. Fuse replaced and supply restored
1157 | Ausnet 18/117 | Ausnet | 18/02/2019 | 43514.7222 | -37.7989 | 145.2159 | 1 CANTALA CRESCENT, RINGWOOD NORTH VIC 3134 | 1210191 | RWN24 | 22kV AC | URBAN | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | E0011010 | 20190219SPN_01 | Possum contacted O/H HV conductors resulting in a small ground fire (0.5m sq) when it fell to ground
1158 | Ausnet 18/118 | Ausnet | 19/02/2019 | 43515.5771 | -37.9322 | 147.0972 | 17 STOCKDALE ROAD, STRATFORD VIC 3862 | 2511984 | MFA21 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0011088 | 20190219SPN_03 | Crew arrived onsite found 6k BA fuse had candled. No other damage and no evidence of fallen material at base of pole. Fuse replaced and supply restored
1159 | Ausnet 18/119 | Ausnet | 24/02/2019 | 43520.7562 | -37.6821 | 145.059 | 60 CARBEEN DRIVE, BUNDOORA VIC 3083 | 905808 | WT6 | 22kV AC | URBAN | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | E0011688 | 20190226SPN_01 | Bird has made contact with live 22kV on pole resulting in a small grass fire of approx 13 x 2 metres when it fell to ground.
1160 | Ausnet 18/120 | Ausnet | 25/02/2019 | 43521.8118 | -38.211 | 146.278 | 220 TWO MILE ROAD, HERNES OAK VIC 3825 | 2206528 | MOE31 | 66kV AC | RURAL LONG | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | VERY HIGH | 1 | 4.6 | E0011790 | 20190226SPN_02 | Semi-Mature Eucalyptus on embankment has failed 2m from ground level and fallen onto 66kv conductors on opposite side of road. White Rot present at site of tree failure, along with 2 x small Fungal Fruiting Bodies on back side of trunk. These would not have been indentified during inspection and, as such, tree was not identified as being hazardous
1161 | Ausnet 18/121 | Ausnet | 25/02/2019 | 43521.8403 | -37.6825 | 145.0118 | 1 SPRING STREET, THOMASTOWN VIC 3074 | 908031 | TT9 | Low voltage AC (<1kV) | RURAL LONG | - connector / termination | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | VERY HIGH | 1 | 0.2 | E0011792 | 20190226SPN_03 | Single phase pole type junction box failed causing hot molten plastic and aluminium to fall to ground igniting a 1.5 x 1 meter grass fire.
1162 | Ausnet 18/122 | Ausnet | 27/02/2019 | 43523.4132 | -38.2024 | 146.0678 | 1 NEAGLE STREET, YARRAGON VIC 3823 | 2202558 | MOE22 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0011955 | 20190227SPN_02 | Candled EDO fuse. No damage to pole and no evidence of ground fire
1163 | Ausnet 18/123 | Ausnet | 2019-01-03 | 43525.0722 | -37.6625 | 145.0458 | 194 CHILDS ROAD, MILL PARK VIC 3082 | 5813564 | EPG34 | Low voltage AC (<1kV) | URBAN | - luminaires (major road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | VERY HIGH | 1 | 0.2 | E0012290 | 20190304SPN_03 | Fault crew attended and found a 150W HPS street light head burnt out. No external fire damage and fault contained within light head. No evidence of ground fire
1164 | Ausnet 18/124 | Ausnet | 2019-01-03 | 43525.6521 | -37.7244 | 145.7644 | 7 WHITEGUM DRIVE, EAST WARBURTON VIC 3799 | 1408778 | WYK13 | 22kV AC | RURAL SHORT | - surge diverter | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | VERY HIGH | 1 | 4.6 | E0012559 | 20190304SPN_04 | During REFCL testing, WYK13 feeder CB tripped to lockout and a fire was reported and extinguished by CFA. A 22kV road side (white phase) lighting arrestor has failed during REFCL testing resulting in a small 2mx2m grass fire as debris fell to ground.
1165 | Ausnet 18/125 | Ausnet | 2019-01-03 | 43525.8826 | -37.6717 | 145.1497 | 22 COLLINS STREET, DIAMOND CREEK VIC 3089 | 926701 | ELM12 | Low voltage AC (<1kV) | URBAN | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | VERY HIGH | 1 | 0.2 | E0012577 | 20190304SPN_06 | A tree branch broke from a gumtree tree and, while falling to ground, clipped LV open wire mains causing LV white & blue phase conductors to clash. The resultant fault current caused a mains connection failure at the s/s LV white phase isolator with holt molten metal to falling to groundand starting a small 2m x 2.5m grass fire at the base of the pole.
1166 | Ausnet 18/126 | Ausnet | 2019-02-03 | 43526.3396 | -38.3521 | 146.4376 | 205 LINDNERS ROAD, JEERALANG JUNCTION VIC 3840 | 2616504 | MWT31 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | HBRA only | 1 | VERY HIGH | 1 | 1 | E0012584 | 20190304SPN_07 | Candled HV EDO fuse only and no evidence of ground fire
1167 | Ausnet 18/127 | Ausnet | 2019-03-03 | 43527.6875 | -37.647 | 145.0368 | 24 GREENBROOK DRIVE, EPPING VIC 3076 | 916606 | EPG34 | Low voltage AC (<1kV) | URBAN | - switch (disconnector/isolator) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | SEVERE | 2 | 0.4 | E0012682 | 20190304SPN_10 | An LV isolator and transformer lead failed on pole LIS916606 resulting in 2 small grass fires (approx 1m sq and 12m sq) as hot molten metal fell to ground.
1168 | Ausnet 18/128 | Ausnet | 2019-03-03 | 43527.7708 | -37.6665 | 145.1213 | 29 RIVER AVENUE, PLENTY VIC 3090 | 923074 | ELM15 | Low voltage AC (<1kV) | RURAL SHORT | - overhead conductor (ABC) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | SEVERE | 2 | 9.2 | E0012617 | 20190304SPN_08 | An ABC mains connection clamp failed due to high electrical demand causing ABC XLPE insulation to melt and drip on ground. The ABC overhead mains also broke and fell on ground. ABC repaired and supply restored
1169 | Ausnet 18/129 | Ausnet | 2019-03-03 | 43527.7708 | -37.6563 | 145.3694 | 2 ANZAC AVENUE, YARRA GLEN VIC 3775 | 1005807 | CPK12 | Low voltage AC (<1kV) | RURAL SHORT | - dropper / bridge | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | SEVERE | 2 | 0.4 | E0012619 | 20190304SPN_09 | A suspected transformer conductor lead failed due to high electrical demand resulting in a small ground fire (approx. 1m x 3m) as hot molten metal and plastic fell to ground. Repair works consisted of replacing with double transformer leads and substation split circuit fusing.
1170 | Ausnet 18/130 | Ausnet | 2019-04-03 | 43528.4868 | -37.769 | 145.3228 | 17 WAINEWRIGHT AVENUE, MOOROOLBARK VIC 3138 | 1012598 | CPK13 | 22kV AC | URBAN | - dropper / bridge | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | E0012763 | 20190304SPN_11 | A suspected centre phase HV dropper lead supplying a ground type substation failed at the pole resulting in a small ground fire as hot molten metal and debris fell to ground.
1171 | Ausnet 18/131 | Ausnet | 2019-05-03 | 43529.7868 | -37.4697 | 144.9236 | 800 OLD SYDNEY ROAD, BEVERIDGE VIC 3753 | 4718493 | KLO24 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | VERY HIGH | 1 | 4.6 | E0013105 | 20190307SPN_02 | Candled HV EDO fuse.
1172 | Ausnet 18/132 | Ausnet | 2019-06-03 | 43530.6458 | -38.2044 | 145.5636 | 25 SPENCERS ROAD, MONOMEITH VIC 3984 | 513165 | LLG11 | 22kV AC | RURAL SHORT | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0013286 | 20190308SPN_02 | Candled HV boric acid fuse. No evidence of ground fire
1173 | Ausnet 18/133 | Ausnet | 2019-06-03 | 43530.7715 | -38.2362 | 146.3955 | 163 PRINCES DRIVE, MORWELL VIC 3840 | 2618799 | MWT11 | 22kV AC | RURAL SHORT | - overhead conductor (covered uninsulated) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | E0013322 | 20190308SPN_03 | Cable fault has occured and cable has failed half way up the cable head resulting in pole fire. Cause of cable fault unknown. No evidence of ground fire.
1174 | Ausnet 18/134 | Ausnet | 2019-07-03 | 43531.5236 | -38.2264 | 145.5412 | 180 EDENS ROAD, CALDERMEADE VIC 3984 | 513552 | LLG11 | 22kV AC | RURAL SHORT | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0014035 | 20190326SPN_03 | Candled Boric Acid HV fuse identified. The fuse base appears to not have been installed correctly, connections were loose and no grease as per manufactures requirements. A technical bulletin is being prepared to highlight this issue and ensure this equipment is installed correctly.
1175 | Ausnet 18/135 | Ausnet | 2019-07-03 | 43531.6771 | -38.0563 | 145.4668 | 125 MULCAHY ROAD, PAKENHAM VIC 3810 | 501073 | OFR23 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | E0013571 | 20190308SPN_05 | Excavator made contact with 22kV Conductors between LIS501074 & LIS501073 which caused 2 fuses to operate and 1 fuse to candle. No further damage was found and no injuries sustained. Fuses were replace and supply to customers restored
1176 | Ausnet 18/136 | Ausnet | 2019-09-03 | 43533.7986 | -38.3076 | 146.5412 | 43 TRARALGON-BALOOK ROAD, TRARALGON SOUTH VIC 3844 | 2605225 | TGN23 | 22kV AC | RURAL SHORT | - overhead conductor (bare; copper) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | E0013787 | 20190312SPN_02 | Semi mature Eucalypt located on creek bank 4m from HV line, has had branch fail at union 10m from ground level and fall onto HV conductors. The union shows signs of minor decay which would not have been visible from a ground based assessment. Signs of fire in 2 areas - Midspan (2x5m), and around the pole & stay wire (2 x 10m). The remaining branch above the point of failure is leaning away from the line & not hazardous to AusNet assets. The span was last cleared on the 2nd of October 2018
1177 | Ausnet 18/137 | Ausnet | 2019-09-03 | 43533.8169 | -38.5582 | 145.8813 | 16 HUNTS ROAD, LEONGATHA SOUTH VIC 3953 | 2010501 | LGA23 | Low voltage AC (<1kV) | RURAL LONG | - connection box | single phase | Otherwise started by a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | E0013786 | 20190312SPN_01 | The fuse mains box on the pole appears to have melted resulting in 0.5m sq grassfire at base of the pole with melted plastic in the area around the burnt grass. Pole has surface burns and transformer is covered in black soot. Pole still alight when crew arrived. Supply isolated and CFA called. Pole was tested and deemed ok to remain, transformer was replaced with single phase 25kVA. New 95mm ABC leads were installed from the transformer to the new krone box. 35mm leads installed from Krone box to new FOLCB to reconnect the existing underground service (no impact to underground service)
1178 | Ausnet 18/138 | Ausnet | 2019-10-03 | 43534.1875 | -38.7987 | 146.2205 | 195 PATERSON ROAD, YANAKIE VIC 3960 | 2027889 | FTR22 | 22kV AC | RURAL SHORT | - overhead conductor (bare; steel) | single phase | Otherwise started by a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | E0013804 | 20190312SPN_03 | Conductor has detached from insulator at pole. 35-45km/h winds in the area. Conductor found hanging approx. 3m from ground height. Small vegetation in vicinity of conductor and scorch marks on vegetation and grass fire approx. 100mx2m long. CFA attended to put out grass fire. There were no signs of corrosion on the tie and it is believed high winds caused the tie to fatigue and fail. In order to restore supply, a new tie was installed however further assessment to be carried out to determine if vibration dampers and/or armour rods are to be installed in this location. No asset failure report available due to nature of incident.
1179 | Ausnet 18/139 | Ausnet | 2019-10-03 | 43534.2083 | -37.1053 | 146.1212 | 405 RIFLE BUTTS ROAD, MANSFIELD VIC 3722 | 3919053 | MSD1 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0013788 | 20190311SPN_01 | 6K BA fuse candling only and no evidence of ground fire
1180 | Ausnet 18/140 | Ausnet | 2019-11-03 | 43535.4604 | -37.9159 | 145.4423 | 36 MEADOWVIEW LANE, EMERALD VIC 3782 | 418996 | BGE22 | 22kV AC | RURAL SHORT | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0013830 | 20190318SPN_01 | Candled 6K BA fuse. No evidence of ground fire, Fault Truck Replaced fuse and restored supply.
1181 | Ausnet 18/141 | Ausnet | 2019-12-03 | 43536.8125 | -36.1439 | 146.8799 | 31 HUON CREEK ROAD, WODONGA VIC 3690 | 5202909 | WOTS25 | 22kV AC | RURAL SHORT | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | E0018410 | 20190403SPN_04 | A council owned poplar tree in a declared area (council responsibility) suffered total root plate failure and has brought multiple spans of conductor to the ground.
1182 | Ausnet 18/142 | Ausnet | 15/03/2019 | 43539.8333 | -36.558 | 145.9794 | 18 MAUD STREET, BENALLA VIC 3672 | 3902405 | BN4 | Low voltage AC (<1kV) | URBAN | - overhead conductor (bare; copper) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | E0015015 | 20190318SPN_03 | Tree branch in Taungurong Park Reserve fell on LV conductor.
1183 | Ausnet 18/143 | Ausnet | 15/03/2019 | 43539.8361 | -38.0623 | 145.6754 | 147 GARFIELD NORTH ROAD, GARFIELD NORTH VIC 3814 | 510683 | WGL12 | 12.7kV AC (SWER) | RURAL LONG | - transformer (pole mounted) | single wire earth return (SWER) | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | E0015009 | 20190319SPN_05 | Candling HV fuse and resulting in 50 sq m ground fire. Spoke to Customer /land owner had observed a bird come into contact with overhead structure and burst into flames. Also Observed tree branches and vegetation piled up close to ISO had been burnt as result of the ember hitting the ground.
1184 | Ausnet 18/144 | Ausnet | 17/03/2019 | 43541.3125 | -37.6247 | 145.4096 | 1691 MELBA HIGHWAY, DIXONS CREEK VIC 3775 | 1007398 | LDL14 | Low voltage AC (<1kV) | RURAL SHORT | - dropper / bridge | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0015034 | 20190325SPN_01 | The fire appears to have been caused by worn exposed non-covered LV leads from the LV bushings of the s/stn to the LV fuses. Cause of failire unknown. LV leads were replaced and a new LV Krone/Isolator box installed.
1185 | Ausnet 18/145 | Ausnet | 17/03/2019 | 43541.7847 | -37.8568 | 145.2262 | 64 AMERSHAM DRIVE, WANTIRNA VIC 3152 | 1031581 | BRA21 | Low voltage AC (<1kV) | URBAN | - LV pillar | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | E0015065 | 20190319SPN_07 | Unknown vehicle reported to have lost control and hit paralleling pillar outside 64 Amersham Drive, Wantirna resulting in a small grass fire of less than 0.25sqm.
1186 | Ausnet 18/146 | Ausnet | 19/03/2019 | 43543.8542 | -36.1561 | 148.0071 | 150 TOWONG HILL ROAD, TOWONG VIC 3707 | 5216213 | WOTS24 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0015832 | 20190320SPN_02 | 6A EDO fuse candled. Fuse replaced
1187 | Ausnet 18/147 | Ausnet | 20/03/2019 | 43544.7778 | -37.3739 | 145.0176 | 120 ARKELLS LANE, WANDONG VIC 3758 | 4700817 | KMS12 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0016019 | 20190321SPN_01 | Lightning storm identified in the area suspected to have caused fuse operation and subsequent candling. No evidence of ground fire
1188 | Ausnet 18/148 | Ausnet | 22/03/2019 | 43546.3125 | -36.4686 | 147.0151 | BELTANA, 4348 KIEWA VALLEY HIGHWAY, DEDERANG VIC 3691 | 5200750 | WOTS11 | 22kV AC | RURAL LONG | - fuse (boric acid) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0016423 | 20190325SPN_05 | Fault crew attended site following a storm and found 2 fuses had successfully operated but the 3rd had hung-up and candled.
1189 | Ausnet 18/149 | Ausnet | 22/03/2019 | 43546.3965 | -36.1237 | 146.9856 | MCINTOSHS ROAD, BONEGILLA VIC 3691 | 5235758 | WOTS-HPS | 66kV AC | N/A | - insulators | three phase | Started by lightning striking a distribution system or a part of a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0016292 | 20190327SPN_01 | 66KV pole on WOTS-HPS line struck by lightning
1190 | Ausnet 18/150 | Ausnet | 22/03/2019 | 43546.534 | -36.457 | 147.2923 | 283 MITTA NORTH ROAD, ESKDALE VIC 3701 | 5210351 | WOTS13 | 22kV AC | RURAL LONG | - insulators | single phase | Started by lightning striking a distribution system or a part of a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0016441 | 20190325SPN_04 | Burnt HV bushing cover on pole type transformer after lightning strike. A storm had passed through the area prior to the crews arrival. Lots of Lightning in the area. No fuses down on substation and customer still on supply. Follow up raised to replace the bushing covers and check the transformer.
1191 | Ausnet 18/151 | Ausnet | 25/03/2019 | 43549.6278 | -37.7658 | 145.4304 | 2 MAURICE ROAD, GRUYERE VIC 3139 | 1002272 | LDL23 | 22kV AC | RURAL LONG | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | VERY HIGH | 1 | 4.6 | E0016756 | 20190326SPN_02 | Total of 4 separate fires reported in the vicinity totalling an estimated 12,000 square metres but geographically disjointed. 2 x fires on property (2 Maurice Rd, Gruyere) and road reserve between LIS1002272 and LIS1002273 following a tree branch making contact with, and bringing down HV conductor at LIS1002273 2 x fires on property (2 Maurice Rd, Gruyere and road reserve) along Victoria Rd between LIS1013967 and LIS1002271 and LIS1013967 to LIS101396 when hanging centre phase 22kV dropper cable made contact with the outer phase at the tee-off pole. The tree in question was located in roadside reserve on the opposite side of the road to the powerline and approximately 15m from the nearest conductors. The fault was caused by the failure of a large leader due to the presence of decay on the upper side of the union (not detectable from ground level). A number of other hazard trees were identified in the vicinity and have been scheduled for cutting. The span was last inspected on the 27/04/2018 and was last cleared on the 16/07/2018.
1192 | Ausnet 18/152 | Ausnet | 27/03/2019 | 43551.3958 | -36.4262 | 147.0368 | 3613 KIEWA VALLEY HIGHWAY, KERGUNYAH SOUTH VIC 3691 | 5200685 | WOTS11 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0017229 | 20190327SPN_02 | EDO fuse failed to operate
1193 | Ausnet 18/153 | Ausnet | 27/03/2019 | 43551.4028 | -37.6408 | 145.0289 | 17 PARK STREET, EPPING VIC 3076 | 5645332 | EPG32 | 22kV AC | RURAL SHORT | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0017237 | 20190401SPN_01 | Crow contacted O/H HV conductors at pole causing phase to ground fault which resulted in a small ground fire approx. 2m x 1m
1194 | Ausnet 18/154 | Ausnet | 29/03/2019 | 43553.4243 | -37.7169 | 145.0809 | 7 WATTLE DRIVE, WATSONIA VIC 3087 | 906803 | WT9 | 22kV AC | URBAN | - crossarm (wood) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | VERY HIGH | 1 | 0.2 | E0018047 | 20190403SPN_02 | Old brown pin type fog insulator has failed resulting in tracking causing the cross arm to burn and fail
1195 | Ausnet 18/155 | Ausnet | 29/03/2019 | 43553.9979 | -38.1895 | 146.5557 | 27 STRATHCOLE DRIVE, TRARALGON VIC 3844 | 2613976 | LLG12 | 22kV AC | RURAL SHORT | - crossarm (wood) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | VERY HIGH | 1 | 0.2 | E0018046 | 20190403SPN_01 | Light rain in the area at the time of the incident resulting in possible tracking causing the wooden HV x-arm to smoulder around where x-arm brace attached to the x-arm. There was no damage to the HV conductors. Wood HV crossarm replaced with steel
1196 | Ausnet 18/156 | Ausnet | 31/03/2019 | 43555.8958 | -37.8046 | 145.2726 | 47 BAYSWATER ROAD, CROYDON VIC 3136 | 5736585 | CYN32 | 22kV AC | URBAN | - fuse (boric acid) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0018113 | 20190403SPN_03 | A bird appears to have come in contact with O/H HV assets on s/stn pole resulting in a candled fuse. Burnt bird found at base of pole but no evidence to ground fire.
1197 | Ausnet 18/157 | Ausnet | 2019-05-04 | 43560.4583 | -37.5145 | 145.3161 | 339 WHITTLESEA-KINGLAKE ROAD, KINGLAKE CENTRAL VIC 3757 | 929986 | KLK21 | Low voltage AC (<1kV) | RURAL SHORT | - rapid earth fault current limiter (REFCL) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | VERY HIGH | 1 | 4.6 | E0018514 | 20190410SPN_01 | Red Phase calibration was carried out with no issues. White phase calibration was then carried out and completed successfully, however a loud bang was heard at its conclusion. Sparks and burning was observed on the top part of the inverter. Upon investigation, the top right hand side fan compartment was on fire and the braking resistor within it badly burnt. The breaking resistors are used to absorb excess energy produced by the inverter during REFCL calibration operation. In this case, a faulty breaking resistor failed and caught fire due to the excessive heat that was generarted as a result of breaking the resistor loop. The breaking resistor was destroyed by the incident. No injuries to personnel were sustained. Following the incident, the inverter was isolated, the covers removed and the unit inspected. It was noted that some molten metal may have dripped through the inverter cabinet and, due to possible contamination from molten metal, the entire inverter cabinet was replaced. The manufacturer of the equipment (Swedish Neutral) has been contacted and engaged to assist with the investigation and the equipment panel has been made availabe to Swedish Neutral to confirm there are no other issues and confirm there is no secondary damage caused by the fault. No human or procedural factors were identified and Swedish Neutral believe this is nothing more than a component failure and have confirmed they are comfortable for all other units to go into service.
1198 | Ausnet 18/158 | Ausnet | 2019-05-04 | 43560.8229 | -37.8469 | 145.4744 | 25 ELEANOR DRIVE, SILVAN VIC 3795 | 1013469 | LDL13 | 22kV AC | RURAL SHORT | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | VERY HIGH | 1 | 4.6 | E0018526 | 20190408SPN_01 | Fault crew attended and found candled 6K BA fuse on the footpath side. No Evidence of ground fire Fuse replaced and supply restored
1199 | Ausnet 18/159 | Ausnet | 2019-12-04 | 43567.4688 | -38.5066 | 145.2839 | 2 DIXON STREET, SURF BEACH VIC 3922 | 2809076 | PHI11 | Low voltage AC (<1kV) | RURAL SHORT | - connector / termination | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | E0018698 | 20190416SPN_02 | Krone box has failed on the pole resulting in small ground fire (1mx1m) at base of the pole. Cause of failure unknown
1200 | Ausnet 18/160 | Ausnet | 13/04/2019 | 43568.8611 | -38.6442 | 146.6719 | 317 YARRAM-PORT ALBERT ROAD, LANGSBOROUGH VIC 3971 | 2608590 | FTR23 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0018722 | 20190416SPN_03 | Candled BA HV fuse. No evidence of ground fire
1201 | Ausnet 18/161 | Ausnet | 15/04/2019 | 43570.6861 | -38.5189 | 146.1199 | 195 DOLLAR ROAD, DUMBALK VIC 3956 | 2005307 | LGA13 | 22kV AC | RURAL LONG | - switch (FuseSaver) | three phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0018804 | 20190416SPN_04 | Customer heard a loud noise in his paddock when he lost power to his house and noticed a small grass fire (1m x 2m). Customer proceeded to extinguish the fire and no emergency services attended. The fire was approx 8 meters west of pole 2005307 and no damage was visible to AusNet assets. Investigation conducted but inconclusive, unable to determine exact cause of protection operation and subsequent fire. There was no bird/animal or vegetation present to provide any indication of how the fire may have started. However, the grass fire is consistent with similar bird/animal faults that have occurred in the past.
1202 | Ausnet 18/162 | Ausnet | 16/04/2019 | 43571.8819 | -37.668 | 145.1893 | 6 VALLEY ROAD, WATTLE GLEN VIC 3096 | 921018 | ELM15 | 22kV AC | RURAL SHORT | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | VERY HIGH | 1 | 4.6 | E0018853 | 20190417SPN_01 | Candled 6k Boric Acid HV fuse. No evidence of ground fire
1203 | Ausnet 18/163 | Ausnet | 18/04/2019 | 43573.4361 | -38.2766 | 145.5695 | 30 WATTLE COURT, LANG LANG VIC 3984 | 514134 | LLG12 | 22kV AC | RURAL SHORT | - fuse (boric acid) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0018927 | 20190418SPN_02 | Candled BA HV fuse. No evidence of ground fire
1204 | Ausnet 18/164 | Ausnet | 19/04/2019 | 43574.7486 | -37.8192 | 145.4203 | 87 QUEENS ROAD, SILVAN VIC 3795 | 1010930 | LDL23 | 22kV AC | RURAL LONG | - fuse (boric acid) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | E0019078 | 20190429SPN_03 | HV BA fuse appears to have hung-up and then candled. No evidence of ground fire
1205 | Ausnet 18/165 | Ausnet | 20/04/2019 | 43575.7104 | -38.1568 | 146.3849 | 55 QUARRY ROAD, YALLOURN NORTH VIC 3825 | 2216241 | MOE14 | 22kV AC | RURAL SHORT | - fuse (any other type) | single phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0018955 | 20190422SPN_05 | Bird has built nest on transformer which has caught fire resulting in a small ground fire. No asset damage identified other than melted bushing cover, burnt dropper at the bushing and flash marks on the transformer/pole. Follow up visit organised to fit appropriate animal proofing to prevent future occurrence.
1206 | Ausnet 18/166 | Ausnet | 21/04/2019 | 43576.8125 | -37.8808 | 145.2718 | 781 BURWOOD HIGHWAY, FERNTREE GULLY VIC 3156 | 1312340 | BRA33 | Low voltage AC (<1kV) | URBAN | - luminaires (major road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | E0018959 | 20190422SPN_01 | Fault crew dispatched and found street light lantern had failed and burnt out. Cause of failure unkown at this time. Area immediately surrounding the PE cell holder was burnt and PE Cell fragments were found on ground but no evidence of ground fire. Lantern replaced and failed lantern returned to depot.
1207 | Ausnet 18/167 | Ausnet | 24/04/2019 | 43579.5 | -38.2203 | 145.3158 | 470 WARNEET ROAD, WARNEET VIC 3980 | 517465 | CRE33 | 22kV AC | RURAL SHORT | - fuse (boric acid) | three phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | E0019046 | 20190426SPN_01 | Candled 6k Boric Acid HV fuse
1208 | Ausnet 18/168 | Ausnet | 2019-01-05 | 43586.2632 | -36.0953 | 146.6571 | 331 Soldiers Rd Barnawartha VIC 3688 | 5235940 | BWA22 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0019184 | 20190501SPN_03 | BA HV fuse has candled
1209 | Ausnet 18/169 | Ausnet | 17/05/2019 | 43602.8403 | -36.5603 | 145.9973 | 15 RIVER GUM AVENUE, BENALLA VIC 3672 | 3920472 | BN6 | Low voltage AC (<1kV) | RURAL LONG | - fuse (any other type) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0020177 | 20190520SPN_01 | rats nest inside the LV side of the kiosk substation cause LV fuses to melt.
1210 | Ausnet 18/170 | Ausnet | 22/05/2019 | 43607.7722 | -36.7182 | 145.6497 | 146 MCKERNANS ROAD, BALMATTUM VIC 3666 | 3901372 | BN1 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | E0020336 | 20190524SPN_01 | Burnt fuse tube hung-up during storm event resulting in EDO HV fuse candling. No evidence of ground fire
1211 | Ausnet 18/171 | Ausnet | 31/05/2019 | 43616.9944 | -37.9117 | 145.2462 | 96 KELLETTS ROAD, ROWVILLE VIC 3178 | 5806314 | FGY31 | Low voltage AC (<1kV) | URBAN | - luminaires (major road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | E0020843 | 20190605SPN_01 | Street light found burnt but fire had been extinguished prior to fault crew arrival. Supply isolated and disconnect at pit and P/L luminaire replaced. No evidence of ground fire. Investigation conducted but inconclusive, suspected internal fault but unable to ascertain exact cause of luminaire failure which lead to fire.
1212 | Ausnet 18/172 | Ausnet | 2019-04-06 | 43620.7132 | -37.8784 | 147.9582 | 21 KALIMNA JETTY ROAD, KALIMNA VIC 3909 | 1901592 | BDL6 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | NO FORECAST | 0.1 | 0.46 | E0021472 | 20190618SPN_02 | Candled EDO HV Fuse. No evidence of ground fire
1213 | Ausnet 18/173 | Ausnet | 2019-05-06 | 43621.7292 | -37.812 | 147.6286 | 46 HOWITT AVENUE, EASTWOOD VIC 3875 | 5655908 | BDL42 | Low voltage AC (<1kV) | RURAL SHORT | - luminaires (major road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | E0020983 | 20190606SPN_01 | Street light appears to have failed internally resulting in it burning. Investigation carried out but inconclusive, unable to determine cause of failure.
1214 | Ausnet 18/174 | Ausnet | 13/06/2019 | 43629.4875 | -37.8611 | 145.6391 | 540 MT BEENAK ROAD, THREE BRIDGES VIC 3797 | 2601656341 | WYK23 | 22kV AC | RURAL SHORT | - fuse (boric acid) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | NO FORECAST | 0.1 | 0.46 | E0021377 | 20190618SPN_01 | Candled BA HV Fuse. No evidence of ground fire
1215 | Ausnet 18/175 | Ausnet | 18/06/2019 | 43634.7361 | -37.3232 | 144.9422 | 118 GEHREYS LANE, KILMORE VIC 3764 | 4716905 | KMS12 | Low voltage AC (<1kV) | RURAL SHORT | - switch (disconnector/isolator) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | NO FORECAST | 0.1 | 0.46 | E0021521 | 20190619SPN_01 | burnt out transformer lv isolators
1216 | Ausnet 18/176 | Ausnet | 25/06/2019 | 43641.4264 | -38.4562 | 145.7006 | 1 TWITES ROAD, BENA VIC 3946 | 2008545 | LGA23 | Low voltage AC (<1kV) | RURAL LONG | - connection box | single phase | Otherwise started by a distribution system | HBRA only | 1 | NO FORECAST | 0.1 | 0.1 | E0021840 | 20190626SPN_01 | Fault crew attended and found LV fuse box had failed and melted. LV U/G cable had also suffered damage at the fuse box. Suspected bad connections at the LV Fuse box which resulted in fire.
1217 | Ausnet 18/177 | Ausnet | 27/06/2019 | 43643.4062 | -36.3189 | 146.8421 | 6 BACK CREEK ROAD, YACKANDANDAH VIC 3749 | 5218276 | WOTS11 | 22kV AC | RURAL LONG | - fuse (boric acid) | three phase | Otherwise started by a distribution system | within electric line construction area | 19.8 | NO FORECAST | 0.1 | 1.98 | E0021950 | 20190704SPN_01 | Candled Boric Acid HV fuse
1218 | Ausnet 18/178 | Ausnet | 30/06/2019 | 43646.5826 | -37.7884 | 147.5687 | 335 HODGES ESTATE ROAD, ELLASWOOD VIC 3875 | 1605515 | BDL44 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | NO FORECAST | 0.1 | 0.46 | E0022092 | 20190708SPN_07 | Boric Acid HV fuse candled. No evidence of ground fire
1219 | United 17/18 | United | 2017-05-07 | 0.73542 | -38.2534 | 145.0309 | 31 CLARKES AVENUE MOUNT MARTHA | 1102020 | MTN31 | Low voltage AC (<1kV) | Urban | - connection box | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5261 | 20170724UTD_02 | Fault crew arrived on site and found JB caught fire and damaged LV ABC Service connections - and 2 x bays of LV ABC @ lis 1102020
1220 | United 17/19 | United | 2017-06-07 | 0.20698 | -38.1765 | 145.0808 | 19 ROSSERDALE CRESCENT MOUNT ELIZA | 3313863 | FSH33 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5277 | 20170809UTD_01 | Fire brigade advised pole # L is 3313863 - LV FMB connection on fire. Crew repl a b/out 3 ph fmb aup the pole end.
1221 | United 17/20 | United | 2017-08-07 | 0.73502 | -38.3313 | 144.7145 | 298 HOTHAM ROAD PORTSEA | 1307139 | STO13 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5278 | 20170809UTD_02 | Cnr franklin & Hotham, lis # 1307139 replaced 3ph FMB and also replaced neutral LV pin and insulator, did ignite LV xarm but is ok, Fire Report # 02284
1222 | United 17/21 | United | 2017-11-08 | 0.13333 | -37.9243 | 145.0439 | 29B LONDON STREET BENTLEIGH | 1802621 | BT 04 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5281 | 20170811UTD_02 | sparking pole, cause possum as per MFB, - fire report completed out by crew- fire @ pole lis # 1802621 and crew reported when plastic came down caused approx 6 inch diameter circle burnt mark on the grass
1223 | United 17/22 | United | 19/08/2017 | 0.47626 | -38.0628 | 145.1179 | 16 WILLIAMS GROVE BONBEACH | 3303133 | CRM22 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5305 | 20170912UTD_01 | Replaced burnt out 3phs pole box at LIS #3303133 - due to birds nest inside - supply feeding unit 1 and 2 /#13
1224 | United 17/23 | United | 21/08/2017 | 0.89414 | -37.8729 | 145.2054 | 229 BALACLAVA ROAD, CAULFIELD NORTH VIC 3161 | 2334727 | EL 09 | Low voltage AC (<1kV) | Urban | - luminaries (major road) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5287 | 20170831UTD_01 | Disconnected 250w HP sodium PE street light head on LIS # 2334727 PWC Pole closest UE Pole 2301427 - head had been on fire but was extinguished by MFB - caused by birds nest
1225 | United 17/24 | United | 24/08/2017 | 0.25535 | -38.0237 | 145.1925 | 80 ORDISH ROAD DANDENONG SOUTH | 3425946 | DSH33 | 22kV AC | Urban | - transformer (pole mounted) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5306 | 20170912UTD_02 | Removed large bird nest from top of tx. cleaned HV transformer bushings. Installed new centre phs bushing covers. LIS# 3425946.
1226 | United 17/25 | United | 31/08/2017 | 0.81225 | -37.8506 | 145.1018 | 114 BURWOOD HIGHWAY BURWOOD | 7050090 | BW 22 | 11kV AC | Urban | - capacity balancing units | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5302 | 20170908UTD_01 | LIS 7050090, CAP BURWOOD-MILICENT has blown up, follow up required Fri 1/9 to have cap bank replaced. Crew to advised depot.
1227 | United 17/26 | United | 28/09/2017 | 0.56752 | -38.3547 | 144.7596 | 8 TADJI STREET SORRENTO | 1306299 | STO13 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5314 | 20171003UTD_03 | Fire Start @ lis # 1306299 LV ABC Inter Pole with a 3 phase junction box located @ 6 Tadji St Sorrento Junction Box melted and caused a fire on top of the pole - debris on ground but no grass fire was involved
1228 | United 17/27 | United | 2017-01-10 | 0.8161 | -37.8806 | 144.987 | 130 MITFORD STREET ELWOOD | 2332245 | EW 01 | Low voltage AC (<1kV) | Urban | - fuse (any other type) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5318 | 20171012UTD_02 | replaced 100a fuse box, burnt out. And 100 a fuse. Tested and left on, CIA LIS# 2332245
1229 | United 17/28 | United | 2017-05-10 | 0.44647 | -38.2238 | 145.2496 | 1 SOUTH BOUNDARY ROAD SOMERVILLE | 9498509 | HGS33 | 22kV AC | Rural Short | - guy wire | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 5317 | 20171012UTD_01 | Appears Guy rod pulled out of log and guy wire contacted LA at MEALY STH BOUNDARY S/S LIS#9498509. Confirmed pole fire & CFA called. Fire Report # 04448 emailed photos to NCC
1230 | United 17/29 | United | 2017-06-10 | 0.18485 | -38.1709 | 145.1058 | 22 HUMPHRIES ROAD MOUNT ELIZA | 3314196 | FSH13 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5330 | 20171103UTD_01 | Cons crew on the way to replace burnt hv x-arm...poly/plastic insulators, LIS - 3314196 HV strain arm replaced cut off top of pole, chse up with James Q & Rod L for fire start report.
1231 | United 17/30 | United | 19/10/2017 | 0.11758 | -37.9771 | 145.0666 | 56 NEPEAN HIGHWAY, MENTONE | 1822129 | M 23 | 11kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5322 | 20171012UTD_02 | HV O/Head Wph down onto LV X-Arm Corner of Nepean Hwy and Flinders St. Maybe a HV sleeve has failed and let go. Sparks from cond started small fire in garden bed at BP petrol station, Fire Start report - 00344.
1232 | United 17/31 | United | 19/10/2017 | 0.45918 | -38.0379 | 145.199 | 97-105 BANGHOLME ROAD, BANGHOLME | 623176 | DVY34 | 22kV AC | Urban | - fuse (boric acid) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5323 | 20171012UTD_03 | Fuse candled. white phase on Cap BANGHOLME HAMMOND. Vaccum switch damaged. Cap BANGHOLME HAMMOND isolated . LIS#3441333. fire ignition report # 00199 - no fire on grass
1233 | United 17/32 | United | 2017-07-11 | 0.46133 | -37.8992 | 145.1724 | 28 COOPER AVENUE GLEN WAVERLEY | 608953 | MGE34 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5333 | 20171108UTD_01 | hv/lv #1258 strain pole needs to be replaced ZNX Duty Officer Peter Marsh advd. W.Highmore doing fire report fire report No3007
1234 | United 17/33 | United | 2017-07-11 | 0.50764 | -37.9018 | 145.1746 | 26 ENTALLY DRIVE WHEELERS HILL | 607733 | MGE34 | 22kV AC | Urban | - fuse (powder filled) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5334 | 20171108UTD_02 | Whisper sent for fire start, candling fuse. replaced 15 B ph PFF at lis 0607733 no cause identified at sub. no wires down as reported by mfb. fire report No3008 per W Highmore
1235 | United 17/34 | United | 23/11/2017 | 0.11706 | -37.8186 | 145.1148 | 434 ELGAR ROAD BOX HILL | 7024750 | BH 23 | 22kV AC | Urban | - underground cable | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5351 | 20171204UTD_03 | HVUG fault from lis 7024750 cnr Elgar & Hopetoun Pde HV Blue phase on the deck in Kent st lis..7037195. Fire report#3870. Possibly the fault current for cause of wire down.
1236 | United 17/35 | United | 24/11/2017 | 0.28718 | -38.3684 | 144.8717 | 2 BROADWAY CAPEL SOUND | 1300184 | RBD23 | 22kV AC | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5353 | 20171206UTD_01 | Copper to Al Ampact connection failed at LIS#1300184 strain pole Elizabeth cnr of Broadway, the preform connection at same location has failed and this let the HV conductor fall. ...HV conductor fell alive onto ground, MFB reported flames 1-2 metres high from the failing ampact connection prior to hv conductor falling to ground.
1237 | United 17/36 | United | 2017-02-12 | 0.97644 | -37.8985 | 144.995 | 60 NORTH ROAD BRIGHTON | 2304847 | NB 22 | 11kV AC | Urban | - crossarm (wood) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5358 | 20171211UTD_02 | Truck hit pole and broke HV Tie which fell onto crossarm causing a fire - LIS 2304847
1238 | United 17/37 | United | 2017-06-12 | 0.53068 | -37.9368 | 145.0027 | 452A HAMPTON STREET HAMPTON | 1818498 | SR 23 | Low voltage AC (<1kV) | Urban | - luminaries (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5389 | 20180109UTD_03 | HPS 250 Watt Lantern had burnt out - Lis 1818498
1239 | United 17/38 | United | 2017-11-12 | 0.38403 | -37.9079 | 145.1606 | 594 SPRINGVALE ROAD, WHEELERS HILL | 8805524 | MGE21 | Low voltage AC (<1kV) | Urban | - luminaries (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5390 | 20180109UTD_04 | HPS 250 Watt Lantern had burnt out - Lis 8805524
1240 | United 17/39 | United | 13/12/2017 | 0.74678 | -38.0312 | 145.1043 | 188 NEPEAN HIGHWAY ASPENDALE | 3302395 | MC 01 | Low voltage AC (<1kV) | Urban | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5369 | 20171218UTD_04 | During hot conditions a LV Krone box failed and caught fire - LIS 3302395
1241 | United 17/40 | United | 14/12/2017 | 0.94058 | -37.9099 | 145.1021 | 8B RAILWAY AV OAKLEIGH | 2325346 | OE 04 | 11kV AC | Urban | - connector / termination | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5373 | 20171215UTD_01 | Fire start adjacent to "Railway P1 West- Warner" S/Stn. The Red phase P/F Fuse unit failed on the top contact of clamp and fuse fell to the ground igniting a small 3Sq/m grass fire - LIS 2325346
1242 | United 17/41 | United | 17/12/2017 | 0.87381 | -38.183 | 145.0757 | 14 KOORNALLA CRESCENT MOUNT ELIZA | 3314469 | MTN22 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5387 | 20180109UTD_01 | Although fire was out when crew arrived the first call comments state flames were visable from a 3 phase FMB - Lis 3314469
1243 | United 17/42 | United | 20/12/2017 | 0.94125 | -37.9592 | 145.1786 | 44 CALLANDER ROAD NOBLE PARK | 633975 | NP 16 | 22kV AC | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5386 | 20180108UTD_04 | Capbank CALLANDER JASON LLC flex at top of fuse unit is failing, causing arcing, no fire at the time of linsmans arrival however 1st call comments idicate flames were witnessed. LIS 0633975
1244 | United 17/43 | United | 22/12/2017 | 0.18138 | -38.3489 | 144.9429 | 13 BAYVIEW ROAD MCCRAE | 8825718 | RBD13 | Low voltage AC (<1kV) | Urban | - luminaries (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5375 | 20171222UTD_01 | a 150W Lantern on pole lis-8825718 Ccaught fire in Bayview Rd, McCrae
1245 | United 17/44 | United | 29/12/2017 | 0.8462 | -38.0108 | 145.2214 | 78-80 WILLIAMS ROAD, DANDENONG SOUTH | 9575750 | DSH22 | Low voltage AC (<1kV) | Urban | - LV pillar | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5379 | 20180102UTD_01 | An LV Distribution cabinet caught fire outside 78 Williams Rd, Dandenong - Closest LIS # 9575750
1246 | United 17/45 | United | 2018-04-01 | 0.015856 | -37.9655 | 145.1737 | 6 DOUGLAS STREET NOBLE PARK | 9821648 | NP 25 | Low voltage AC (<1kV) | Urban | - luminaries (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5381 | 20180104UTD_01 | Pole No. 9821648 s/l head melted & wiring was burnt - has been isolated in the pit - crew to return thursday night to repair. light repaired, rewired & head replaced
1247 | United 17/46 | United | 2018-05-01 | 0.70385 | -37.9528 | 145.1536 | 3 UNION GROVE SPRINGVALE | 613560 | SS 13 | Low voltage AC (<1kV) | Urban | - overhead service conductor (residential) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5383 | 20180108UTD_01 | on at 1900 repl a 2 core service n/screen b/out at clamp. Started small fire in front yard to number 3. LIS # 13560 fire ignition report # 02524. Whispir sent
1248 | United 17/47 | United | 2018-07-01 | 0.85478 | -38.0364 | 145.1062 | 2A-2B DUDLEY GROVE, EDITHVALE | 3302798 | MC 01 | Low voltage AC (<1kV) | Urban | - connection box | two phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5385 | 20180108UTD_03 | two phase fmb box on the pole had b/out and on fire. some grass (small) fire. It fed an u/ground service which fed 2a and 2 b Denman. crew replaced box. NST and on supply. Fire ignition report num is 00349. Whispir sent
1249 | United 17/48 | United | 2018-08-01 | 0.50957 | -37.9088 | 145.0612 | 325 EAST BOUNDARY ROAD BENTLEIGH EAST | 2333019 | OR 24 | 66kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5391 | 20180109UTD_05 | Tree is near 66 HTN to NB line. council tree dropped brach which caught fire is clear now but needs to be cut back ideally this week, shut down will be required, LIS - 2333019
1250 | United 17/49 | United | 2018-12-01 | 0.16567 | -38.3869 | 144.9313 | 69 CARRATHOOL AVENUE ROSEBUD | 1311457 | RBD12 | 22kV AC | Rural Short | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5396 | 20180112UTD_04 | EDO fuse tube candled, replaced 10a fuse and tube on the white phase, ncf. fire report #6623
1251 | United 17/50 | United | 18/01/2018 | 0.018692 | -37.9102 | 145.0919 | 1177 NORTH ROAD OAKLEIGH | 2326221 | OE 04 | 11kV AC | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 5403 | 20180122UTD_02 | An cu/al ampact connection failure resulting in the 11kV conductor falling to the ground and thus scorching the grass underneath
1252 | United 17/51 | United | 18/01/2018 | 0.73302 | -37.9695 | 145.1863 | 74 CHANDLER ROAD NOBLE PARK | 619054 | NP 36 | Low voltage AC (<1kV) | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 5400 | 20180122UTD_01 | LIS - 0619054 crew replcd burnt off red phase lv lead conn to tx lv isolator completed fire ignition report - grass had been burnt approx 1 cubic meter crew have taken photos of grass and pole to be passed onto chris willey
1253 | United 17/52 | United | 18/01/2018 | 0.76686 | -38.2417 | 145.0473 | 253 DUNNS ROAD MORNINGTON | 1100188 | MTN31 | Low voltage AC (<1kV) | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 5401 | 20180122UTD_03 | burnt out connection at sub IKARA DUNNS blue phs, remade connection. LIS#1100188 - base of pole had burn marks Fire report 02285 Cause unknown, grass fire 4x2 mtrs.
1254 | United 17/53 | United | 19/01/2018 | 0.62265 | -37.8238 | 145.1574 | 45 WELLINGTON AVENUE BLACKBURN | 7037553 | NW 21 | 22kV AC | Urban | - overhead conductor (bare; copper) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 5404 | 20180122UTD_04 | Original Fault was private tree branch across w/b HV phases at #6 Lake Rd north east of LIS#7029960. This causes many secondary faults, onne of which resulted in HV clashing which ignited a small grass fire
1255 | United 17/54 | United | 22/01/2018 | 0.64387 | -38.0095 | 145.2161 | 90A DANDENONG-FRANKSTON RD DANDENONG SOUTH | 635472 | DSH32 | Low voltage AC (<1kV) | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5405 | 20180123UTD_01 | W phase lv had clashed with the electrolis cable - crew installed some stinger insualtion onto the conductors & filled out fire report# 05629 less than 1 square meter of grass burnt.
1256 | United 17/55 | United | 22/01/2018 | 0.73284 | -37.9093 | 145.1958 | 13 PALMERSTON CRESCENT WHEELERS HILL | 8808475 | MGE12 | Low voltage AC (<1kV) | Urban | - LV pillar | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5406 | 20180123UTD_02 | Refer to t/o: 1140334 - u/g pillar @14 Palmerston St blew up - fire report #: 1140338 - (fire burnt customers knee high plant to the ground - u/g crew on site replacing pillar -
1257 | United 17/56 | United | 25/01/2018 | 0.5305 | -37.7809 | 145.1234 | 71 WILLIAMSONS ROAD DONCASTER | 7055546 | WD 15 | 11kV AC | Urban | - capacity balancing units | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5421 | 20180205UTD_01 | Isolated a damaged capacitor bank as per the control room. The Cap Back flashed over and caused a small fire up the pole that self extinguished
1258 | United 17/57 | United | 25/01/2018 | 0.75016 | -37.9945 | 145.208 | 13 DALGETY STREET DANDENONG | 8813035 | KBH32 | 22kV AC | Urban | - transformer (pole mounted) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5410 | 20180129UTD_01 | Transformer blown up and fire on the pole crew arranging // and isolating supply. 200kva transformer blown up. leaking out of LV bushings. Small fire on the ground.
1259 | United 17/58 | United | 26/01/2018 | 0.18564 | -37.9405 | 145.1877 | 46 ASCOT DRIVE, NOBLE PARK NORTH | 8809817 | LD 03 | Low voltage AC (<1kV) | Urban | - LV pillar | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5418 | 20180201UTD_03 | UG on site replacing damaged pillar, crew attending to isolated bonded LV ccts & issue permit. Crew reattended/cancelled permit & restored supply at 1515
1260 | United 17/59 | United | 27/01/2018 | 0.67245 | -38.3678 | 144.893 | 221 EASTBOURNE ROAD ROSEBUD | 1309970 | RBD24 | 22kV AC | Urban | - surge diverter | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5412 | 20180129UTD_03 | Refer TE1141571, Crow at RDB24 fdr exit CHP RB0184 caused a small grass fire. Fire report#01687
1261 | United 17/60 | United | 28/01/2018 | 0.44236 | -38.1593 | 145.1092 | 39A BRUARONG CRESCENT FRANKSTON SOUTH | 3315978 | FSH13 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 5422 | 20180205UTD_02 | 400a fuses in krone box feeding ABC, crew looking for //'s. Burnt out krone box on pole. No fire on the ground. Fire incident report #02805 . Replaced the north circuit krone box and 3 x 315A din fuses. LIS# 3315978.
1262 | United 17/61 | United | 28/01/2018 | 0.79514 | -37.7827 | 145.1542 | 3 DAWS ROAD DONCASTER EAST | 7063276 | DC 03 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 5423 | 20180205UTD_03 | Replaced red and white phs south cct 315amp din fuses - cause: burnt out u/g junction box on lis: 7063276 - Possibly due to overload
1263 | United 17/62 | United | 30/01/2018 | 0.36172 | -37.8306 | 145.1871 | 125 ROOKS RD NUNAWADING | 7031360 | RWT24 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5424 | 20180205UTD_04 | Construction crew on site replacing x-arm, on pole #7031360. xarm replaced. no interuption.
1264 | United 17/63 | United | 2018-10-02 | 0.0034722 | -37.8216 | 145.1577 | 4 GLEN EBOR AVENUE BLACKBURN | 7033760 | NW 21 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 5459 | 20180308UTD_04 | On arrival a possum was on the top of the LV krone box and tracking accross, s/stn isolated lv/hv to remove possu, dmage to krone box... #12 Glen Ebor Ave.. LIS= 7033760
1265 | United 17/64 | United | 2018-12-02 | 0.14464 | -37.7564 | 145.1249 | 3 SWILK STREET TEMPLESTOWE | 7057869 | BU 14 | 11kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5430 | 20180219UTD_01 | Person reported loud bang off pole 12 swilks st - which meets foot st. Possum caused flashover on LIS # 7057869, no apparent damage. Small fire when fell to the ground , Fire report#03169
1266 | United 17/65 | United | 13/02/2018 | 0.73402 | -37.8853 | 145.0252 | 37 MASTERS STREET CAULFIELD | 2301975 | CFD13 | 11kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5439 | 20180223UTD_03 | Customer indicated pole on fire - A HV bridge in master 1n pine lis 2301978, indicated a bird had caused a flashover which showed burn marks on crossarm
1267 | United 17/66 | United | 14/02/2018 | 0.37448 | -37.8872 | 145.0249 | 865 GLEN HUNTLY ROAD CAULFIELD | 2306516 | CFD13 | 11kV AC | Urban | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 5440 | 20180308UTD_02 | As per MFB-- Flames coming from powe lines from a blown HV Bridge LIS = 2306515
1268 | United 17/67 | United | 14/02/2018 | 0.41058 | -38.3069 | 145.0302 | 231 NEPEAN HIGHWAY DROMANA | 1103402 | DMA24 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | Very high | 1 | 1 | 5440 | 20180226UTD_01 | A Tree has fallen on to HV, caused grass fire at lis # 1103402, no damage to UE assets, Fire Report #6723
1269 | United 17/68 | United | 14/02/2018 | 0.79678 | -37.7889 | 145.1905 | 49 GARDEN ROAD DONVALE | 7067244 | NW 13 | 22kV AC | Urban | - overhead conductor (ABC) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 5431 | 20180216UTD_01 | Old Generation HV ABC failure in Garden Rd between LIS#7067244 & LIS#7067243, lying on ground, fire start approx 3m2, report #03170.
1270 | United 17/69 | United | 16/02/2018 | 0.16806 | -38.0904 | 145.1254 | 39 NEPEAN HIGHWAY SEAFORD | 3318167 | CRM33 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5434 | 20180219UTD_03 | LIS # 3318167 fire is out but xarm is burnt. Needs replacement.
1271 | United 17/70 | United | 16/02/2018 | 0.96032 | -37.9655 | 145.1734 | 6 DOUGLAS STREET NOBLE PARK | 9821649 | NP 25 | Low voltage AC (<1kV) | Urban | - luminaries (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5433 | 20180219UTD_02 | There is a damaged street light head 250w HPS has been disconnected at the base of the pole. Crew to return AH during week to replace the head. TO1153661 raised for ace to repalce head LIS 9821649
1272 | United 17/71 | United | 19/02/2018 | 0.75118 | -37.9846 | 145.032 | 9 GARETH AVENUE BEAUMARIS | 1811309 | BR 04 | Low voltage AC (<1kV) | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 5456 | 20180308UTD_01 | Per mfb - tree has come down brought wires down & possibly tree was on fire - LIS = 1811309
1273 | United 17/72 | United | 21/02/2018 | 0.49694 | -37.8371 | 145.118 | 12 LYNDOCH STREET BOX HILL SOUTH | 7037421 | BH 21 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5441 | 20180226UTD_02 | Contact with HV during high winds of HV outside 4 Lyndoch, some branches have burnt/appears tree has sustained fire damage. LIS 7037421
1274 | United 17/73 | United | 22/02/2018 | 0.82986 | -38.1319 | 145.2222 | 55 LYPPARDS ROAD LANGWARRIN | 3312536 | LWN21 | Low voltage AC (<1kV) | Rural Short | - transformer (pole mounted) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 5445 | 20180227UTD_01 | LV Bushing on Tx melted Small Grass fire . Tx replaced under A/P Fire report# 6821 LIS#3312536 ,
1275 | United 17/74 | United | 26/02/2018 | 0.58786 | -38.4043 | 144.9364 | 74 HYSLOPS ROAD BONEO | 1308857 | RBD12 | 22kV AC | Rural Short | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 5446 | 20180301UTD_02 | Pole fire reported. lis#1308857, Auditor on site. Burning at the king bolt.
1276 | United 17/75 | United | 27/02/2018 | 0.70377 | -37.9273 | 145.0009 | 19 YUILLE STREET BRIGHTON | 1805141 | MR 32 | Low voltage AC (<1kV) | Urban | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5448 | 20180301UTD_03 | Confirmed fire at the base pole, lis#1805141 and not spread. The lead coming out of the YUILLE ROSLYN transformer isolator has burnt off. fire was out on arrival - area size of shoe box
1277 | United 17/76 | United | 28/02/2018 | 0.46638 | -38.3076 | 145.1795 | 184 HIGH STREET HASTINGS | 1110404 | HGS32 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 5449 | 20180301UTD_04 | Council tree branch cracked and fell onto HV in tee to High-Tavern S/S. Small grass fire started underneath approx 2 square metres. CFA had already put out when crew arrived. LIS#1110404. Fire ignition report # 6724.
1278 | United 17/77 | United | 28/02/2018 | 0.70061 | -37.8859 | 145.1375 | 464 WAVERLEY ROAD MOUNT WAVERLEY | 602741 | GW 03 | Low voltage AC (<1kV) | Urban | - overhead service conductor (residential) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 5451 | 20180301UTD_05 | Private tree loc at 462 Waverley came down, pulled service down, active/neutral sitting on tree cause branch to catch on fire, grass fire only in nature strip area, lis 602741. I
1279 | United 17/78 | United | 2018-01-03 | 0.19221 | -38.0681 | 145.1232 | 14 BREEZE STREET BONBEACH | 3302609 | CRM14 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5452 | 20180302UTD_02 | X-arm broken at pole LIS 3302609. Replaced xarm, repaired LV mains, replaced insulators on HV.
1280 | United 17/79 | United | 2018-01-03 | 0.22292 | -38.0018 | 145.0875 | 32 BARKLY STREET MORDIALLOC | 1807136 | MC 02 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5460 | 20180308UTD_05 | Hv termination xarm needs to be replaced - & hv pff fuse units & hv droppers needs to be replaced lis# 1807136 -
1281 | United 17/80 | United | 2018-01-03 | 0.2376 | -37.9423 | 145.1022 | 113 ELDER STREET CLARINDA | 2330256 | CDA22 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5455 | 20180306UTD_02 | X arm burnt through at HV isols OA3477. Replaced x-arm and 3 HV isolators at OA3477. LIS 2330256
1282 | United 17/81 | United | 2018-01-03 | 0.25502 | -37.8358 | 145.1212 | 2 ASQUITH STREET BOX HILL SOUTH | 7037441 | BH 21 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5458 | 20180308UTD_03 | Arm broken 2 poles east of Station St in Asquith st. Tee Off conections broken at first pole in Asquith st. LIS 7037441
1283 | United 17/82 | United | 2018-01-03 | 0.29671 | -37.836 | 145.1951 | 678 MITCHAM ROAD VERMONT | 639555 | RWT24 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5461 | 20180309UTD_01 | @0637 hrs mfb advised are on site - insulator has burnt off - HV is stiing on it and about to drop - xarm is on fire and mfb request attendance asap as they require to put water on fire, lis # 0639555
1284 | United 17/83 | United | 2018-01-03 | 0.29682 | -37.9507 | 145.0871 | 47 GOLF VIEW ROAD HEATHERTON | 1814372 | HT 10 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5462 | 20180309UTD_02 | X-arm fire damaged at T-off Golf View Cnr Henry. LIS 1814372. X-arm replaced under access permit.
1285 | United 17/84 | United | 2018-01-03 | 0.31912 | -37.8323 | 145.18 | 1 WENDY STREET FOREST HILL | 7033459 | NW 33 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5463 | 20180309UTD_03 | LIS #7033459 pole fire / X-Arm failure Mt Pleasant Rd X-arm replaced under Access Permit.
1286 | United 17/85 | United | 2018-07-03 | 0.94356 | -37.8697 | 144.9775 | 19 SPENSER STREET ST KILDA | 2306019 | EW 12 | 11kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5470 | 20180313UTD_04 | Private large private palm tree located at #19 Spencer St buring out on hv street mains - G&B crew to attend first thing AM Thurs 8/3/18 to cut back tree - lis: 2306019
1287 | United 17/86 | United | 2018-08-03 | 0.77207 | -37.8843 | 144.991 | 11A FOAM STREET ELWOOD | 2308135 | EW 14 | 11kV AC | Urban | - surge diverter | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5474 | 20180315UTD_02 | lis 2308135 per MFB o/s #11 - fuses activated at lis 2308130 per mfb - Suspected Surge arrestor exploded igniting some vegetation underneath
1288 | United 17/87 | United | 2018-09-03 | 0.3412 | -38.3818 | 145.1243 | 5 YORK AVENUE BALNARRING | 1106688 | HGS23 | Low voltage AC (<1kV) | Rural Short | - overhead service conductor (residential) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5523 | 20180501UTD_03 | Private tree rubbed through service and caught fire approx 2sqm on ground replaced grey twisted service that had rub thru on cust tree, LIS - 1106688, tree cut back
1289 | United 17/88 | United | 2018-10-03 | 0.78642 | -38.2501 | 145.0818 | 945 MOOROODUC HIGHWAY MOOROODUC | 1104826 | MTN24 | Low voltage AC (<1kV) | Rural Short | - connection box | single phase | Started in or originated from a distribution system | HBRA only | 1 | Very high | 1 | 1 | 5473 | 20180313UTD_06 | replcd 100amp fuse box due to burnt out box caused fire on the ground... fire report # 6761…..LIS 1104826
1290 | United 17/89 | United | 17/03/2018 | 0.33959 | -38.3742 | 145.0903 | 35 STANLEYS ROAD MERRICKS | 1108223 | MTN32 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | Severe | 2 | 2 | 5484 | 20180320UTD_02 | Tree on OHC , lis1108223 tee ex MT0227 spur. ACR open to L/O S/E/F 50a. Tree inside #31 Stanleys Rd
1291 | United 17/90 | United | 17/03/2018 | 0.59215 | -38.2275 | 145.1595 | 66 CLARENDON DRIVE SOMERVILLE | 1112407 | HGS22 | 22kV AC | Rural Short | - insulators | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 5524 | 20180501UTD_04 | Passer by reported flames, sparking and acking from pole top. Tx + fuse units flashed over and have been replaced, system restored to normal. LIS 1112407
1292 | United 17/91 | United | 18/03/2018 | 0.45704 | -37.9441 | 145.0777 | 125 COCHRANES ROAD MOORABBIN | 1815975 | HT 03 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 5481 | 20180319UTD_04 | x arm fire - lis 1815975 - HV strain arm burnt and req replacement - blue phase HV insulator on top of strain arm tracked to x-arm.
1293 | United 17/92 | United | 18/03/2018 | 0.53338 | -37.9924 | 145.0724 | 29 THE CORSO PARKDALE | 1808896 | M 35 | 11kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 5482 | 20180319UTD_05 | Crew found HV int xarm broken with HV conductor hanging close to LV. LIS#1808896 Antibes St Nth of Corso.
1294 | United 17/93 | United | 18/03/2018 | 0.54032 | -37.7959 | 145.1419 | 85 WETHERBY ROAD DONCASTER | 7061588 | DC 03 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 5485 | 20180320UTD_03 | Part of DC10 DC3 feeder fault -Tree in park failed starting a ground fire - fire report 03009…..LIS 7061588
1295 | United 17/94 | United | 18/03/2018 | 0.5461 | -38.0227 | 145.2047 | 54 ELLIOTT ROAD DANDENONG SOUTH | 635717 | DSH14 | 22kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 5486 | 20180320UTD_04 | Crew found 66/22 KV pole broken due to a pole fire at the king bolt of the tee off xarm LIS#0635717.
1296 | United 17/95 | United | 18/03/2018 | 0.55957 | -37.8499 | 145.1157 | 213 BURWOOD HIGHWAY BURWOOD | 7029110 | EB 11 | Low voltage AC (<1kV) | Urban | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 5525 | 20180501UTD_05 | Refer to TE#1162535. Crew found private tree from Deakin Uni on the LV mains at LIS#7029110 which caused a 15E BA fuse Bph to blow at the TX
1297 | United 17/96 | United | 18/03/2018 | 0.56001 | -38.3465 | 144.9556 | 12 BRACKEN RIDGE DROMANA | 1306759 | DMA13 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | Severe | 2 | 2 | 5487 | 20180321UTD_01 | CFAadvised that live line is whipping around on the ground causing grass spot fires- refer details on f tbl 1162842….LIS 1306759
1298 | United 17/97 | United | 18/03/2018 | 0.59542 | -38.2278 | 145.1915 | 12 DROVERS LANE SOMERVILLE | 1109045 | HGS33 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 5488 | 20180321UTD_02 | Cause was private tree branch from number 14 Drovers Lane at LIS# 1109045. Damage: HV condctor on deck as above and to be repaired under A/P. Small grass fire started on site.
1299 | United 17/98 | United | 18/03/2018 | 0.72234 | -38.4036 | 145.0696 | 3670 FRANKSTON-FLINDERS RD, MERRICKS | 9648679 | DMA15 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | Severe | 2 | 2 | 5489 | 20180322UTD_01 | Large tree failed and brought down HV, 100m2 grass fire, LIS 9648679
1300 | United 17/99 | United | 19/03/2018 | 0.89583 | -38.1034 | 145.1285 | 48 RAILWAY PARADE SEAFORD | 3306355 | CRM33 | 22kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 5492 | 20180322UTD_04 | Top of HV / LV pole on fire at 2 way tee pole corner of Station St and Railway Pde in Seaford. Emergency switching to de-energise 22 kV conductors to allow Fire brigade to put out fire. Fire Report #6824. LIS 3306355
1301 | United 17/100 | United | 20/03/2018 | 0.011806 | -38.075 | 145.1228 | 499 STATION STREET CARRUM | 3304906 | CRM12 | 22kV AC | Urban | - insulators | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5527 | 20180502UTD_01 | Also see TE# 1163349. Cause was tracking of HV fuse units in misty weather, which flashed over to steel x-arm / concrete pole. LIS 3304906
1302 | United 17/101 | United | 21/03/2018 | 0.54604 | -38.2747 | 145.0291 | 21 GREENFIELD WAY MOUNT MARTHA | 1102825 | DMA24 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 5494 | 20180326UTD_01 | Tree bought down HV ex HV fuses MT0042. LIS# 1102825 29 Greenfield rd. (5 doors down from Bay rd). 1 Bay of single phase HV on the ground. Repaired under AP.
1303 | United 17/102 | United | 22/03/2018 | 0.8448 | -38.383 | 144.9229 | 20 WAKOOL AVENUE ROSEBUD | 1311483 | RBD12 | Low voltage AC (<1kV) | Rural Short | - overhead service conductor (residential) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5495 | 20180326UTD_02 | Replaced OH single phs service, cut cust tree clear, tested and left on. Started small fire half sq meter, already put out, service had rubbed through on tree, fire start fire report 6825. LIS# 1311483.
1304 | United 17/103 | United | 24/03/2018 | 0.45189 | -37.9845 | 145.1411 | 1 TERALBA CLOSE DINGLEY VILLAGE | 618974 | NP 12 | 22kV AC | Urban | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5526 | 20180501UTD_06 | LIS 0618974 - MFB reported pole on fire, On arrival flex had burnt off and likely cause was a possum…..however will record as connection failure
1305 | United 17/104 | United | 24/03/2018 | 0.46594 | -38.1074 | 145.1531 | 217R AUSTIN ROAD SEAFORD | 3307951 | FTN12 | 22kV AC | Urban | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5528 | 20180502UTD_02 | Tree branch on HV bushing, removed and replaced 16A PFF. lis 3307951. Bushing cover melted and cleaned up with new cover under EAP26809 I@15:55 C@16:05. Possom proofed.
1306 | United 17/105 | United | 24/03/2018 | 0.60764 | -37.816 | 145.1667 | 19 PEACEDALE GROVE NUNAWADING | 7029117 | NW 21 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5500 | 20180328UTD_01 | MFB advised pole fire at lis # 7029117 - This was alledgedy caused by lightening
1307 | United 17/106 | United | 24/03/2018 | 0.64986 | -38.0432 | 145.1258 | 42 JACKSONS ROAD CHELSEA | 3304380 | CRM35 | Low voltage AC (<1kV) | Urban | - underground cable | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5529 | 20180502UTD_03 | LV crutch on U/G has blown up, requires U/G to repair - ug reterminated cabled that had blown at the crutch at the pole lis# 3304380 replcd white & blue 160amp hrc fuses
1308 | United 17/107 | United | 26/03/2018 | 0.56667 | -38.3823 | 144.8321 | 2 CRESTVIEW COURT RYE | 1317970 | STO23 | 22kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5502 | 20180329UTD_02 | Tracking at LV X-arm King Bolt, cause pole to break, HV swinging in the air - clashed, pole LSI#1317970. crew to replace pole with HV LV strain arm with bus fuse isols on LV. 12.5/12 pole.
1309 | United 17/108 | United | 2018-11-04 | 0.034363 | -37.794 | 145.1419 | 77 WETHERBY ROAD DONCASTER | 7061503 | DC 03 | 22kV AC | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5511 | 20180427UTD_04 | Possum on HV open HV bridges, #3 Dunoon. LIS#7061503 This caused HV wire on ground cnr Dunoon and Wetherby (Ampac failed at this location and centre phase HV conductor made contact with white phase LV),
1310 | United 17/109 | United | 2018-12-04 | 0.0013889 | -38.1922 | 145.2068 | 70 WEST ROAD LANGWARRIN SOUTH | 3301177 | HGS33 | Low voltage AC (<1kV) | Rural Short | - underground service cable (residential) | two phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | Very high | 1 | 1 | 5512 | 20180427UTD_05 | LIS# 3301177 - Pole only slight schorch marks, person had tied chain around pole to remove car from trailer, which damaged assets and caused a small fire- few square meters under base of pole, fire report 03822
1311 | United 17/110 | United | 14/04/2018 | 0.43384 | -38.3741 | 145.1254 | 3045 FRANKSTON-FLINDERS ROAD BALNARRING | 1105857 | MTN32 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 5556 | 20180608UTD_02 | Reported as tree on fire by CFA, Tree removed from the overhead. Tree out side 3045 Frankston Flind Rd Balnarring
1312 | United 17/111 | United | 14/04/2018 | 0.45596 | -38.3386 | 145.122 | 230 MYERS ROAD BALNARRING | 3440979 | HGS23 | 22kV AC | Rural Short | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | Very high | 1 | 1 | 5557 | 20180608UTD_03 | Cust reporting that tree branch on lines is currently on fire - Private tree branch has been taken off overhead conductors, no damage to UE assets/no follow up required, lis 3440979,
1313 | United 17/112 | United | 14/04/2018 | 0.52451 | -37.9826 | 145.0244 | 1 SURF AVENUE BEAUMARIS | 1811508 | BR 04 | 11kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 5515 | 20180430UTD_01 | HV X-Arm burnt at Lis 1811508, EAP#48659 I@19:45 C@21:15, x-arm replaced and ok for service.
1314 | United 17/113 | United | 14/04/2018 | 0.54706 | -37.9721 | 145.0625 | 1300 NEPEAN HIGHWAY CHELTENHAM | 1822160 | M 23 | 11kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 5517 | 20180430UTD_03 | CH8926 discs damaged and pole top burning. - resagged and repaired 3 x HV conductors and replaced 2x poly HV insulators lis # 1822160- follow up is required new pole and gas switch - Fire report 2012 by
1315 | United 17/114 | United | 2018-08-05 | 0.33681 | -38.3185 | 144.9872 | 90 MARINE DRIVE, SAFETY BEACH | 8825005 | DMA14 | 22kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5536 | 20180514UTD_01 | Pole fire at MARINE PRESCOTT s/s pole to be replaced under EAP. LIS 8825005
1316 | United 17/115 | United | 2018-08-05 | 0.75037 | -37.9403 | 145.0287 | 41 WIDDOP CRESCENT HAMPTON EAST | 1821596 | SR 14 | Low voltage AC (<1kV) | Urban | - connection box | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5537 | 20180517UTD_01 | replaced burnt out 3ph fmjb on ug service feeding cricket club (LIS 1821596)
1317 | United 17/116 | United | 2018-09-05 | 0.97218 | -38.3385 | 144.9697 | 2 FRIEDA STREET DROMANA | 1317512 | DMA13 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5538 | 20180517UTD_03 | crew found a HV xarm fire at pole Lis#1317512, and replaced it under EAP. PM notif# 1000651866
1318 | United 17/117 | United | 14/05/2018 | 0.875 | -37.9441 | 145.068 | 35A ROBERNA STREET MOORABBIN | 1816408 | HT 13 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5551 | 20180531UTD_02 | Crew advise burnt marks on the x-arm 35% and 20% on pole at x-arm. Followedup with duty officer who will arrange crew to replace x-arm tonight. Lis#1816408 at front of 31 ROBERNA ST MOORABBIN VIC 3189.
1319 | United 17/118 | United | 17/05/2018 | 0.78403 | -37.942 | 145.1022 | 109 ELDER STREET CLARINDA | 2330255 | CDA22 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5540 | 20180522UTD_01 | crossarm fire, section switched out for AP emergency switching, refer LIS 2330255
1320 | United 17/119 | United | 26/05/2018 | 0.87962 | -37.965 | 145.1735 | 99A LIGHTWOOD ROAD NOBLE PARK | 620877 | NP 25 | Low voltage AC (<1kV) | Urban | - luminaries (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5552 | 20180531UTD_01 | Crew replaced 1x150HPS street light after being burnt out. Pole is ok. Lis#0620877.
1321 | United 17/120 | United | 26/05/2018 | 0.99374 | -37.7879 | 145.1193 | 551 DONCASTER ROAD DONCASTER | 7055915 | WD 23 | 22kV AC | Urban | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5558 | 20180608UTD_04 | MFB reported a fire and upon attendance a HV SW connection failed at a manual gas SW DT 0077 in Baily Grove Lis 7055915
1322 | United 17/121 | United | 29/05/2018 | 0.86578 | -38.0124 | 145.0907 | 28 NEPEAN HWY ASPENDALE | 3302246 | MC 01 | Low voltage AC (<1kV) | Urban | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5555 | 20180608UTD_01 | Crew isolated the substation LV/HV and replaced the TX LV leads and Krone box as they had melted together. LIS # 3302246.
1323 | United 17/122 | United | 31/05/2018 | 0.70514 | -37.8231 | 145.2121 | 2 WALWA STREET MITCHAM | 7029309 | RWT34 | 22kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5553 | 20180601UTD_01 | Pole LIS 7029309, Culwell Av cnr Walwa St, HV anchor pole has burnt off approx 1 metre from the top. d. Ppole replaced under EAP #11320. No report of any ground fire present.
1324 | United 17/123 | United | 2018-08-06 | 0.50604 | -38.2567 | 145.1896 | 1506 FRANKSTON-FLINDERS ROAD TYABB | 1108046 | HGS33 | 22kV AC | Rural Short | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5561 | 20180612UTD_01 | FRANKSTON-FLINDERS RD, LIS #1108046, 3 . Pole burning at the x-arm strap. Tracking down the pole from the top 22kV x-arm to the lighting bracket (below the LV) fire report # 00710
1325 | United 17/124 | United | 2018-09-06 | 0.71624 | -38.3389 | 144.7306 | 38 NORMANBY ROAD SORRENTO | 1306940 | STO13 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5562 | 20180612UTD_02 | There was a fire at the fmb up the pole. no fire on the ground. crew replaced the FMB LIS # 1306940. Fire Report # 05305
1326 | United 17/125 | United | 2018-12-06 | 0.28316 | -38.2205 | 145.0408 | 67 BARKLY STREET, MORNINGTON | 9833531 | MTN21 | Low voltage AC (<1kV) | Urban | - luminaries (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5568 | 20180626UTD_01 | 150w SL head burnt out. no flames visible. mfb on site. isolated SL pole# 9833531 at FMB on LIS# 1100704. head will require repalcement. TO# 1187484 raised for ace
1327 | United 17/126 | United | 15/06/2018 | 0.39931 | -37.833 | 145.1593 | 1A LAGOONA COURT BLACKBURN | 7026473 | BH 11 | Low voltage AC (<1kV) | Urban | - luminaries (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5571 | 20180626UTD_02 | burnt out S/L head on lis # 7026473, 150 HPS lantern, isolated at service on lis # 7018257, traffic control required or do early or late in day, refer # 1189087
1328 | United 17/127 | United | 16/06/2018 | 0.27228 | -38.3582 | 145.1625 | 1 WELLINGTON ROAD BITTERN | 1107245 | HGS23 | 22kV AC | Rural Short | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 5566 | 20180619UTD_01 | LIS#1107245 Single phase sub , footpath fuse candling. replace 6 amp edo
1329 | United 17/128 | United | 19/06/2018 | 0.1875 | -38.3569 | 144.7508 | 1 KEATING AVENUE SORRENTO | 1306410 | STO13 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 5572 | 20180626UTD_03 | repl 2 x 3ph FMB's - lis 1306410 - fire report 2044 - nst all ok and supply left on affecting #2-6, 8 and 10 - fire out on arrival - poss salt corrosion
1330 | United 17/129 | United | 25/06/2018 | 0.54854 | -38.1361 | 145.1289 | 72 DANDENONG ROAD FRANKSTON | 8818998 | FTN14 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5595 | 20180720UTD_02 | Customer reported "power pole on fire, half way up pole" Replaced 3ph FMB feeding p2p U/g to #68, ,lis # 8818998,
1331 | United 17/130 | United | 26/06/2018 | 0.99861 | -38.2536 | 145.0573 | 118 RACECOURSE ROAD MOUNT MARTHA | 9751716 | MTN24 | 22kV AC | Rural Short | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5581 | 20180710UTD_01 | lis#9751716 Confirmed pole fire. Suspect HV insulators tracking. Pole burnt out and needs replacing. Fire report # 04449 per S Goodman.
1332 | United 17/131 | United | 30/06/2018 | 0.83711 | -38.3838 | 144.7929 | 10 CLEMATIS COURT RYE | 1318371 | STO21 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5582 | 20180710UTD_02 | Repaired connections at FOLCB at pole end to house 24. repaired connection to service at num 22. Fire report at pole end. # 6762. LIS 1318371
1333 | Powercor 17/18 | Powercor | 2017-01-07 | 0.26181 | -37.98302685 | 144.50026095 | 720 Old Melbourne Rd., Little River. | 30059970 | FNS022 | Low voltage AC (<1kV) | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 13270 | 20170731PWA_05 | At 6:17am, a fault was reported as All Supply Fail at the incident location. The crew attended and found that a LV Crossarm and fuse box had caught fire overnight. Debris fell to the ground but did not start a fire. The crew made repairs as required and the site was made safe. There were no reported shocks, injuries or ground fire.
1334 | Powercor 17/19 | Powercor | 2017-05-07 | 0.50278 | -36.68321263 | 144.92031643 | 431 Andersons Rd., Goobarup. | 33102775 | SHP021 | 12.7kV AC (SWER) | Rural Long | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 13205 | 20170706PWA_02 | A customer reports a tree had been cut and it had fallen onto the power lines and started a fire at the above address. A crew attended and found the land owner had been pushing trees over with a bull dozer when one of the trees had contacted an SWER O/H HV conductor, breaking the conductor, causing it to fall to the ground. The contacting tree branch started to burn but there was no ground fire start. The customer extinguished the fire. Protection operated. Colbinabbin P244A ACR went to lock out. The crew repaired the broken conductor and restored supply. Final conductor height btn P12 and P12E Karagounis S/L is 8.3m mid span. There were no reported shocks, injuries or 3rd party damage.
1335 | Powercor 17/20 | Powercor | 2017-09-07 | 0.77778 | -36.87484888 | 143.87416363 | 3842 Bendigo Maryborough Rd., Eddington. | 32029298 | MRO007 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 13207 | 20170711PWA_01 | VicFire reported that a conductor was down at the incident location, A customer also reported flickering lights and partial supply for a period of approximately 15 minutes. On arrival the crew found that a conductor of a single phase spur line had failed approximately 10m from T/off pole 213 Tarnagulla, the conductor remained back-fed via the HV winding of the load side transformer for a period prior to Tarnagulla ACR tripping to lockout on SEF. A fuse on Tarnagulla P211 operated but hung up. Approximately 12 small patches of burnt crop were observed by the crew, caused by the downed HV conductor remaining in an energised state until the ACR operated.There were no reported injuries or 3rd party damage. NAO requested crew to send section of failed conductor to asset investigations team.
1336 | Powercor 17/21 | Powercor | 14/07/2017 | 0.39514 | -37.86957256 | 144.72514986 | 1 Industrial Ave, Hoppers Crossing. | 30115749 | LV005 | 22kV AC | Urban | - insulators | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 13267 | 20170731PWA_02 | A customer informed a broken insulator on the ground and the wire resting on cross arm at the incident location. On arrival the Powercor crew found that a Pole Fire had occurred on INDUSTRIAL DUNLOP P02E (LIS 204466 intermediate pole). The crew made the place safe and repairs arranged. There was no ground fire, third party damage, injury, outage or HVI found.
1337 | Powercor 17/22 | Powercor | 25/07/2017 | 0.49236 | -34.35970805 | 141.97983566 | Cnr of Meridian Rd and Millewa Rd., Merrinee. | 32141660 | RCT023 | 22kV AC | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 13254 | 20170726PWA_02 | Emergency Services reported a grass fire at the incident location. Upon arrival, the Powercor crew found that a bird flashover and small grass fire (150 sq mts). No obvious damage on network assets found. Crew made the place safe. Appears a bird flashed over from live line flex to steel crossarm. A FFU raised to complete repairs including earthing. There was a ground fire (150 sq mts) no injuries.
1338 | Powercor 17/23 | Powercor | 30/07/2017 | 0.91389 | -37.60142707 | 143.84094246 | 235 Albert St., Sebastopol. | 34000831 | BAS034 | Low voltage AC (<1kV) | Urban | - lamps (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 13266 | 20170731PWA_01 | A report was received from Vic Fire that a street light was on fire outside of 235 Albert Street Sebastopol. On arrival the crew found that one of the light heads on the pole in the median strip at the above location had caught fire and self-extinguished. The crew isolated supply to the pole and the light will be replaced at a later date. There was no injury, shock, ground fire or third party damage.
1339 | Powercor 17/24 | Powercor | 2017-03-08 | 0.74306 | -36.74891577 | 144.28504632 | 79 Lucan St., Bendigo. | 30027839 | EHK033 | Low voltage AC (<1kV) | Urban | - fuse (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 13327 | 20170818PWA_01 | Vicfire called reporting pole fire. Upon arrival crew were advised that the CFA had already departed. No sparking was evident from the FSD at pole LUCAN 73 (LIS-424910). The FSD is a normally open point between bare LV and LV ABC. The cause of the sparking is believed to have been incited by wet weather. Crew advised that the LV fuse back at the substation had blown therefore there was no more evident sparking. Crew advised only slight burning, (hardly visible) of the cross-arm under which sat the fuse box. The crew replaced the partially melted fuse box and restored supply. There was no other damage to assets or private property.
1340 | Powercor 17/25 | Powercor | 2017-03-08 | 0.78542 | -37.88807590 | 144.61829758 | 4 Valley Mews, Wyndham Vale. | 30320417 | WBE023 | Low voltage AC (<1kV) | Rural Short | - fuse (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 13322 | 20170817PWA_01 | Powercor was contacted by several customers indicating no supply. On arrival, the crew found that the LV fuse board of the Kiosk substation ‘VALLEY-GREENS’ had caught fire due to an overheating fault. The fire was contained inside the kiosk substation and extinguished by itself. The LV board was deemed not serviceable and the 3 x LV cables attached to the LV board and connections were damaged. The crew made the place safe and at the time of my call the crew was in the process to repair the LV cables. Repair works still to be completed. There were no reported injuries, third party damage or ground fire.
1341 | Powercor 17/26 | Powercor | 15/08/2017 | 0.76667 | -36.71372268 | 142.19901795 | 2 Bradbury lane, Horsham. | 30260985 | HSM010 | Low voltage AC (<1kV) | Urban | - fuse (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 13344 | 20170828PWA_01 | Vic Fire reported an overhead service cable on fire at the incident location. On arrival the crew found that the LV Fused Mains Box connected to the overhead service had been on fire The LV Fused mains box had melted, and parts had fallen to the ground. There was no ground fire or any other damage caused by this incident.
1342 | Powercor 17/27 | Powercor | 20/08/2017 | 0.31667 | -38.38342379 | 142.16867619 | 2976 Princes Highway, Port Fairy. | 30135294 | KRT013 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 13360 | 20170908PWA_03 | The CFA reported a pole fire at the incident location. On arrival the crew found that the pole had burnt and the CFA had extinguished it. Talking to the crew there was no ground fire. No third party damage or injury was reported. The crew made the site safe, conducted repairs and supply was restored.
1343 | Powercor 17/28 | Powercor | 2017-10-09 | 0.87917 | -38.11347315 | 144.65764493 | 2 The Esplanade, Portarlington. | 32070587 | DDL021 | Low voltage AC (<1kV) | Rural Short | - fuse (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 13375 | 20170926PWA_06 | CFA reported a pole fire at the incident location. On arrival the crew found that fuse box, LV droppers and conduit had melted due to an overheated connection. The CFA told the crew they had extinguished a fire prior to their arrival and only melted plastic on the ground. No ground fire, no injuries, no third party damage.
1344 | Powercor 17/29 | Powercor | 2017-11-09 | 0.67986 | -37.97095435 | 141.73206568 | Henty Highway, Condah. | 33058882 | HYT011 | 22kV AC | Rural Short | - pole (concrete) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 13362 | 20170912PWA_03 | Vicfire reported a two vehicle collision brought down power lines and started a grass fire at the incident location. On arrival the crew found that a truck had veered off the road to miss another vehicle hitting the pole and the HV conductors had started multiple small fires (approx. 5m2 in total). Hamilton Police were also in attendance and reported no injuries.
1345 | Powercor 17/30 | Powercor | 17/09/2017 | 0.37292 | -38.25233286, | 142.41669021 | 420 Thwaites Rd., Winslow. | 32195765 | KRT012 | Low voltage AC (<1kV) | Rural Long | - fuse (any other type) | single phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 13374 | 20170926PWA_05 | The CFA reported a fire in the meter board at their dairy at the incident location. On arrival the Electrical Inspector found that a Low Voltage fuse/s has failed and caused the meter panel including the meter to catch fire. The LV fuses are a Powercor asset. Talking to the Electrical Inspector there was no ground fire. No third party damage and no injury was reported. The crew made the site safe, the meter panel and associated equipment was replaced and supply was restored.
1346 | Powercor 17/31 | Powercor | 18/09/2017 | 0.78958 | -34.18144579 | 142.05563670 | 128 Fifth St., Merbein. | 32142995 | MBN014 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 13372 | 20170926PWA_03 | CFA Comms reported pole fire at 128 Fifth St Merbein. On arrival crew found HV cross arm that had caught fire but had extinguished. Crew inspected arm which had charring on it and raised fault follow up to repair. No injuries, no ground fire, no third party damage.
1347 | Powercor 17/32 | Powercor | 18/09/2017 | 0.82222 | -34.12829024 | 142.00884079 | 791 Wentworth Rd., Yelta. | 32150293 | MBN013 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 13371 | 20170926PWA_02 | CFA Comms reported wires sparking at 791 Wentworth Rd Yelta. On arrival crew found HV intermediate cross arm that had caught fire but has since extinguished. Insulator had snapped as a result of the fire and conductor was on the cross-arm. Crew isolated and repaired on site. No injuries, no ground fire, no third party damage.
1348 | Powercor 17/33 | Powercor | 25/09/2017 | 0.19514 | -38.27937004 | 142.20564062 | Spencer rd (Cnr of old spencer rd), Tarrone. | 30144811 | KRT013 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 13373 | 20170926PWA_04 | Person driving past reported a pole fire. On arrival the crew found that the High Voltage cross arm on pole 1 had burnt. The crew isolated supply and installed a new cross-arm on a raiser bracket. There was no reported ground fire, injury or shocks.
1349 | Powercor 17/34 | Powercor | 28/09/2017 | 0.67778 | -36.30583987 | 141.06623411 | 692 Dinyarrak, Lillmur. | 33047492 | NHL031 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 13395 | 20171002PWA_01 | CFA reported a wire down and a fire start at the above location. A crew attended and found a tree had fallen across 1 phase of a single phase HV line, breaking 2 Cross arms and starting a ground fire but no conductor on ground. CFA attended and extinguished fire. One blown 16K HV fuse at P443 Kaniva S/L. Crew replaced broken blown fuse and HV Xarms at P25 and P26 Dinyarrak S/L. Fire started at tree that had fallen onto line. Fire area approx. 50m x 25m. Grass fire in paddock. No third party damage. There were no reported shocks, injuries or 3rd party damage.
1350 | Powercor 17/35 | Powercor | 2017-04-10 | 0.47847 | -36.34760627 | 145.44063807 | 335 Ford Rd., Grahamvale. | 33096629 | SHN024 | Low voltage AC (<1kV) | Rural Short | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 13398 | 20171005PWA_01 | A customer reported a fire on the pole at the incident location. On arrival the crew found that a neutral connection in a crossarm mounted junction box had overheated. Hot debris fell to the ground causing a grassfire of approx. 1m x 2m= 2m2 on the roadside. The crew also stated that the customer had to replace a damaged power circuit breaker on their switchboard. The initial report stated that the customer had sustained damage to some equipment, however this could not be verified. There were no injuries reported.
1351 | Powercor 17/36 | Powercor | 2017-07-10 | 0.60972 | -35.50218803 | 143.67216428 | 21 cornish Avenue, Tresco. | 30247555 | KGT004 | 22kV AC | Rural Long | - underground cable | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 13412 | 20171009PWA_03 | Powercor received report of a fire. Fire was out on when crew attended onsite. Cause to be confirmed, however it is suspected that the fire started at the HV Underground Cable Head Pole and was possibly a bird flashover (KGT004).
1352 | Powercor 17/37 | Powercor | 2017-07-10 | 0.91042 | -38.388109 | 142.565220 | 10440 Princes Hwy, Allandford. | 31030223 | WBL002 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 13410 | 20171009PWA_01 | Powercor received a call from VicFire reporting “sparking wires” at Warrnambool. When crews arrived on site they found CFA crews in attendance and they had extinguished a number of spot fires, approx. 5m x 80m along the Princes Hwy, approx. 1.2km east of Staffords Rd. The cause of the fires appeared to be a broken 22kV conductor.
1353 | Powercor 17/38 | Powercor | 2017-08-10 | 0.49236 | -38.04708347 | 144.14165308 | BANNOCKBURN-SHELFORD Rd., Bannockburn. | 30231988 | GL012 | 22kV AC | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 13411 | 20171009PWA_02 | On Sun 8 Oct 2017 at 11:49am, Powercor received a call from VicFire reporting a wire down at LIS989876 with a small grass fire when crews arrived at the incident site, they found a broken tree branch across the 22kV HV overhead conductors. A small ground fire (2m x 2m) near the base of the pole had been extinguished by the CFA. The tree was part of the Bannockburn Recreation Reserve. No conductors fell to ground. No other third party property damage was reported. No injuries were reported.
1354 | Powercor 17/39 | Powercor | 2017-09-10 | 0.53889 | -36.35844026 | 142.99145627 | 27-29 Corack Rd., Donald. | 32019143 | CTN006 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 13415 | 20171011PWA_02 | Numerous customers reported no supply . Crew attended to find end of HV cross-arm had burnt off and HV insulator was resting on LV cross-arm. There was no ground fire, no reported injuries or third party property damage.
1355 | Powercor 17/40 | Powercor | 2017-11-10 | 0.85069 | -38.11989462 | 144.32707340 | 18 Heather St., Hamlyn Heights. | 30074807 | GL013 | Low voltage AC (<1kV) | Urban | - fuse (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 13463 | 20171103PWA_03 | A customer reported pole fire outside the above address. Crew Located Burnt out FSD. Report from customers that had been on fire and now out there was no ground fire, no injuries or third party property damage. Record located during OMS month end search.
1356 | Powercor 17/41 | Powercor | 2017-11-10 | 0.66458 | -34.21014657 | 142.19179688 | 473-481 Karadoc Ave, Nichols Point. | 30095498 | RCT011 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 13461 | 20171103PWA_01 | Pole fire on "Pole 8". HV Xarm Replaced. No report of ground fire. Record found during OMS data check at month end.
1357 | Powercor 17/42 | Powercor | 2017-11-10 | 0.77847 | -37.58894686 | 143.96398948 | 2805 Old Melbourne Rd., Dunnstown. | 33006274 | BAS023 | 22kV AC | Rural Short | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 13462 | 20171103PWA_02 | Customer rang to advise of intermittent supply and sparks/fire coming from pole out front of property. Crew attended and found the foot path side EDO fuse had blown but the tube had hung up. This cause the tube to arc and burn internally. The crew also found the copper flex between the EDO unit and the O/H mains had frayed and stranded. The crew isolated the transformer, repairing the flex and replacing the burnt EDO tube. The crew then restored supply. There was not ground fire start. There were no reported shocks, injuries, or 3rd party damage. Note: Incident was not reported to the A/H NAO. It was picked up the next day by the asset investigation group.
1358 | Powercor 17/43 | Powercor | 2017-12-10 | 0.29792 | -35.24898179 | 143.47224915 | Athorn Rd., Woorinen. | 31022238 | SHL004 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 13464 | 20171103PWA_04 | Passing truck driver advised crossarm rotten, has broken and wires hanging low with insulator off beam, not within reachable height but a breeze could cause wires to make contact with pole. In Athorn Rd between Ridge Rd and Goodman Rd. Area also known as Woorinen North or Beverford. On arrival crew found crossarm burnt off at end.
1359 | Powercor 17/44 | Powercor | 13/10/2017 | 0.40278 | -35.05216529 | 142.50476315 | Lot 1 Daley Rd., Ouyen. | 32153108 | OYN003 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 13458 | 20171030PWA_02 | A customer reported a pole down at the incident location. On arrival the crew found that a pole fire the pole appears to have burnt from the base upward and was laying on the ground. The crew also reported there was no ground fire. Third party damage in the form of a dead sheep was found by the crew. No injury was reported.
1360 | Powercor 17/45 | Powercor | 14/10/2017 | 0.077778 | -37.96336084 | 144.50522521 | 7 Harold court, Little River. | 33040949 | FNS022 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 13456 | 20171030PWA_01 | Vicfire reported a fire at this address. On arrival the crew found that a fused Overhead line connector box had failed. The falling ash and debris fell to ground without causing a ground fire. There was no reported injuries or third party property damage.
1361 | Powercor 17/46 | Powercor | 18/10/2017 | 0.55556 | -38.0187035 | 144.391754 | 39 Kees Rd., Lara. | 30071450 | FNS012 | 22kV AC | Rural Short | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 13425 | 20171019PWA_01 | Local resident reported that a tree branch has fallen across the high voltage overhead line one phase has broken and a small ground fire at the incident location. On arrival the fault crew found that a branch from a large tree towering over the line had broken off, falling onto the high voltage overhead breaking the outer phase conductor which then fell onto the low voltage circuit below. There was no injury as result of this incident. High voltage injection suspected but no damage found (over 100 customers checked). Crew carried out repairs to conductors.
1362 | Powercor 17/47 | Powercor | 25/10/2017 | 0.16042 | -34.29972053 | 142.18533345 | 15 Avocat Avenue N, Red Cliffs. | 32141274 | RCT023 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13465 | 20171108PWA_01 | Pole fire found on Avocat Sewerage 6. Conductors down in tree, tree on fire. HV And LV crossarms replaced. There was no ground fire, no reported injuries or third party property damage.
1363 | Powercor 17/48 | Powercor | 29/10/2017 | 0.65833 | -37.52578822 | 143.866 | 2 Easey St., Invermay Park. | 33005393 | BAN007 | 22kV AC | Rural Short | - fuse (boric acid) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13460 | 20171031PWA_01 | A customer rang to advise a pole was arcing and sparking resulting in a ground fire start at the incident location. A crew attended and found that at P8 Swinglers S/L, the roadside boric acid HV fuse had hung up and burnt, dropping debris on the ground resulting in a ground fire of approx. 1m/sq on road reserve. A CFA crew attended and extinguished the fire. The crew replaced the failed HV fuse and restored supply. There were no reported shocks or injuries.Note: The original fuse operation is related to a previous 48hr report on the 29/10/2017 at 15:48hrs when a tree contact the HV conductors at 12 Taylor Rd., Invermay.
1364 | Powercor 17/49 | Powercor | 2017-02-11 | 0.58264 | -38.22273909 | 141.75523419 | 1514 Clay Rd., Tyrendarra. | 30091494 | PLD001 | 12.7kV AC (SWER) | Rural Long | - fuse (boric acid) | single wire earth return (SWER) | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 13539 | 20171220PWA_01 | A Fault crew attending following an outage found that an Boric Acid fuse had operated at the incident location, however the barrel of the Boric Acid fuse stayed in position without dropping down. The barrel then caught fire. There was no ground fire. There were no reported injuries or third party property damages.
1365 | Powercor 17/50 | Powercor | 2017-09-11 | 0.82153 | -36.37549983 | 145.43190412 | 109 Doyles Rd., Grahamvale. | 33092008 | STN024 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13477 | 20171110PWA_03 | Crew attended to find small ground fire had been extinguished by Vic Fire on road verge. Evidence of a dead crow at the base of the pole. Feeder CB STN024 operated just prior to report from Vic Fire. There were no injuries or third party property damage.
1366 | Powercor 17/51 | Powercor | 2017-11-11 | 0.44167 | -38.11631 | 144.328949 | 134 Vines Rd., Hamlyn Heights. | 32080104 | GL013 | Low voltage AC (<1kV) | Urban | Service lines | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13479 | 20171113PWA_03 | Vicfire reported a fire at the incident location. On arrival the crew found that a neutral screen service cable had failed at the house end roller termination, resulting in blackening of the POA area and the live service cable falling to the ground. The service cable falling to the ground in turn resulted in a grassfire of approx. 1m x 2m= 2m2 in a garden bed in the front yard of the house. There were no injuries or other damage reported.
1367 | Powercor 17/52 | Powercor | 2017-11-11 | 0.45347 | -37.75861529 | 142.11218310 | 541 W Schultz Rd., Hamilton. | 33058168 | NRB-HTN | 66kV AC | Unknown | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 13480 | 20171113PWA_04 | A Powercor crew were patrolling following a 66kV fault, and reported a fire at the incident location. On arrival the crew found that an Ibis had caused a flashover on a 66kV pole and fallen to the ground starting a grassfire of approx. 200m2 of mostly road reserve, with a small area of private land burnt and minor fence damage. The crew extinguished the fire, the CFA did not attend. There were no injuries or other damage reported.
1368 | Powercor 17/53 | Powercor | 2017-12-11 | 0.28125 | -37.8768234 | 142.29509 | 59 Watton St., Penhurst. | 32127148 | HTN003 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13488 | 20171117PWA_05 | A Powercor fault crew were patrolling following a feeder outage and found a crossarm burnt off at the strap bolt at the incident location. There was no ground fire and no reported third party damage or any injuries.
1369 | Powercor 17/54 | Powercor | 2017-12-11 | 0.49931 | -37.0883636 | 143.797623 | 437 Landrigan Rd., Carisbrook. | 33011414 | MRO007 | Low voltage AC (<1kV) | Rural Long | - connector / termination | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 13478 | 20171113PWA_02 | Crew attended to find a connection between bare LV Mains and Service Connection Junction Box had Burnt off on the red phase. A small ground fire on the road verge area resulted. This fire was extinguished by Vic Fire . On arrival crew carried out repairs. There was no property damage, No injuries or reported shocks.
1370 | Powercor 17/55 | Powercor | 14/11/2017 | 0.21597 | -35.05154696 | 143.31663428 | 70 MURRAY STREET, PIANGIL. | 30147267 | SHL002 | Low voltage AC (<1kV) | Rural Long | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 13651 | 20180123PWA_07 | Crew attended to find Junction Box had burnt out between Gang Operated LV Switch and customer Underground Mains. No Ground Fire , No property damage, No injuries, No reported shocks.
1371 | Powercor 17/56 | Powercor | 16/11/2017 | 0.60833 | -37.3616676 | 144.550919 | 1808 Mt Macedon Rd., Woodend. | 31006854 | WND012 | 22kV AC | Rural Long | - insulators | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 13485 | 20171117PWA_02 | Emergency Services informed a pole fire at the incident location. On arrival the crew found that a HV conductor sitting on the cross arm and the arm smoking (one stage the arm and pole slightly burnt through). The protection operated. This was due to a damage/crack on top part of insulator that came off with conductor and rested on the arm. The crew made the place safe and repairs done. There was no ground fire, third party damage or injury.
1372 | Powercor 17/57 | Powercor | 17/11/2017 | 0.42847 | -38.1196556 | 144.349167 | 41- 47 Roseneath St., North Geelong. | 32081845 | GB031 | 22kV AC | Urban | - overhead conductor (bare; copper) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13486 | 20171117PWA_03 | A contractor reported that a scissor lift has inadvertently contacted overhead lines at the incident location. On arrival the fault crew found that a contractor was repairing the scissor lift which was located under the high voltage overhead line, not being fully aware of the high voltage line above. The contractor raised the lift which contacted the live overhead line. This caused arcing between line and scissor lift, the overhead power line broke falling onto the ground starting a small fire at the incident location. MFB crews arrived on site and a small fire was extinguished. (1m by 0.5m). The operator of the lift appeared to be uninjured, he was advised to seek medical attention.
1373 | Powercor 17/58 | Powercor | 18/11/2017 | 0.48333 | -36.0738831 | 145.417465 | 128 Allens Rd., Numurkah. | 32185391 | SHTS-NKA2 | 66kV AC | Unknown | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13495 | 20171121PWA_02 | Vicfire advised of a x-arm fire AT P375 ON SHTS-NKA No.2 line. Upon arrival crew found that the 66kV x-arm had burnt off and the 66kV conductor had landed on the subsidiary 22kV line breaking a 22kV insulator. The structure was a 66kV/22kV INTER. Maree in operations organised the 66kV switching for repairs to be made. All repairs to 66kV and 22kV apparatus were made by 17:30 Causal effects lending to the incident were a dirty 66kV insulator and misting rain at the time of the fault causing the 66kV to track over the x-arm strap onto the arm thereby creating an arm fire. A ground fire ensued in road reserve covering an area of approximately 70m x 5m, there was no reported damage to private property.
1374 | Powercor 17/59 | Powercor | 22/11/2017 | 0.33611 | -35.00414586 | 143.04091930 | 578 Walters Rd., Manangatang. | 30350763 | BBD014 | 12.7kV AC (SWER) | Rural Short | - overhead conductor (bare; aluminium core steel reinforced) | single wire earth return (SWER) | Started by any other thing forming part of or coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 13506 | 20171127PWA_01 | Customer reports a fire start after harvester contact SWER O/H conductor on property. Customer states on the 22nd Nov he was operating a harvester in the paddock when a ground fire start occurred, burning approx. 20 acres of stubble paddock. CFA attended and extinguished fire. Smart meter data shows a momentary outage for a SWER ACR reclose at the time of this event. The next day ( 23rd Nov ) the customer notices a burn make on the harvesters GPS aerial. The fire started when the harvester drove under the SWER overhead conductor. A crew attended and measured to SWER O/H at 5.8m ( Policy states the minimum clearance height for transvers able land is 5.6M ). The crew fitted a raiser bracket to P102 and re tensioned the SWER conductor at P103 to achieve a mid span ground clearance of 7.1m. No damage to the 3/2.75SC. There were no reported shocks or injuries. Note: The span btn P102 and P103 was listed as low conductor in March 2016 at 5.5m. P103 was replaced in April 2016 to achieve a clearance of 5.8m. Customer harvester clearance is 6.0m to top of aerial.
1375 | Powercor 17/60 | Powercor | 22/11/2017 | 0.61181 | -38.16677763 | 144.37001824 | 186 Fyans St., South Geelong. | 32069759 | GLE033 | 22kV AC | Urban | - switch (disconnector/isolator) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13504 | 20171123PWA_01 | A bird flashover occurred at pole adjacent to 170 fryans st ( Lis 17498). Due to fault current there was a flashover at an isolator pole( Lis 17264) which caused a ground fire due to fallen debris. There were no reported injuries or third party property damage.
1376 | Powercor 17/61 | Powercor | 22/11/2017 | 0.59514 | -35.955452 | 145.567657 | 381 Churchill Rd., Yarroweyah. | 32185760 | CME015 | 22kV AC | Rural Short | - switch (disconnector/isolator) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13505 | 20171123PWA_02 | VicFire reported a fire at the incident location. On arrival the crew found that a bird had caused a flashover on open point switch pole, causing the bird to fall to the ground resulting in a ground fire on road reserve. There were no reported injuries.
1377 | Powercor 17/62 | Powercor | 25/11/2017 | 0.79931 | -37.84726520 | 144.67978120 | 1 Verona avenue, Tarneit. | 35264672 | LV001 | 22kV AC | Rural Short | - transformer (kiosk mounted) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13507 | 20171127PWA_02 | Customer reported car hit pole at the incident location. On arrival the crew found serious multiple vehicle accident and one of the vehicle had hit the Sayers – Verona 315kVA Kiosk substation causing major damage to the substation starting fire and oil leak as a result of the vehicle impact. No oil loss into any nearby drains. Ground fire at the base of the kiosk (small area), possible third party property damage to the fence adjacent to the substation due to fire and smoke. The occupants of the vehicle were taken to hospital prior to the fault crew arriving at the scene.
1378 | Powercor 17/63 | Powercor | 26/11/2017 | 0.6875 | -35.85244828 | 142.29081810 | 1175 Rosebery-Rainbow Rd., Beulah. | 32109148 | HSM003 | 12.7kV AC (SWER) | Rural Long | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 13508 | 20171127PWA_03 | A Powercor LSA crew attended a reported fire at the incident location. On arrival the crew found that a cactus bush centre runner had caused a HV conductor to break and fall to the ground starting a grassfire of approx 100 acres of private grass land. The CFA extinguished the fire, There were no reported injuries or other damage.
1379 | Powercor 17/64 | Powercor | 26/11/2017 | 0.098611 | -35.9405327 | 145.66951 | 146 (150) Pullar Rd., Cobram. | 33083463 | CME021 | Low voltage AC (<1kV) | Rural Short | - overhead service conductor (residential) | two phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13516 | 20171201PWA_01 | Vic Fire rang to advise of wire down and small grass fire at the incident location. On arrival the crew found a tree limb had damaged service wire resulting in a grass fire of approx. 2m X 10m A Vic Fire crew attended and extinguished the fire. There were no reported shocks or injuries.
1380 | Powercor 17/65 | Powercor | 28/11/2017 | 0.11875 | -38.07099243 | 144.22791481 | 1366 Midland Hwy (Cnr Bakers Bridge rd), Gheringhap. | 30266389 | GL015 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 13511 | 20171129PWA_01 | At 2:51am, emergency services reported conductor down across the road at the incident location. Attending crew found the red phase of steel conductor had broken between P71 (LIS-59813) and P1 (LIS-747554) resulting in a small ground fire/burns to the ground. The fire was approximately 3m long (100mm wide). The crew indicated the cause was a failed/deteriorated splice and conductor. The crew made the site safe and handed over to the daytime faults crew, who later replaced the damaged span. There was no third party damage or injuries reported.
1381 | Powercor 17/66 | Powercor | 28/11/2017 | 0.65625 | -36.02009792 | 145.3861068465576 | 1335 Boothroyds Rd., Numurkah (Katunga). | 32186418 | NKA006 | Low voltage AC (<1kV) | Rural Long | - overhead service conductor (residential) | two phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13517 | 20171204PWA_01 | Vic Fire rang to advise of a grass fire at the incident location. On arrival the crew found a tree had fallen onto service line straining connections in fuse box, this in turn caused arcing resulting in a grass fire of approx. 0.5HA. A Vic Fire crew attended and extinguished the fire. There were no reported shocks or injuries.
1382 | Powercor 17/67 | Powercor | 29/11/2017 | 0.58125 | -38.30334862 | 142.99422427 | 380 Erreys Rd., Cobrico. | 30305107 | TRG003 | 22kV AC | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 13514 | 20171130PWA_02 | Crew patrolling line in response to a feeder outage found vegetation had contacted the line resulting in some singing of the vegetation.
1383 | Powercor 17/68 | Powercor | 29/11/2017 | 0.83681 | -37.737793 | 144.807373 | 83 Millewa ave, St Albans. | 31024776 | SA005 | Low voltage AC (<1kV) | Urban | - fuse (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13515 | 20171130PWA_03 | Vic Fire rang to advise fuse has blown and caused grass fire at the incident location. On arrival the crew found at the cnr of Biggs St and Millawa Ave, St Albans on LIS 8958 red phase LV fused isolator had failed dropping debris on the ground resulting in a grass fire of approx. 2m X 10m on road reserve. A Fire crew attended and extinguished the fire.
1384 | Powercor 17/69 | Powercor | 29/11/2017 | 0.36736 | -37.76129189 | 144.24884438 | 400 Brisbane ranges Rd., Mt Wallace. | 31025054 | BMH003 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 13592 | 20180117PWA_03 | Emergency Services informed a fallen transformer on fire. On arrival the crew found that a Pole Fire had occurred at the incident location. The top part of this swer pole burnt through and fell on to ground. On arrival crew isolated supply and carried out repairs. There was no ground fire ,no injuries or third party property damage.
1385 | Powercor 17/70 | Powercor | 29/11/2017 | 0.87917 | -37.29687997 | 144.87627342 | 715 Kilmore Lancefield Rd., Forbes. | 33024727 | WND013 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | within electric line construction area | 19.8 | High | 0.5 | 9.9 | 13519 | 20171204PWA_03 | Customer advised of loud bang, no supply and small grass fire at the incident location. On arrival the crew found at an EDO fuse had operated resulting in a grass fire of approx. 300mm x 300mm but There were no reported shocks or injuries. There are no photos available. The crew replaced EDO fuse.
1386 | Powercor 17/71 | Powercor | 2017-04-12 | 0.82083 | -36.23895521 | 145.46512067 | 410 Victoria Rd., Tallygaroopna. | 33090222 | SHN011 | 22kV AC | Rural Long | - insulators | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13524 | 20171205PWA_02 | Following the recent storm events and a reclose on the SHTS-NKA No 1 line, a crew was asked to patrol 20 poles either side of the distance to fault that was recorded in the fault log. At P 109 SHTS-NKA No 2 line the crew found that a bird had flashed over an insulator, it had come to ground and started a ground fire of approximately 40 m X 6 m. On arrival crew assessed damage and arranged repairs. No third party damage or injury was reported.
1387 | Powercor 17/72 | Powercor | 2017-08-12 | 0.44792 | -36.01261938 | 144.55497197 | 174 Fulham Rd., Torrumbarry. | 33017122 | CHA005 | 22kV AC | Rural Long | - connector / termination | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 13538 | 20171219PWA_03 | The CFA reported a grass fire at the incident location. On arrival the crew found that a “T” Clamp had faulted at the incident location. The ground fire was approximately 100m X 250m. Damage was reported to the grassland only, no injury was reported. The crew made the site safe, and repaired the connection.
1388 | Powercor 17/73 | Powercor | 2017-10-12 | 0.44792 | -34.307208886941396 | 142.1562754404755 | 75 Nealie St., Cardross. | 33062189 | RCT023 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13525 | 20171212PWA_01 | Customer reported a “pole fire” and grass fire caused by Powercor assets at the incident location. On arrival the crew found that a FOLCB on a concrete pole had failed and ignited, the molten material falling to the ground and igniting a small area of grass at the base of the pole approximately 3m x 1m in size. CFA attended & extinguished the fire. There were no reported injuries, no 3rd party damage.
1389 | Powercor 17/74 | Powercor | 2017-12-12 | 0.85 | -36.24029417 | 142.39752350 | 23 Rainbow Rd., Warracknabeal. | 33050983 | HSM003 | Low voltage AC (<1kV) | Rural Long | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 13526 | 20171214PWA_01 | CFA reported sparking on a pole at the incident location. On arrival the crew found that a connection had overheated on a LV isolator causing hot debris to fall to the ground resulting in a ground fire (Approx. 30m x 40m) on private property. On arrival crew isolated supply and carried out repairs. There were no reported injuries or third party property damages.
1390 | Powercor 17/75 | Powercor | 13/12/2017 | 0.55208 | -36.27289156 | 143.35832119 | 3 Jenkins St., Charlton. | 30021640 | CTN005 | Low voltage AC (<1kV) | Rural Short | - overhead service conductor (residential) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 13528 | 20171214PWA_04 | The customer reported a wire down that had started a small fire at the incident location. On arrival the crew found that an LV neutral screened service cable had faulted. It caused a ground fire of approximately 2m X 2m. No damage or injury was reported. The crew made the site safe, and replaced the service.
1391 | Powercor 17/76 | Powercor | 13/12/2017 | 0.55833 | -38.39973047 | 143.88586762 | 36 Deans Marsh – Lorne Rd., Deans Marsh. | 33039995 | WIN011 | 22kV AC | Rural Long | - overhead conductor (insulated) | single phase | Started in or originated from a distribution system | within electric line construction area | 19.8 | High | 0.5 | 9.9 | 13529 | 20171215PWA_01 | Customer reported a grass fire near one of our poles. On arrival the crew found that the Insulated cable connected to the fuse unit had faulted. A fire of approximately 300 mm diameter was subsequently found at the base of the pole.
1392 | Powercor 17/77 | Powercor | 13/12/2017 | 0.43194 | -36.21554046 | 145.46509981 | Edwards Rd., (Cnr of McKenzie Rd), Tallygaroopna. | 33090074 | SHTS-NKA1 | 66kV AC | Unknown | - overhead conductor (bare; steel) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 13527 | 20171214PWA_02 | The CFA reported a grass fire at the incident location. On arrival the crew found that a hawk had flashed over on our HV assets, coming to ground and causing a ground fire. The ground fire was approximately 120m X 10m. Damage was reported to the grassland and fence line, no injury was reported. The crew found no damage to our assets.
1393 | Powercor 17/78 | Powercor | 14/12/2017 | 0.73472 | -36.54479311 | 144.93193440 | GEODETIC ROAD N, CARAG CARAG. | 30255374 | SHP021 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 13530 | 20171215PWA_06 | Crew attended to find small ground fire had been extinguished by local farmer on road verge area burnt 150 metres by 6 metres. Starling birds had caused a flashover on the concrete pole steel crossarm ACR structure, starting a small grass fire. No property damage, No injuries, No reported shocks. On arrival crew confirmed site safe - no damage to assets.
1394 | Powercor 17/79 | Powercor | 15/12/2017 | 0.75 | -37.58958757 | 143.75741380 | 4 Kingston Court, Smythes Creek. | 32007168 | BAS021 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 13537 | 20171218PWA_05 | Vic Fire reported a fire at the incident location. On arrival the crew found that an EDO fuse had operated. The barrel of the EDO fuse stayed in position without dropping down. The barrel then caught fire resulting in a ground fire (approx. 50 square metres) on the road reserve and private property. There were no reported injuries .
1395 | Powercor 17/80 | Powercor | 19/12/2017 | 0.52153 | -36.45755071 | 145.32567859 | 800 Toolamba Rd., Toolamba. | 32189917 | MNA034 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 13540 | 20171220PWA_03 | The CFA reported a grass fire at the incident location. On arrival the crew found that a HV Splice had faulted at Tee Pole 118 and the conductor had come to ground between Tee pole 118 and pole 1 causing a ground fire. On further inspection it was found that a bird had flashed over at pole 1 Waugh spur. Damage was reported to grassland only, no injury was reported.
1396 | Powercor 17/81 | Powercor | 20/12/2017 | 0.44097 | -36.12938359 | 144.55265119 | 1578 Mount Terrick Rd., Rosylnmead. | 32181340 | ECA012 | Low voltage AC (<1kV) | Rural Long | - overhead service conductor (residential) | two phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 13543 | 20171221PWA_03 | The CFA reported a grass fire at the incident location. On arrival the crew found that a tree had come over causing an LV service to come to ground and short out on a steel fence poSt., which in turn caused a ground fire of approximately 10m X 10m at the incident location. Damage was reported to the grassland only, no injury was reported.
1397 | Powercor 17/82 | Powercor | 20/12/2017 | 0.69167 | -35.51158350 | 143.88425762 | 691 Murrabit West Rd., Murrabait. | 33022802 | KGT003 | 12.7kV AC (SWER) | Rural Long | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | Very High | 1 | 1 | 13544 | 20171222PWA_01 | Crew attended to find pole had been extinguished by CFA in paddock. Crew found tree across SWER between pole # 1 and pole # 2 Murrabit West Spur. No property damage, No injuries, No reported shocks.
1398 | Powercor 17/83 | Powercor | 20/12/2017 | 0.74306 | -36.99440384 | 144.38380602 | 585 Jennings Rd., Sutton Grange. | 33029021 | CMN003 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 13545 | 20171222PWA_02 | Crew attended to find cable down between pole # 9 and pole # 10 Sutton Grange East Spur where an epicormics attached limb had dislodged and was blown across the HV Conductors . Estimated 50 acres of property burnt. No injurie, no reported shocks.
1399 | Powercor 17/84 | Powercor | 21/12/2017 | 0.79861 | -38.33854702 | 143.82442224 | 4100 Ripple Vale Cape Otway Rd., Birregurra. | 32062882 | WIN011 | 22kV AC | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started in or originated from a distribution system | within electric line construction area | 19.8 | Low-moderate | 0.2 | 3.96 | 13546 | 20171222PWA_03 | Customer reported a whirly wind had blown straw onto power lines at the incident location. On arrival the crew found that the straw had caused a flash over which in turn started a ground fire at the base of Ingleby P12 (LIS-7534) (approx. 16m2 in total). The fire self-extinguished due to the moist ground. A successful reclose occurred on the upstream ACR (@1703hrs). No injuries, no third party damage reported.
1400 | Powercor 17/85 | Powercor | 22/12/2017 | 0.675 | -36.73828668 | 144.15520 | 1229 Calder Highway, Marong. | 30147098 | BET001 | 22kV AC | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within electric line construction area | 19.8 | High | 0.5 | 9.9 | 13550 | 20180102PWA_02 | VicFire Reported a grass fire near the intersection of allies st Marong. Attending crew found branch had contacted HV and high voltage fuses had operated.
1401 | Powercor 17/86 | Powercor | 26/12/2017 | 0.88472 | -37.037680 | 143.47849 | 340 Avoca- Bealiba Rd., Rathscar. | 30020147 | MRO008 | Low voltage AC (<1kV) | Rural Long | - fuse (any other type) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 13551 | 20180102PWA_03 | VicFire Reported grass fire around the base of wood pole. The attending powercor crew found that a low voltage fuse box had malfunctioned.
1402 | Powercor 17/87 | Powercor | 26/12/2017 | 0.56667 | -34.190067 | 142.09628 | 85 Gibbs St., Mildura. | 33064015 | MBN012 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 13552 | 20180102PWA_04 | Powercor crew were patrolling line after reclose and found small fire in the vicinity of the line.
1403 | Powercor 17/88 | Powercor | 26/12/2017 | 0.61319 | -35.969852 | 145.63590 | 146 Healy Rd., Cobram. | 33087379 | CME015 | 22kV AC | Rural Short | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13553 | 20180102PWA_05 | Vicfire reported grassfire started by an EDO fuse falling to the ground at the intersection of Healy Rd and Cobram South Rd. Attending crew identified fault tamer fuse had mal-operated.
1404 | Powercor 17/89 | Powercor | 26/12/2017 | 0.5875 | -36.280125 | 145.42837 | 35 Zeerust Rd., Congupna. | 33093453 | SHN011 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13555 | 20180102PWA_06 | Powercor crew locating fault found that a tree had fallen, bringing down conductor and resulting in a small grass fire
1405 | Powercor 17/90 | Powercor | 29/12/2017 | 0.95972 | -34.6173058 | 142.7695 | 282 Crete Rd., Robinvale. | 33061544 | RVL001 | Low voltage AC (<1kV) | Rural Short | - overhead service conductor (residential) | two phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13558 | 20180102PWA_08 | Vic Fire reported grass fire and powerline down at intersection of Robinvale-Sea Lake Road and Crete Road Robinvale. Attending crew found service line to unoccupied house was on the ground and a small grass fire had occurred.
1406 | Powercor 17/91 | Powercor | 30/12/2017 | 0.60764 | -37.01383 | 143.11824 | 105 Rifle Butts Rd., Landsborough. | 33050264 | STL007 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 13560 | 20180102PWA_09 | Customer called to advise of a fire start at the above address. A crew attended and found a HV fuse tube malfunctioned, dropping hot material onto the ground, starting a ground fire of approx. 20m x 10m in area on private property. Customer extinguished fire.
1407 | Powercor 17/92 | Powercor | 2018-03-01 | 0.48264 | -36.4698470 | 145.08976181 | 623 Harston Rd., Harston. | 30126897 | SHP014 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13563 | 20180103PWA_03 | Emergency Services reported a grass fire that occurred two days ago at the incident location and possible cause was tree branches touching the power line. Upon arrival, the Powercor crew found that tree branches contacting the power line when there is a wind.
1408 | Powercor 17/93 | Powercor | 2018-04-01 | 0.45347 | -38.4383163 | 143.7394 | 170 Dewings Bridge Rd., Gerangamete. | 32065469 | CLC007 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 13597 | 20180105PWA_01 | VicFire report a grass fire start at the above location. A crew attended and found a bird had caused a flash - over igniting approximately 30m/sq of grass burnt in a private paddock. No injuries or damage to Powercor assets.
1409 | Powercor 17/94 | Powercor | 2018-06-01 | 0.62153 | -38.17365197 | 142.96592474 | 38 Wallaces Rd., Glenormiston South. | 30049396 | TRG001 | 22kV AC | Rural Short | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Extreme | 3.5 | 16.1 | 13564 | 20180108PWA_01 | Powercor protection equipment reclosed on a rural feeder, 3 minutes later the CFA control centre received a call advising of a grass fire start at the Wallace lane, Glenormiston south. Powercor assistance was offered but not initially required. Vicpol and CFA fire investigators to conduct investigation. A fire of some 31 Ha ensued. A crew was despatched following morning to confirm isolations and determine probable cause. The crew advises “Customer has lost about 50 acres caused by fire. Lost a old house, hay shed full of hay, silage, fence posts, hay stacked in paddock and one cow. At Wallace rd pole 1 SW 10819 we found a crow skeleton about 1.4m from the pole in the direction of the wind. Farmer across the rd heard a bang and looked towards switch pole and sore fire at bottom of pole just inside paddock which fits where bird skeleton is. Looked over SW pole and it all looks ok but it does have and old gac switch on it”. Supply to shed/s restored to provide water for livestock. There were no reported shocks or injuries. The fire was rapidly brought under control by 5 aircraft and 23 ground based units . Note image of crow taken by crew does not appear fresh, further discussion with fire investigators in progress to confirm cause.
1410 | Powercor 17/95 | Powercor | 2018-06-01 | 0.66181 | -36.73858512 | 144.15765856 | 1181 Calder HWY, Marong. | 30147096 | BET006 | 22kV AC | Rural Short | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within electric line construction area | 19.8 | Severe | 2 | 39.6 | 13572 | 20180110PWA_01 | During high winds tree branch's were blown onto HV conductors starting a small grass fire at the incident location. There were no reported shocks or injuries. The crew removed branches, replaced fuses and restored supply.
1411 | Powercor 17/96 | Powercor | 2018-06-01 | 0.80972 | -36.33843117 | 144.67353591 | 358 Restdown Rd., Rochester. | 32184954 | SHP012 | 22kV AC | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 13574 | 20180110PWA_02 | CFA reported a small grass fire at the incident location. On arrival the crew found at mid span from LIS 17037 trees making contact to HV resulting in a grass fire of approx. 100m x 100m, with damage to fencing & machinery. There were no reported shocks or injuries. The crew made safe/trimmed trees and restored supply.
1412 | Powercor 17/97 | Powercor | 2018-06-01 | 0.61111 | -38.46602585 | 144.08126531 | 1 Werona Rd., Fairhaven. | 33041158 | WPD014 | Low voltage AC (<1kV) | Rural Short | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Extreme | 3.5 | 0.7 | 13565 | 20180108PWA_02 | Vicfire reported a small grass fire at Fairhaven. On arrival the Powercor crew found the fire had been extinguished by local residents. An area of grass some 5 by 5 metres at the base of the substation pole was burnt. A ruptured copper to aluminium tee clamp connection was subsequently found and repaired. There were no reported shocks or injuries.
1413 | Powercor 17/98 | Powercor | 2018-06-01 | 0.82292 | -37.79910726 | 144.80462730 | 129A The Avenue, Sunshine West. | Pa0119174 | SU035 | Low voltage AC (<1kV) | Urban | - transformer (kiosk mounted) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Extreme | 3.5 | 0.7 | 13581 | 20180111PWA_05 | Customer reported a transformer fire at the incident location. On arrival the crew found that a kiosk substation had caught fire, resulting in a fire behind the closed doors of the kiosk substation. Protection operated. There were no reported injuries, no shocks, no ground fire, no HVI. The fence adjacent to the kiosk damaged due to the fire. Supply isolated. Repairs/replacement organised.
1414 | Powercor 17/99 | Powercor | 2018-07-01 | 0.12569 | -36.05109767 | 145.20580210 | 1 Kostadt St., Nathalia. | 33079710 | NKA002 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13575 | 20180110PWA_03 | An EDO Candled and burnt in Half at the incident location. On arrival crew carried out repairs and restored supply. There was no ground fire, no reported injuries or third party property damage.
1415 | Powercor 17/100 | Powercor | 2018-08-01 | 0.82569 | -35.76325969 | 143.93149776 | Loddon Valley Hwy corner of Murray Valley Hwy, Kerang. | 32029791 | KGT003 | 22kV AC | Rural Long | - pole (wood) | three phase | Started by lightning striking a distribution system or a part of a distribution system | HBRA only | 1 | Very High | 1 | 1 | 13579 | 20180111PWA_03 | Vic Fire reported pole fire at the incident location. On arrival the crew found a pole had been struck by lightning causing the transformer to fail and ignited a small grass fire. 10m x 10m. There were no reported shocks or injuries.
1416 | Powercor 17/101 | Powercor | 2018-08-01 | 0.94444 | -34.88611870 | 143.12723987 | Bolton - Kooloonong Rd., Bolton. | 32149634 | BBD014 | 12.7kV AC (SWER) | Rural Short | - pole (wood) | single wire earth return (SWER) | Started by lightning striking a distribution system or a part of a distribution system | HBRA only | 1 | Very High | 1 | 1 | 13576 | 20180110PWA_04 | Customer reported outage. Crew attended and found SWER pole had been struck by lightning and had burnt through at the base, falling to ground. There was a resulting ground fire start around the base of the pole of approx. 6mx6m. There were no reported shocks or injuries. Fire extinguished by crew. Pole replaced supply restored.
1417 | Powercor 17/102 | Powercor | 2018-09-01 | 0.83056 | 36.15737795 | 143.27268392 | 2112 CHARLTON-THALIA Rd., TEDDYWADDY WEST. | 32029041 | CTN003 | 22kV AC | Rural Long | - pole (wood) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very High | 1 | 4.6 | 13578 | 20180111PWA_02 | Vic Fire reported grass fire at the incident location but fire start was not initially thought to be connected to Powercor assets . On arrival the crew found damaged pole at 2112 Charlton-Thalia Rd Teddywaddy WeSt., LIS 602961, and another damaged pole at LIS 602320, Calder Highway Glenloth. The following day it was identified ( CFA investigation) that the fire start was related to Goanna at LIS 602961, starting a grass fire of approx. 100HA, damaging shedding & fencing and destroying an unoccupied dwelling. The crew made safe, replacing both poles. There were no reported shocks or injuries.
1418 | Powercor 17/103 | Powercor | 2018-10-01 | 0.90972 | 38.56623511 | 142.85991495 | Great Ocean Rd., Peterborough. | 30251713 | WBL012 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 13577 | 20180111PWA_01 | Customer called to report no supply, On arrival the Powercor crew found one strand of the steel conductor had unravelled and a fire of approximately 1 acre had occurred. On further inspection, the deteriorated carcass of a pelican was found near the conductor damage indicating that this may have previously initiated the conductor damage. Fire had been extinguished by CFA. There were no reported shocks or injuries. On arrival crew isolated supply and carried out repairs.
1419 | Powercor 17/104 | Powercor | 2018-10-01 | 0.48403 | -36.89827234 | 144.21426693 | 88 BICKFORDS Rd.,, RAVENSWOOD. | 30333711 | CMN003 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 13582 | 20180112PWA_01 | A contractor reported a crane had struck and pulled down wires at the above location. A crew attended and found a Franna crane had struck and broken one 22kV conductor and brought two others to the ground. This resulted in clashing conductors and a ground fire start btn P240 and P241A Harcourt S/L. CFA attended and extinguished fire of approx. 4 Acres in area. Damage was sustained to a number of trees and fences on private property. The site is a temporary works yard for C.P.B contractors who are constructing a new roundabout for VicRoads. The company who owns and operates the crane is Big Hill Cranes. The site supervisor for C.P.B advises the crane had just completed loading an item onto a semi with the help of a spotter. The crane operator then backed up to collect another load while the spotter was securing the load to the truck. The crane was still raised and back into the HV conductors. The crane operator lowered the boom and left the crane before the crew arrived. The ACR at Harcourt P82 reclosed and all three HV fuses at Harcourt P231 operated. Two fuses operated correctly but the third unit hung up. Pole 240, 241 and 241A all sustained damage. Crew made repairs and restored supply. Final conductor heights after repairs are 7.8m There were no reported shocks or injuries.
1420 | Powercor 17/105 | Powercor | 2018-11-01 | 0.047917 | -38.40279186 | 144.19091662 | 16 Wray St., Anglesea. | 30073092 | WPD021 | Low voltage AC (<1kV) | Rural Short | - fuse (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 13583 | 20180112PWA_02 | Vic Fire reported a transformer on fire at the incident location. Upon arrival, the Powercor crew found that an UG service fuse box on a pole caught fire and melted debris fell on to ground causing a small ground fire. There were no injuries. CFA attended. On arrival crew isolated supply and carried out repairs.
1421 | Powercor 17/106 | Powercor | 2018-11-01 | 0.69375 | -37.6819954 | 144.575531 | 24 Vista Drive, Melton. | 32178447 | MLN022 | Low voltage AC (<1kV) | Rural Short | - overhead conductor (bare; steel) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 13584 | 20180112PWA_03 | Report received from residents that a tent/gazebo had blown onto the wires outside their property, causing sparks. Upon arrival the fault crew found that a lightweight portable gazebo had in fact been swept up by the wind and blown into the open wire LV conductors. This caused the sparking and shorting between circuits which was reported by the residents, and eventually led to the red phase and neutral conductor to break mid span and come to ground, causing a small grass fire of (3m2) in the nature strip in front of 24 Vista Drive. The MFB were also in attendance and the small grass fire was extinguished. There was no reported third party property damage. No shock or injuries to report. On arrival crew isolated supply and carried out repairs.
1422 | Powercor 17/107 | Powercor | 2018-12-01 | 0.9125 | -36.34311262 | 145.19951820 | 1020 Lilford Rd., Gillieston. | 30128571 | SHTS-KYM1 | 66kV AC | Unknown | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 13587 | 20180115PWA_03 | Vic Fire reported a pole fire at the incident location. On arrival the crew found that a wood cross-arm had burnt through at the insulator pin causing the conductor to come adrift and rest on the cross arm. CFA extinguished the cross-arm fire, a controlled interruption on SHTS-KYM #1 was required. There was no ground fire, no reported injuries, no 3rd party damage, no protection operated. Note: incident location was advised as P171 by crew, upon investigation it was found that the pole fire location was in fact P172.
1423 | Powercor 17/108 | Powercor | 2018-12-01 | 0.53889 | -37.27639404 | 142.93347477 | 47 McNeill St., Ararat. | 32109235 | ART031 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13585 | 20180115PWA_01 | Customer advised loud bang at the incident location. On arrival the crew found, that HV conductor fell on to LV due to damaged cross arm. There was suspected HVI damage to around 10 houses. There was no ground fire or injuries reported.
1424 | Powercor 17/109 | Powercor | 13/01/2018 | 0.73611 | -35.383422731135546 | 142.18751449465572 | 54 Federation St., PATCHEWOLLOCK. | 32151382 | OYN005 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very High | 1 | 1 | 13586 | 20180115PWA_02 | Customers reported all supply fail and hearing nearby fire sirens at incident location. On arrival the crew found that a HV strain cross-arm had burnt through on P124 Patchewollock line on the footpath side causing HV conductor to fall onto the LV circuit below. CFA in attendance, to extinguish the cross-arm fire, but also the air conditioning unit in the adjacent Town Hall building which the embers from the burning cross-arm are believed to have entered, CFA have had to remove the evaporative unit to douse the roof cavity to extinguish the fire in the roof of the structure LEI ( BE Garraway ) advised damage due to HVI relatively minor with only 1 fridge found damaged @ #44 Federation St., the rest of the damage ( other than the town hall ) was loss of freezer stock at the general store and pub due to the lengthy outage duration. There were no reported injuries, go ground fire. Protection operated, Patchewollock P1A ACR tripped to lockout ( DMS case F-10974-B ), also LV HRC fuses at S/Stn “Yenolum Main 123” operated. Damage • 1x Westinghouse fridge at #44 Federation Street ( Melting ice / thawing food inside unit, confirming it was in operation prior to incident ) • Freezer stock losses at General Store • Freezer stock losses at Pub • Evaporative cooler / roof damage, carpet damage and possible other water damage at Town hall
1425 | Powercor 17/110 | Powercor | 14/01/2018 | 0.93472 | -37.11373917 | 144.05772420 | 16 Campbell St., Newstead. | 30031722 | CMN002 | 22kV AC | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13590 | 20180116PWA_02 | CFA reported a grass fire caused by Powercor assets at the incident location. On arrival the crew found that a possum had flashed over on a HV circuit which transitions from vertical to horizontal construction, causing the possum to fall to the ground and ignite a small grass fire, approximately 20M x 40M square was burnt. CFA extinguished the fire and reported the freshly deceased possum in the fire area. There were no reported injuries, no 3rd party damage, CMN002 feeder successfully reclosed. On arrival crew inspected assets no repairs required. Design check being initiated.
1426 | Powercor 17/111 | Powercor | 15/01/2018 | 0.48681 | -37.73423204 | 142.018555 | 40 Dickens St., Hamiton. | 30089969 | HTN004 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13591 | 20180116PWA_03 | A customer advised a loud bang and power outage at the incident location. On arrival the crew found that a HV cross arm caught fire and a part of arm fell on to ground. The fallen debris from the ignited arm caused very minor grass fire at the pole base. There was no injuries or third party property damage On arrival crew carried out repairs.
1427 | Powercor 17/112 | Powercor | 15/01/2018 | 0.46042 | -35.06809733 | 143.33548174 | 4077 Murray Valley Highway, Piangil. | 30100069 | SHL002 | 22kV AC | Rural Long | - capacity balancing units | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13589 | 20180116PWA_01 | Emergency Services reported a pole fire at the incident location. Upon arrival, the Powercor crew found 100*20 Sqm grass fire. There was a report of capacitor unit and transformer sparking at the incident location. The protection operated. CFA attended. There were no injuries. The crew was not able to find the direct cause of this grass fire. An investigation of the plant and equipment is underway.
1428 | Powercor 17/113 | Powercor | 15/01/2018 | 0.70278 | -36.29780290 | 145.22308033 | 1580 Tatura - Undera Rd., Undera. | 33096503 | KYM003 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13594 | 20180117PWA_02 | FA reported a grass fire caused by tree over powerlines at the incident location. On arrival the crew found that tree branch approximately 15M in length from outside the clearance space had failed and fallen over one phase of a 3 phase spur line. The conductor struck the fence igniting 2 ground fires 300 metres apart (140x 10 & 70 x 10 mtrs) . The conductor remained suspended in free air still alive. There were no reported injuries. On arrival crew isolated supply and carried out repairs.
1429 | Powercor 17/114 | Powercor | 16/01/2018 | 0.89306 | -37.55561594 | 143.97299788 | 57 Bungaree - Wallace Rd., Bungaree. | 32000693 | BAN011 | 22kV AC | Rural Long | - connector / termination | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 13596 | 20180118PWA_01 | VicFire reported a fire start in proximity of a Powercor asset at the incident location. A crew attended but were unable to identify possible cause of fire start. CFA attended and extinguished ground fire of approx. 20m x 10m in area. A crew attended the following day and identified an overheated connection. There were no reported shocks, injuries or third party property damages. The crew replaced the overheated connection.
1430 | Powercor 17/115 | Powercor | 17/01/2018 | 0.40139 | -37.84671700357965 | 144.72452705886076 | 8 Toritta Way, Truganina. | 30239859 | LV002 | Low voltage AC (<1kV) | Rural Short | - LV pillar | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13595 | 20180117PWA_04 | A customer advised a pillar box has been hit by a car at the incident location. The customer also reported the box on fire, which was extinguished by persons unknown. Upon arrival, the Powercor crew found that the UG pillar had been run over by a vehicle causing a small fire. There were no injuries or third party property damage. On arrival crew isolated supply and carried out repairs.
1431 | Powercor 17/116 | Powercor | 18/01/2018 | 0.0375 | 38.75095014 | 143.66329754 | 1/29 Murray St., Apollo Bay. | 30052457 | CLC007 | Low voltage AC (<1kV) | Rural Long | - fuse (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 13864 | 20180309PWA_01 | Crew reported FSD burnt out and had caught fire. Customers underground service burnt off. There was no ground fire, no reported injuries.
1432 | Powercor 17/117 | Powercor | 18/01/2018 | 0.59583 | -38.19268140 | 144.61133747 | 561 Anderson Rd., Drysdale. | 32083675 | DDL012 | 22kV AC | Rural Short | - fuse (powder filled) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very High | 1 | 1 | 13602 | 20180119PWA_01 | A passer-by reported something dropped from pole and started a grass fire at the incident location. Upon arrival, the Powercor crew found that a grass fire (approx. 3 acres area) in the vicinity of the pole. There were no injuries. The grass fire on a private property and it caused minor fire damage to fence. No other damage identified by the crew.
1433 | Powercor 17/118 | Powercor | 18/01/2018 | 0.99097 | -38.02332106 | 144.36538033 | 10 Fairway Drive, Lara. | 33044395 | FNS011 | 22kV AC | Rural Short | - fuse (powder filled) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very High | 1 | 1 | 13609 | 20180122PWA_03 | At approximately 11:30pm on 18/01/18, the CFA reported a pole had caused grass fire at the incident location. A crew was dispatched to investigate the incident. The attending crew found evidence of a small grass fire around substation pole 2 Fairway Drive (LIS-59510). The roadside LA on the pole was broken in half but remained attached to the pole. It was unknown what had caused this to occur. The roadside HV powder filled fuse had operated and fallen to the ground. The fire, totalling approximately 3m x 5m had been extinguished by the CFA and nearby resident. There was minor burns to a private fence post (10 Fairway Drive, Lara), however the fence appeared to remain intact (secure). Definitive cause of the fire is unknown, however it seems that fallen debris from either the blown powder filled fuse or the broken lightning arrestor may have been the ignition. Appropriate isolations were made and the site was made safe, the fault was handed to the day time crew for final repairs. 1 customer was left off supply for the remainder of the night.
1434 | Powercor 17/119 | Powercor | 19/01/2018 | 0.45208 | -36.35049097 | 141.63397215 | Corner of Western Hwy and Irwins Rd., Nhill. | 30077028 | NHL016 | 22kV AC | Rural Long | - surge diverter | three phase | Started in or originated from a distribution system | HBRA only | 1 | Severe | 2 | 2 | 13608 | 20180122PWA_02 | CFA reported a ground fire start near a Powercor pole at the incident location. CFA attended and extinguished fire. A crew attended and found an area of approx. 1acre burnt around the base of the pole. Protection operated. There were no reported shocks or injuries.
1435 | Powercor 17/120 | Powercor | 19/01/2018 | 0.83611 | -36.77244762 | 144.49577389 | 120 Sugarloaf Rd., Axedale. | 30266277 | BET005 | 22kV AC | Rural Long | - underground cable | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very High | 1 | 4.6 | 13612 | 20180122PWA_06 | Numerous Customers called reporting supply issues of partial supply. Powercor Employee Mark Kita also part of the local community and affected by the supply issues went for a quick patrol along the HV line and came across the HV Underground cable on a concrete pole burning at pole 5 Cochrane South Spur 120 Sugarloaf Road AXEDALE. Mark quick thinking doused the grass fire at the bottom of the pole. HV underground failed above the steel covers and cable head connections to overhead line. Crew attended and made isolations of the affected spur line and HV underground to restore supply to majority of customers. Small grass fire at base of the pole. No property damage, shock reports or injuries reported.
1436 | Powercor 17/121 | Powercor | 19/01/2018 | 0.78403 | -34.31273065 | 142.18653210 | 107 Jacaranda St., Red Cliffs. | 32140300 | RCT023 | Low voltage AC (<1kV) | Rural Long | - overhead service conductor (residential) | two phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 13611 | 20180122PWA_05 | Customer reported wire down at premise starting a small grass fire. Crew attended and found Black XLPE service mains cable had failed at the Point of Attachment and had fallen onto concrete footpath and scorched ground. There were no reported shocks or injuries or damages. On arrival crew isolated supply and carried out repairs.
1437 | Powercor 17/122 | Powercor | 19/01/2018 | 0.45208 | -36.31066129 | 145.36914379 | McCrakens Rd., Shepparton. | 33094747 | SHN021 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | Very High | 1 | 1 | 13607 | 20180122PWA_01 | A customer reported a burnt area of ground around a pole at the incident location. The customer requested a crew attended to inspect the substation pole. A crew attended and found an area approx. 25m x 25m burnt around the base of P70 Boulevard S/L. A dead magpie was found at the base of the pole. Crew suspect the bird had flashed over and fallen to the ground causing the fire start. This fire had occurred sometime previous to today. No damage to pole or third party assets. There were no reported shocks or injuries.
1438 | Powercor 17/123 | Powercor | 19/01/2018 | 0.45208 | -37.68551904 | 143.36498260 | Cnr Montgomery and Anderson St., Skipton.. | 33106473 | BAS021 | Low voltage AC (<1kV) | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 13753 | 20180208PWA_05 | A customer reported that a truck has struck a wire and the wire was on the ground and started a ground fire at the incident location. On arrival the crew found that a truck had contacted the LV mains conductors crossing Glenelg Hwy and causing a conductor to break and fall to the ground. There was a resulting ground fire start of approx. 1m/sq on road reserve. CFA attended. Following repairs, the final height was measured at 7.2m above the point of contact. There were no reported injuries or third party property damages.
1439 | Powercor 17/124 | Powercor | 20/01/2018 | 0.50833 | -37.98418959 | 143.34377289 | Corner of Four tree rd & Gnarpurt Rd., Lismore. | 30042226 | CDN004 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 13865 | 20180309PWA_02 | CFA reported a pole fire at the incident location. On arrival crew found HV crossarm burnt off. There was no ground fire, no reported injuries or third party property damage. On arrival crew isolated supply and carried out repairs.
1440 | Powercor 17/125 | Powercor | 20/01/2018 | 0.73819 | -35.92517450 | 145.49447536 | Mywee Rd., Strathmerton. | 30124251 | NKA003 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 13610 | 20180122PWA_04 | Customer Chris Scott at 50 Mywee Road Strathmerton call that trees were in contact with HV and had started a grass fire in Roadside Vegetation Plantation. Approximately 110 metres by 22 metres and another small 10 metres by 10 metres grass fire in road verge and into customers property. Property damage was some fencing and irrigation pipes. There were no reported injuriesCrew attended no operations on the network no loss of supply. Reported to Vegetation Manager who arranged for the trees in all three spans to be cut.
1441 | Powercor 17/126 | Powercor | 20/01/2018 | 0.71528 | -36.75451451 | 144.30396449 | 2 Harpin Place, East Bendigo. | 33032935 | BGO022 | Low voltage AC (<1kV) | Urban | - fuse (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 13614 | 20180123PWA_02 | Numerous customers called reporting no supply. Crew attended to LV Fused Disconnecting Box on Substation Pole # 6 Lloyd Solomon in Lloyd Street Bendigo East. LV Fuse had overheated and melted the box and fell to the ground resulting is causing a small grass fire at base of the pole. No property damage, shock reports or injuries reported.
1442 | Powercor 17/127 | Powercor | 21/01/2018 | 0.65556 | -37.58091435 | 143.84150245 | 901 Skipton St., Redan. | 30012689 | BAS034 | Low voltage AC (<1kV) | Urban | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13613 | 20180123PWA_01 | A Powercor crew attended a report of an All Supply Failure at the above location. On arrival the crew found that the white phase LV Isolator on the North Circuit of “Skipton-Cooke” substation had failed and molten metal had fallen to the group starting a small fire (4 x 2 metres) which self-extinguished. There was no injury, shock or third party damage. On arrival the crew replaced the damaged isolator and restored supply.
1443 | Powercor 17/128 | Powercor | 22/01/2018 | 0.10694 | -35.33931368 | 143.56095417 | 123 CURLEWIS STREET, SWAN HILL. | 32158229 | SHL008 | 22kV AC | Urban | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 13656 | 20180125PWA_02 | VicFire reported a pole fire at the incident location. On arrival, crew found that a candled fuse hanging up on SW#34828. There were no injuries and ground fire.
1444 | Powercor 17/129 | Powercor | 23/01/2018 | 0.5875 | -38.15320270 | 143.10695933 | 599 DARLINGTON-CAMPERDOWN Rd., BOOKAAR. | 33037204 | CDN006 | 22kV AC | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 13655 | 20180125PWA_01 | The CFA reported a fire at the incident location. On arrival the crew found that a bird had caused a flashover on a 22kV pole and fallen to the ground starting a grassfire of approx. 2 Hectares of mostly road reserve, with some private land burnt and fence damage. There were no injuries or other damage reported. The protection operated.
1445 | Powercor 17/130 | Powercor | 25/01/2018 | 0.47431 | -36.44109882 | 143.96782735 | 1789 BRIDGEWATER-SERPENTINE Rd., SERPENTINE. | 30027013 | EHK024 | Low voltage AC (<1kV) | Rural Long | - overhead conductor (bare; copper) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | within electric line construction area | 19.8 | High | 0.5 | 9.9 | 13684 | 20180129PWA_02 | CFA reports a car has hit a pole resulting in a grass fire at the incident location. Police also in attendance. A crew attended and found a high load had contacted and broken a low voltage conductor across a road, resulting in the conductor falling to the ground, starting a grass fire of 600sq/m on the road reserve, The high load vehicle did not stop. The crew isolated the LV supply and repaired the conductor. The 3 remaining LV conductor not broken in the incident measured a height of 5.6m at centre of road . There were no reported shocks or injuries. Note: Police advise witnesses saw a truck with a grain auger contact and break the conductor. Contact Serpentine Police on 5437 8318 for further detail.
1446 | Powercor 17/131 | Powercor | 28/01/2018 | 0.6 | -38.60302069 | 143.01630735 | 129 Currells Rd., Port Campbell. | 30045051 | TRG003 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very High | 1 | 4.6 | 13678 | 20180129PWA_01 | The CFA reported a grass fire which had possibly started due to trees being too close to powerlines. A crew was dispatched to investigate. The crew attended and confirmed a fire had occurred due to trees within close range to the road side conductor (2-3/2.75 ST/GZ) HV line between P4 (LIS-400219) and P5 (LIS-400220). The grass fire of approximately 10m x 60m in the road reserve had been extinguished prior to their arrival and the crew could make necessary repairs. The crew cut some branches back and made as safe as possible. They advised there were more trees in the same span which they could not reach which required trimming as soon as possible. The NAO reported this to the Vegetation Manager and Dispatch, a job was created for the trimming to take place later that night. The Escalation Manager was updated of the situation. The crew advised there was a small amount of damage to a customer’s fence. No protection operated. There were no reported shocks or injuries.
1447 | Powercor 17/132 | Powercor | 28/01/2018 | 0.60139 | -38.23871363 | 143.14135479 | 4 Shaw St., Camperdown. | 32059660 | CDN003 | Low voltage AC (<1kV) | Urban | - overhead service conductor (residential) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 13698 | 20180129PWA_04 | The CFA reported a grass fire which had possibly started due to powerlines. A crew was dispatched to investigate. The crew attended and confirmed a 5m x 7m ground fire had occurred outside 3 Shaw St around the base of LV pole (LIS-422531). It was identified that the neutral screen service to # 4 Shaw St had failed, leaving the customer with no power. There was a loose neutral connection on (LIS-422531) which may have contributed to the fault. There were no obvious signs of how the fire started, however the crew suggested that fault current in the failed service at the loose connection may have caused a spark to fall to the ground, igniting the fire. The neutral screen service cable and connection was sent to Warrnambool depot, to be forwarded to the failed asset team in Ballarat. No protection operated. There were no reported shocks or injuries. No further damage identified.
1448 | Powercor 17/133 | Powercor | 28/01/2018 | 0.82292 | -38.2684021 | 144.521988 | 73-75 Dare St., Ocean Grove. | 32071761 | DDL023 | Low voltage AC (<1kV) | Rural Short | - fuse (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 13710 | 20180130PWA_01 | The CFA reported a ground fire had occurred at the incident location. A crew was dispatched to investigate. The crew attended and found an FSD had burnt out and fallen to the ground. This had caused scattered burns to the ground totalling approximately 1m x 1m. The CFA had left site before the crew arrived. The FSD was a substation bus fuse for “Presidents Terrace P61” S/S pole. The crew made appropriate repairs and the site safe. There were no reported shocks or injuries. No further damage identified.
1449 | Powercor 17/134 | Powercor | 28/01/2018 | 0.82292 | -38.20741342 | 144.30270706 | 23-29 Ghazeepoore Rd., Waurn Ponds. | 32084727 | WPD031 | Low voltage AC (<1kV) | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 13725 | 20180131PWA_01 | The CFA reported a ground fire had occurred at the incident location. The report from the CFA was that the fire had started from a blown fuse. A crew was dispatched to investigate. The crew attended and found evidence of a ground fire totalling approximately 1m x 3m. They advised the cause was likely falling debris from an overheated LV copper-aluminium clamp. The CFA was not onsite when the crew arrived. The crew performed appropriate repairs and made the site safe. There were no reported shocks or injuries. No further damage identified.
1450 | Powercor 17/135 | Powercor | 29/01/2018 | 0.89375 | -38.04156823 | 142.81945467 | 412 MORTLAKE-ARARAT Rd., MORTLAKE. | 32061375 | TRG002 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 13873 | 20180315PWA_01 | Report from Vic Fire of pole fire at incident location. On arrival crew found crossarm burnt off. There was no ground fire , no reported injuries and no third party property damage.
1451 | Powercor 17/136 | Powercor | 29/01/2018 | 0.64583 | -36.29199490 | 145.39933881 | 385 SHEPPARTON-ZEERUST Rd., ZEERUST. | 33093573 | SHN011 | 22kV AC | Rural Long | - insulators | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 13724 | 20180130PWA_08 | Vic Fire reported grass fire at base of pole # 84. On arrival the crew found evidence of a flashover on a 22kV insulator that has had damage to one of the sheds on the insulator which will need to be replaced. Crew found a “raven or crow” at base of pole that was burnt along with approx. 100m x 5m of burnt grass in road reserve. Crew arrange a fault follow up to repair insulator. Also a small amount of damage was noticed on the fence adjacent to the road reserve. ESV notified. No shock or injuries.
1452 | Powercor 17/137 | Powercor | 29/01/2018 | 0.82292 | -37.6757431 | 144.544 | 94 Westlake Drive, Melton West. | 34031832 | MLN022 | Low voltage AC (<1kV) | Rural Short | - LV pillar | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 13726 | 20180131PWA_02 | Customer reported a fire incident at an LV pillar in front of No. 94 Westlake Drive Melton 3337. The fire brigade was called and attended to the fire. There were no reported injurieThere was no ground fire.
1453 | Powercor 17/138 | Powercor | 30/01/2018 | 0.22708 | -36.22941927 | 140.99669386 | SERVICETON NORTH-TELOPEA DOWNS Rd., SERVICETON. | 32120511 | NHL031 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very High | 1 | 1 | 13785 | 20180207PWA_01 | A crew attended an outage at the incident location. On arrival the crew found that a pole fire had occurred on a 22kV pole which burnt the top of the pole. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. There was No ground fire start, no reported injuries or third party property damage.
1454 | Powercor 17/139 | Powercor | 2018-03-02 | 0.50069 | -36.12977543 | 145.04245073 | 116 Hutchins Lane, Kotupna. | 32193175 | KYM004 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 13784 | 20180206PWA_01 | Vicfire reported grassfire started by a HV wire falling to the within private property, fire brigade were onsite as well as police. Upon arrival crew found that the fire had been extinguished and that the CFA were still onsite. Linesmen confirmed that the fire was indeed started by a HV wire falling to the ground (the wire was broken by a falling tree branch). Only one wire of the single phase line was broken. The fire was approximately 3-4acres in area (fire burnt in private property). The fire burnt between LOWBAR P3 (LIS-17394) (Northern pole) and LOWBAR P4 (LIS-17395) (Southern pole). Repair works consisted of approx. 250m of 3/12 steel being replaced as the steel that had lay on the ground in the fire had the galvanisation burnt off it. A couple of HV arms initially appeared to be twisted due to the force of the branch falling on the wire however these pulled back into placed once the new conductor was sleeved in. Restoration time was about 13:30 with only one customer on LOBAR S/L remaining off for slightly longer than the other customers. There was no private property damage sustained , no injuries, no reported shocks. Isolation was made at WYUNA P6 ACR.
1455 | Powercor 17/140 | Powercor | 2018-06-02 | 0.66181 | -37.72638 | 142.0239 | 93 Park St., Hamilton. | 30094546 | HTN004 | Low voltage AC (<1kV) | Rural Long | - overhead service conductor (residential) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 13788 | 20180207PWA_04 | Vicfire reported a wire down and sparking at the incident location. On arrival the crew found that a neutral screen service had failed near the POA and fallen to the ground starting a grassfire of approx. 2 square metres of the customer’s front lawn. There were no injuries or other damage reported. On arrival crew isolated supply and carried out repairs.
1456 | Powercor 17/141 | Powercor | 2018-07-02 | 0.94306 | -36.20614661 | 144.61686941 | 72 Bamawm Rd., Bamawm Extension. | 33084014 | ECA012 | 22kV AC | Rural Long | - insulators | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 13789 | 20180209PWA_01 | Emergency services reported grass fire possibly started by Powercor assets, requested Powercor attend. Upon arrival crew found that there had been a flashover on the t-off arm on P153 BAMAWM RD LIS-28004. Crew recovered remains of bird from the arm. The bird had flashed across the 5 shed bridging insulator on the t-off arm. No damage to private assets or Powercor assets was sustained.
1457 | Powercor 17/142 | Powercor | 2018-08-02 | 0.68056 | -37.73943820 | 144.82224900 | 2 Biggs St., St Albans. | 32175211 | SA005 | Low voltage AC (<1kV) | Urban | - fuse (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13791 | 20180212PWA_01 | VicFire reported a Fire outside 2 Biggs St., St Albans. Upon arrival the crew had found that the POA/FOLCB at incident location, had failed and caused the POA/FOLCB to melt and burn away, approximately 6-7 inches of the customers mains had also been damaged and burnt as a result of this incident. The resultant hot melted plastic from the POA/FOLCB above had fallen onto the grassed front yard/lawn below causing a very-minor grass fire within the front yard of approximately 0.5m² total area. The MFB attended site and the grass fire was extinguished. There was no reported injury or shocks as a result of this incident.
1458 | Powercor 17/143 | Powercor | 2018-09-02 | 0.79028 | -36.37988138 | 145.41534968 | 34 - 36 Byass St., Shepparton. | 33093066 | STN013 | 22kV AC | Urban | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 13793 | 20180212PWA_02 | CFA reported pole fire at corner of Bypass St and Lockwood Road. (SPC) Upon arrival crew found that the fire had been extinguished. The small fire approx. 3m² was in nature strip around the base of LIS-2698 HV SW# 21825 conc pole. Crew found that there had been evidence of a flashover between the LA on the HV cable head and the HV screen on the centre phase.
1459 | Powercor 17/144 | Powercor | 2018-11-02 | 0.99167 | -38.47640461 | 143.75054598 | 1724 BIRREGURRA-FORREST Rd., BARWON DOWNS. | 33039489 | CLC007 | 22kV AC | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 13798 | 20180214PWA_02 | Powercor received a call from VicFire reporting a grass fire caused by a pole fire at 1724 Forrest Rd., Barwon Downs. When crews arrived at the incident site, they found a deceased possum on the ground at the base of the pole., located on the road reserve. A small ground fire (35m x 15m) near the base of the pole had been extinguished by the CFA. No conductors fell to ground. No electrical asset damage was found. No other third party property damage was reported. No injuries were reported.
1460 | Powercor 17/145 | Powercor | 13/02/2018 | 0.73819 | -37.75753376 | 144.83555748 | 96 Munro Avenue, Sunshine North. | 30245830 | SSE012 | 22kV AC | Urban | - overhead conductor (ABC) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13802 | 20180215PWA_01 | Upon arrival the crew had found that the 185mm 3/C HVABC at HV Pole LIS-727309 had failed, resulting in a flashover, the resultant sparks from the failed HVABC have fallen onto the nature strip grassed area below causing a grass fire of approximately 6m x 2m. The crew has advised that upon arrival the grass-fire had self-extinguished. There was no reported HVI, injury or shocks as a result of this incident.
1461 | Powercor 17/146 | Powercor | 13/02/2018 | 0.86319 | -36.85650627 | 144.19975889 | 74 BELVOIR PARK Rd., RAVENSWOOD. | 32014982 | BET004 | 22kV AC | Rural Short | - fuse (boric acid) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 13801 | 20180214PWA_05 | A customer reported sparking at top of pole behind their house. Upon arrival @21:30:00 crew found that a BA fuse had candled on the T/Pole at the incident location. There was no ground fire, no injuries or third party property damage.
1462 | Powercor 17/147 | Powercor | 15/02/2018 | 0.54514 | -35.95156457 | 145.68240072 | 3186 MURRAY VALLEY HIGHWAY, COBRAM. | 30143478 | CME021 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13811 | 20180216PWA_03 | CFA reported a grass fire at the incident location. On arrival the crew found that a branch had blown onto the HV fuses at P1 Wyatt Spur in high winds, it subsequently came to ground and caused a ground fire at the incident location. The ground fire was approximately 20m X 40m. Damage was reported to the grassland only, no injury was reported. The crew made the site safe, and inspected the HV fuses for damage.
1463 | Powercor 17/148 | Powercor | 15/02/2018 | 0.55208 | -38.23218392 | 141.44966090 | 1901 PORTLAND-NELSON Rd., GORAE WEST. | 32129434 | PLD003 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 13810 | 20180216PWA_02 | The CFA reported a grass fire at the incident location. On arrival the crew found that a crossarm had caught fire which also resulted in a ground fire at the incident location. The ground fire was spread across approximately 1.5 acres. Damage was reported to the grassland only, no injury was reported. The crew made the site safe, and replaced the crossarm.
1464 | Powercor 17/149 | Powercor | 16/02/2018 | 0.58403 | -37.68935646 | 144.60304998 | 66 HIGH STREET, MELTON. | 30112318 | MLN021 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13948 | 20180409PWA_01 | During feeder patrol crew located pole fire outside 66 High St. Melton. A HV termination crossarm had broken as a result of a pole fire. There was no ground fire, no reporteed injuries or third party property damage.
1465 | Powercor 17/150 | Powercor | 16/02/2018 | 0.15278 | -37.6301765 | 144.067947 | 847 yendon - egerton Rd., Millbrook. | 32007089 | BAN011 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 13817 | 20180219PWA_01 | A call was received from the customer at 847 Yendon-Egerton Rd., Millbrook that an explosion had occurred on the pole out the front of the above property. On arrival the crew found that a X-arm Fire had occurred on Millbrook Pole 82. The X-arm had burnt through where the EDO fuse unit mounts to the X-arm. Protection operated as expected
1466 | Powercor 17/151 | Powercor | 17/02/2018 | 0.72361 | -35.863382 | 145.58724 | TORGANNAH Rd., KOONOOMOO. | 32181198 | NKA005 | Low voltage AC (<1kV) | Rural Short | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 13819 | 20180220PWA_02 | CFA reported a grass fire near Powercor assets at the incident location. On arrival the crew found that a LV isolator overheated, dropping burning materials to the ground and igniting a grass fire around the base of the substation pole, approximately 10 metres square was burnt.
1467 | Powercor 17/152 | Powercor | 18/02/2018 | 0.24097 | -36.70819163 | 144.24277605 | 132 Sailors Gully Rd., Sailors Gully rd. | 30030467 | EHK024 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13833 | 20180223PWA_08 | Vic Fire reported a pole fire at the incident location. On arrival the crew found that a wood cross-arm had burnt through at the insulator pin causing the conductor to come adrift and hang by the bridge. There was no sign of the HV conductor making contact with the LV circuit below. CFA extinguished the cross-arm fire, a controlled interruption was required. There was no ground fire, no reported injuries, no 3rd party damage, no protection operatedNote: the initial report from the CFA suggested that nearby vegetation was ignited, there was no evidence on site to support this statement.
1468 | Powercor 17/153 | Powercor | 18/02/2018 | 0.80347 | -34.18444722 | 142.19304039 | 15 Benetook Ave, Mildura. | 30099309 | MDA024 | 22kV AC | Urban | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 13820 | 20180220PWA_03 | Customer reported dim lights and a load bang at the incident location. On arrival the crew found that tree branch from a nearby tree (outside clearance space ) was blown onto single phase transformer, landing between the HV bushings and surge diverters. The branch began to burn due to electrical tracking, dropping burning material to the ground, a grass fire approximately 3m square resulted at the base of the pole.
1469 | Powercor 17/154 | Powercor | 18/02/2018 | 0.49097 | -35.81807415 | 142.13220835 | 570 Whites Rd., Rainbow. | 320898781 | NHL015 | 12.7kV AC (SWER) | Rural Long | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any other thing forming part of or coming into contact with a distribution system | HBRA only | 1 | Very High | 1 | 1 | 13818 | 20180220PWA_01 | Vic Fire reported that a tractor towing a grain auger had contacted the SWER line as 570 Whites Rd., Rainbow. On arrival the crew found that farmer towing a grain auger had contacted the SWER line between Poles 32 and 33 Nandemarriman Spur line. The contact resulted in a fire that burnt approx. 0.1 hectares of stubble paddock and also destroyed the tractor. Minor damage was sustained to the conductor. At the point of contact the conductor height was measured at 7.4 metres. The crew isolated supply and carried out repairs. The driver of the tractor reported receiving a minor shock when he jumped off the tractor. The crew advised him to seek a medical assessment. The driver Patrick White attended the local hospital later in the day for checks.
1470 | Powercor 17/155 | Powercor | 19/02/2018 | 0.29792 | -36.74803508 | 144.28811743 | 125 BRIDGE STREET, BENDIGO. | 30025745 | EHK033 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 13847 | 20180227PWA_02 | A passer-by reported a pole fire at the incident location. On arrival the Powercor fault crew found that the HV cross am and pole top slightly burnt through. There was no ground fire, no reported injuries or third party property damage. On arrival crew isolated supply and carried out repairs.
1471 | Powercor 17/156 | Powercor | 19/02/2018 | 0.61389 | -36.27880941 | 144.77413771 | ECHUCA-NANNEELLA Rd., NANNEELLA. | 30122451 | KYM001 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 13822 | 20180221PWA_01 | Customer reported a low conductor at the incident location. On arrival the crew found that a wood cross-arm had burnt through at the kingbolt through to the insulator pin on one side causing the conductor to come adrift and hang approximately 5.0m above the ground, the other phase was still attached to the pole via the cross-arm strap. There was no ground fire, no reported injuries, no 3rd party damage, no protection operated. Note: The cross-arm fire was believed to have occurred on the night of the 18th of February, not discovered till the following day by the customer making the report. The crew were questioned about the conductor height and advised it was still 5.0m above the ground, not within reach as the reporter indicated.
1472 | Powercor 17/157 | Powercor | 19/02/2018 | 0.29097 | -36.74813724 | 144.26915259 | 32 BANNERMAN STREET, BENDIGO. | 32040059 | BET002 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 13834 | 20180223PWA_09 | Vic Fire reported a pole fire at the incident location. On arrival the Powercor fault crew found that a HV cross am and pole top had slightly burnt through. There were no injuries, HVI or ground fire.
1473 | Powercor 17/158 | Powercor | 20/02/2018 | 0.99167 | -37.65400531 | 142.30651809 | 45 Cavendish Rd., Dunkeld. | 33058547 | HTN005 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very High | 1 | 4.6 | 13823 | 20180221PWA_02 | The CFA reported a grass fire at the incident location. On arrival the crew found that a grass fire (10x10m) had been extinguished by the CFA. Fire started at the base of the pole, flash marks observed on the LV buckram strap. No damage, no injuries were reported. The crew made the site safe, and inspected all connections on the pole. Earth fault targets were present on the upstream auto sectionaliser but did not cause any prot to operate.
1474 | Powercor 17/159 | Powercor | 21/02/2018 | 0.83125 | -35.88529941 | 144.23161251 | 90 HORFIELD SCHOOL Rd., HORFIELD. | 33022765 | CHA005 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 13824 | 20180223PWA_01 | CFA reported a grass fire caused by Powercor assets at the incident location. On arrival the crew found that a bird had flashed over on the bypass switch on load side of an ACR pole, causing the bird to fall to the ground and ignite a small area of grass commencing at the base of the pole and running along a roadside drain, approximately 10m x 60m square was burnt. CFA attended and extinguished the fire. There were no reported injuries, no 3rd party damage, Hawken P1 ACR successfully reclosed.
1475 | Powercor 17/160 | Powercor | 22/02/2018 | 0.91875 | -36.61544152 | 142.42896795 | 1976 WIMMERA HIGHWAY, MURTOA. | 30085231 | HSM001 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 13829 | 20180223PWA_06 | VicFire reported a pole fire at the incident location. On arrival the crew found that the wooden crossarm and pole top assembly required replacement due to fire damage. There was no ground fire, no reported injuries or third party property damage.
1476 | Powercor 17/161 | Powercor | 22/02/2018 | 0.90764 | -36.76572166 | 141.10013723 | 7894 NATIMUK-FRANCES Rd., NEUARPURR. | 32091284 | HSM004 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 13828 | 20180223PWA_05 | VicFire reported a pole fire at the incident location. On arrival the crew found that the wooden pole and crossarm required replacement due to pole top fire damage. There was no ground fire, no injuries or third party party property damage.
1477 | Powercor 17/162 | Powercor | 22/02/2018 | 0.41389 | -37.59714186 | 143.76861697 | 679 GLENELG HIGHWAY, SMYTHES CREEK. | 33000200 | BAS021 | 22kV AC | Rural Long | - fuse (boric acid) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 13827 | 20180223PWA_04 | A number of customers reported voltage issues beyond P1 Bells Rd., Smythes Creek. On arrival the crew found a HV boric acid fuse had hung up and burnt through. This caused a ground fire in two spots of approximately 1m square and 2m square. Damage was reported to the grassland only, no injury was reported. The crew made the site safe, and the HV fuse was replaced.
1478 | Powercor 17/163 | Powercor | 23/02/2018 | 0.40208 | -36.41122171 | 142.48413189 | 790 KEWELL EAST Rd., KEWELL. | 30226897 | HSM005 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Severe | 2 | 2 | 13835 | 20180223PWA_10 | Customers called to advise of an outage and a pole fire that had occurred at the above location. A crew attended and found there had been a pole fire at P34A Kellalac east S/L. Protection operated. CFA did not attend. Customer extinguished fire. Ground fire start of approx.2sq/m on private property. There were no reported shocks or injuries.
1479 | Powercor 17/164 | Powercor | 23/02/2018 | 0.19097 | -37.74349719 | 142.02819907 | 1237 French St., Hamilton. | 32126397 | HTN005 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 13878 | 20180315PWA_06 | Emergency services reported a pole on fire. On arrival the attending crew found the wooden HV cross-arm on pole 47 had ignited at the king bolt and burnt the pole top and cross-arm. There was no ground fire. There were no reported shocks or injuries.
1480 | Powercor 17/165 | Powercor | 25/02/2018 | 0.59931 | -37.39842951 | 143.94647264 | 135 KINGSTON Rd., KINGSTON. | 32001388 | BAN009 | Low voltage AC (<1kV) | Rural Long | - overhead conductor (bare; copper) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 13846 | 20180227PWA_01 | Customer reported a small ground fire at the incident location. On arrival the crew found that an elm tree branch had come down in windy conditions and contacted a 3 phase open wire low voltage line. There was a small ground fire of approximately 3m². There were no injuries.
1481 | Powercor 17/166 | Powercor | 26/02/2018 | 0.78472 | -37.74718873 | 144.57146880 | 1243-1257 EXFORD Rd., EXFORD. | 30142925 | MLN011 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 13915 | 20180327PWA_05 | Report received from a motorist driving along Exford Rd towards Eynesbury of a line that had come down; not disconnected but hanging low in the paddock. Upon arrival the fault crew found that at LIS-936380 the outer section of the 3-phase HV wood crossarm had burnt through. The outer phase HV conductor falling to within 1.5m-2.0m of the ground. Supply remained alive and no protection operated as a result of the incident, and apart from the burnt crossarm, there was no further damage sustained to the pole or the HV conductor. There was no asset fire/ground fire, shock or third party damage to report.
1482 | Powercor 17/167 | Powercor | 28/02/2018 | 0.77708 | -37.88152012 | 142.97343112 | 1316 DARLINGTON-NERRIN Rd., DUNDONNELL. | 30047629 | CDN006 | 22kV AC | Rural Long | - fuse (boric acid) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very High | 1 | 4.6 | 13854 | 20180301PWA_03 | Customer reported information about a potential cause of an outage and that “a transformer had arced out caused a fire but has now been put out”. On arrival the attending crew found a HV fuse had mal-operated . Parts of the fuse barrel had fallen to the ground and there was a fire of some 150m x 6m on the road reserve. There were no reported shocks or injuries. Crew advised that they also suspect there was an internal fault in the transformer.
1483 | Powercor 17/168 | Powercor | 28/02/2018 | 0.61181 | -38.50696204 | 142.93408879 | BOUNDARY Rd., TIMBOON WEST. | 30255711 | TRG005 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very High | 1 | 4.6 | 13852 | 20180301PWA_01 | Emergency services reported power lines down and had possibly caused a fire. On arrival the attending crew found a tree had broken brought down 3 HV conductors between poles 35 and 36 of the Peterborough line. There was a fire of some 200 by 20 m on private property. Crew advise large gum tree broke approximately 1 metre above the ground during high winds. Unclear if tree is on private property or unused road reserve. There were no reported shocks or injuries.
1484 | Powercor 17/169 | Powercor | 28/02/2018 | 0.64514 | -36.76123879 | 144.28797682 | MUNDY STREET, BENDIGO. | 33017852 | BGOEHK | 66kV AC | Unknown | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 13856 | 20180302PWA_01 | 66Kv Feeder CB for BGO EHK 66Kv Feeder dropped off BGO Zone Substation 22KV feeders. Line patrol found tree in contact with 66Kv at Pole # 22 LIS # 413178 in gusty wind in VLine Reserve near the corner of Mundy and McLaren Streets BENDIGO. Ground fire 15 Metres X 8 Metres. No shocks, No third party damage.
1485 | Powercor 17/170 | Powercor | 28/02/2018 | 0.5625 | -38.09026 | 144.264481 | 35 CULLINAN Rd., BATESFORD. | 33043550 | GL015 | Low voltage AC (<1kV) | Rural Long | - fuse (any other type) | single phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very High | 1 | 4.6 | 13964 | 20180411PWA_03 | A customer reported that their lights are flickering and a smell is coming from the supply box at the incident location. On arrival the fault crew found that a loose connection had caused heating of the fuse connection resulting in charring of the meter panel. On arrival crew isolated supply and replaced meter board. There was no ground fire and no injury as a result of this incident.
1486 | Powercor 17/171 | Powercor | 2018-01-03 | 0.58194 | -38.16516189 | 144.41690544 | 2415 PORTARLINGTON Rd., BELLARINE. | 30076493 | GLE031 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13921 | 20180328PWA_03 | A passer-by reported an insulator hanging down. On arrival the crew found that a HV crossarm had burnt through and the insulator had let go from the crossarm. There was no ground fire, no third party damage or injury was reported.
1487 | Powercor 17/172 | Powercor | 2018-01-03 | 0.25764 | -37.86679552 | 144.82511519 | 36 ROMAWI STREET, ALTONA. | 30107670 | AL012 | 11kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13918 | 20180328PWA_01 | Vic Fire reported a pole fire at the incident location. On arrival the crew found that a pole and HV crossarm had caught fire. There was no ground fire, no reported injuries or third party property damage.
1488 | Powercor 17/173 | Powercor | 2018-01-03 | 0.35625 | -37.72607636 | 144.81573257 | 12 TARELLA DRIVE, KEILOR DOWNS. | 30111815 | SA006 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13920 | 20180328PWA_02 | Customer reported an insulator hanging down. On arrival the crew found that a HV crossarm had burnt through and the insulator had let go from the crossarm. There was no ground fire, no third party damage or injury was reported.
1489 | Powercor 17/174 | Powercor | 2018-01-03 | 0.29861 | -37.88609438 | 144.77766417 | 46 EDWARDS DRIVE, ALTONA MEADOWS. | 30116799 | LVN022 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13917 | 20180327PWA_07 | A customer reported that there is a pole on fire at the incident location. On arrival the fault crew found that the roadside fog insulator and end of the wooden cross-arm had burnt through causing the cross-arms to fail at the incident location. There was no ground fire and no injury as a result of this incident.
1490 | Powercor 17/175 | Powercor | 2018-01-03 | 0.29861 | -37.88348963 | 144.77883397 | 16 EDWARDS DRIVE, ALTONA MEADOWS. | 30116842 | LVN022 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13916 | 20180327PWA_06 | A customer reported that there is a pole on fire at the incident location. On arrival the fault crew found that the roadside fog insulator and end of the wooden cross-arm had burnt through causing the cross-arms to fail at the incident location. There was no ground fire and no injury as a result of this incident.
1491 | Powercor 17/176 | Powercor | 2018-02-03 | 0.59722 | -37.68319177 | 144.48853779 | 735 BACCHUS MARSH Rd.,, MERRIMU. | 30116368 | BMH006 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 13857 | 20180305PWA_01 | Employee reports a broken HV Xarm at P84 Melton line. Xarm burnt though at king bolt and hanging from pole by bridges. On arrival crew isolated supply and carried out repairs. No ground fire sta There were no reported shocks or injuries.
1492 | Powercor 17/177 | Powercor | 2018-02-03 | 0.98958 | -35.98026038 | 142.91278334 | 13 MORRISON STREET, BIRCHIP. | 32018655 | CTN001 | Low voltage AC (<1kV) | Rural Long | - insulators | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13859 | 20180305PWA_02 | CFA advised pole fire outside 13 Morrison St – Birchip. Upon arrival crew found that an LV bushing cover had melted and had fallen to the ground at incident location. The melted bushing had caused a 1m² grassfire at the base of the pole. There was no shock, no injury, no damage to private property. On arrival crew isolated supply and carried out repairs.
1493 | Powercor 17/178 | Powercor | 2018-02-03 | 0.29583 | -37.94144240 | 144.70887774 | 749 Duncans Rd., Werribee South. | 30112650 | WBE034 | 22kV AC | Rural Short | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 14051 | 20180514PWA_01 | Reported pole fire at incident location. There was no ground fire, no reported injuries or third party property damage.
1494 | Powercor 17/179 | Powercor | 2018-02-03 | 0.38194 | -35.08197575 | 142.17059948 | GALAH NORTH Rd., OUYEN. | 32145208 | OYN001 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 14052 | 20180514PWA_02 | Pole fire reported at incident location. There was no ground fire, no reported injuries or third party property damage.
1495 | Powercor 17/180 | Powercor | 2018-03-03 | 0.58542 | -37.42247150 | 142.85688994 | 7507 MORTLAKE-ARARAT Rd., MAROONA. | 33054332 | ART033 | 22kV AC | Rural Long | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very High | 1 | 4.6 | 13861 | 20180306PWA_01 | Emergency Services reported a grass and scrub fire at the incident location. On arrival the attending crew found a HV Flex on the white phase had failed causing it to flash over on the blue phase. The result has caused two grass fires, one 20 mtrs x 75 mtrs and the second 5 mtrs x 5 mtrs both in the road reserve and customers property which had been extinguished by the CFA prior to Powercor attendance . There were no reported shocks or injuries. The crews replaced the Blue and White phase Flex’s and inspected the Red phase which was in good order.
1496 | Powercor 17/181 | Powercor | 2018-04-03 | 0.4 | -37.86985413 | 144.78563043 | 44 TALBOT STREET, ALTONA MEADOWS. | 32177509 | LVN022 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13862 | 20180306PWA_02 | Report was received of a HV conductor down at pole LIS 213813 Cnr of Talbot st and Alma Ave. Possible HVI, LEI required. On arrival the crew found, that a HV conductor fell on to LV due to a burnt off HV crossarm cross arm. This resulted in the outer phase HV conductor falling on top of the LV conductors. There was no ground fire, no third party damage or injuries reported. The LEI, Damian Harris, tested all customer connections and confirmed no HVI and no damage to customer property. The site was made safe and appropriate repairs were made.
1497 | Powercor 17/182 | Powercor | 2018-08-03 | 0.62153 | -36.49884418 | 144.93079068 | 980 TWO TREE Rd., CARAG CARAG. | 30255469 | SHP021 | 22kV AC | Rural Long | - fuse (boric acid) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 13866 | 20180309PWA_03 | Vic Fire reported grass fire and fuses down near intersection of Two Trees Rd and Geodetic Rd Carag Carag. On arrival the crew found evidence of a flashover on the Boric Acid fuse unit. Flash over marks on fuse unit bracket. An Area of approx. 80m x 20m of burnt grass in road reserve. Also a small amount of damage was noticed on the fence adjacent to the road reserve. There was no reported injuries.
1498 | Powercor 17/183 | Powercor | 2018-09-03 | 0.85694 | -36.72566313 | 144.25826013 | 369 EAGLEHAWK Rd., CALIFORNIA GULLY. | 30026311 | EHK031 | 22kV AC | Rural Short | - overhead conductor (bare; copper) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13871 | 20180314PWA_01 | Customer reported powerline down at 69 Victoria St Eaglehawk. When crew arrived they reported that they suspected a bat had flown into HV conductors causing a phase to phase fault. They were unsure if a HVI had occurred as HV conductors had dropped into LV conductors. LEI Bill Rounds attended site and confirmed that no HVI had occurred at this site. Report room advised that a subsequential fault had also occurred that was likely due to fault current. Crew attended secondary site and found that centre phase HV conductor had come down and a ground fire had been extinguished at base of the pole. Crew advised that the fault appeared to be due to a bad connection at the connection between the bridge and conductor on the centre phase. Crew replaced connection. Area of fire was approx. 12m x 6m. The following day, a customer reported that they still had no power and had heard a loud bang coming from her meter box shortly after noticing a fire outside her window (at base of pole). LEI Bill Rounds attended and confirmed that either a LVI or HVI had occurred but was unsure which. Bill also confirmed that property damage had occurred to at least an oven and some medical charging equipment. ESV notified of ground fire with unknown cause, property damage with unknown cause, media and community interest. Local paper had reported an outage at a cycling event which may have been related. Could not confirm but also advised ESV that there was interest from the community about this outage also. Later found that cycling event outage was unrelated to this incident. No shock or injuries.
1499 | Powercor 17/184 | Powercor | 2018-10-03 | 0.10903 | -36.35641819 | 145.46192390 | 105 Lemnos North Rd., Lemnos. | 33096892 | SHN024 | 22kV AC | Rural Short | - insulators | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13867 | 20180313PWA_01 | Vic Fire reported grass fire at 105 Lemnos North Rd Lemnos. On arrival the crew found evidence of a flashover from a bat on a HV 5 shed insulator. Crew raised fault follow up to replace insulator. Area of approx. 15m x 30m of burnt grass in the road reserve. Also a steel fence adjacent to the road reserve was blackened. ESV notified. No shock or injuries.
1500 | Powercor 17/185 | Powercor | 2018-11-03 | 0.072222 | -37.56578712 | 143.87324182 | 146 EUREKA STREET, BALLARAT EAST. | 30262779 | BAN015 | Low voltage AC (<1kV) | Rural Short | - luminaires (minor road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13874 | 20180315PWA_02 | VicFire reported a pole fire at the incident location. On arrival the crew found that the wiring in the 80w Mercury Vapour Street Light attached to this pole had shorted and had melted / burned the wiring in the Street Light. There was no ground fire. There were no injuries.
1501 | Powercor 17/186 | Powercor | 2018-11-03 | 0.51736 | -37.80089808 | 143.11048440 | 380 PEMBERTONS Rd., VITE VITE. | 32061488 | CDN006 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 13882 | 20180316PWA_04 | A customer reported an insulator on a cross arm had broken causing conductor to hang very low. The attending crew found evidence of a HV crossarm fire. The live HV conductor was hanging at a waste height. There was no evidence of ground fire. There were no reported shocks or injuries.
1502 | Powercor 17/187 | Powercor | 2018-11-03 | 0.76042 | -38.36423959 | 141.62532641 | 823 MADEIRA PACKET Rd., PORTLAND. | 32135488 | PLD006 | 22kV AC | Rural Short | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13922 | 20180328PWA_04 | An employee reported a pole fire had occurred at the incident location. The attending crew found that Pole 13 (LIS-905457) had caught fire at the HV tee off insulator position. There were no reported shocks or injuries. No evidence of ground fire.
1503 | Powercor 17/188 | Powercor | 2018-11-03 | 0.30278 | -38.16526772 | 144.36704636 | 161 FYANS STREET, SOUTH GEELONG. | 35407507 | GLE033 | Low voltage AC (<1kV) | Urban | - luminaires (minor road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 14053 | 20180514PWA_03 | Report from customer of Public Lantern on fire at incident location. There was no ground fire, no reported injuries and no third party property damage.
1504 | Powercor 17/189 | Powercor | 13/03/2018 | 0.27778 | -37.74803359 | 144.66738939 | 171 TROUPS ROAD S, TRUGANINA. | 30108240 | MLN021 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 13875 | 20180315PWA_03 | CFA reported a pole fire at the incident location. On arrival the Powercor fault crew found that a HV cross arm had slightly burnt through. There was no ground fire, no reported injuries or third party property damage.
1505 | Powercor 17/190 | Powercor | 15/03/2018 | 0.40625 | -37.37356087 | 143.74882403 | 970 Coghills Creek Rd., Coghills Creek. | 30006858 | BAN006 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 13879 | 20180316PWA_01 | An employee reported a burnt cross arm on a pole at the incident location. On arrival the crew found that a cross arm fire had occurred on a 22kV pole which burnt the cross arm only. Protection operated. There was no ground fire. There were no reported injuries or third party property damages.
1506 | Powercor 17/191 | Powercor | 15/03/2018 | 0.63333 | -38.33059551 | 141.58720305 | Corner of Henty Hwy & Wilson Rd., Portland. | 32134173 | PLD002 | 22kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 13880 | 20180316PWA_02 | Vicfire reported a pole on fire at the incident location. On arrival the crew found that a 22kV angle pole was on fire just below the steel cross arm. The crew attempted to isolate supply, however the pole burnt off before the isolation was completed, resulting in the crossarm and conductors falling to the ground causing a small grass fire on the road reserve of around 20m2 in size. There were no injuries, and no other damage reported.
1507 | Powercor 17/192 | Powercor | 15/03/2018 | 0.73056 | -38.0953636 | 144.339249 | 18 MALINDA CRESCENT, BELL PARK. | 34013007 | CRO022 | Low voltage AC (<1kV) | Urban | - LV pillar | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13881 | 20180316PWA_03 | A customer reported that the pillar outside his property had caught on fire at the incident location. On arrival the crew found that a 415V LV UG pillar had been damaged by an unknown vehicle at some time in the past. The Customer reported that he tried to straighten the Pillar by pushing on the lid, at which time the cables inside the pillar began arcing, resulting in a small grass fire of less than 0.5m2 around the base of the pillar. The Customer did not receive a shock, and was not injured. There were no injuries, and no other damage reported.
1508 | Powercor 17/193 | Powercor | 16/03/2018 | 0.31875 | -37.40481807 | 143.89216661 | Lot 1 10 BROOMFIELD Rd., CRESWICK. | 30013362 | BAN009 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 14054 | 20180514PWA_05 | Report of a pole fire at the incident location. There was no ground fire, no reported injuries or third party property damage.
1509 | Powercor 17/194 | Powercor | 17/03/2018 | 0 | -38.44804243 | 143.14160083 | 880 TIMBOON-COLAC Rd., SIMPSON. | 30044211 | COB011 | 12.7kV AC (SWER) | Rural Long | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | Severe | 2 | 2 | 13901 | 20180322PWA_06 | Emergency services reported that there was a number of fires in the south west of Victoria. One of these fires was in the Simpson (Timboon Colac road) area. A farmer reported the pole was severely damaged. The attending crew replaced a pole and subsequently identified a large tree had contacted with the 22kV line between poles 2 and 3 of the SMIT spur. There was a ground fire of some 400 by 500 m that was extinguished by the CFA. It is unconfirmed that the CFA found the conductor suspended approximately 1.8 m above the road and cut the tree allowing the conductor to clear the road. The conductor was sitting on but not attached to the damaged pole. This fire has not (yet) been given a specific name. This fire does not appear in EMCOP, there is another fire nearby that this one may have been confused with. Preliminary information only. Site made safe. Pole replaced.
1510 | Powercor 17/195 | Powercor | 17/03/2018 | 0.62778 | -38.37398596 | 142.49128527 | 85 Jamieson St., Warrnambool. | 30137710 | WBL008 | 22kV AC | Urban | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 13896 | 20180322PWA_02 | It could not be determined who reported this incident. On arrival the crew found that a 22kV HV Isolator top connection had failed, causing hot debris to fall to the ground, resulting in a grass fire of approx. 8m x 8m = 64m2. There were no injuries, and no other damage reported.
1511 | Powercor 17/196 | Powercor | 17/03/2018 | 0.91597 | -38.54708305 | 143.09185584 | 100 BOOROOK Rd., COORIEMUNGLE. | 30149644 | COB011 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | Severe | 2 | 2 | 13889 | 20180320PWA_03 | A customer reported a Cyprus tree fell on to powerlines at the incident location. Upon arrival, the Powercor crew found a large tree fell on to the HV line, conductors had been damaged and approx. 2sqm grass burnt. There were no injuries.
1512 | Powercor 17/197 | Powercor | 17/03/2018 | 0.90278 | -38.29901377 | 142.43315220 | MAILORS FLAT-KOROIT Rd., MAILORS FLAT. | 31017376 | KRT-PLD2 | 66kV AC | Unknown | - pole (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Severe | 2 | 9.2 | 13895 | 20180322PWA_01 | On arrival the crew found that a pole fire had occurred on a 22kV & 66kV pole. The pole fire resulted in a grass fire of approx. 5m x 100m = 500m2 of mostly road reserve. There was minor damage to fences and a small area of private property burnt. There were no injuries, and no other damage reported.
1513 | Powercor 17/198 | Powercor | 17/03/2018 | 0.86736 | -38.21841956863587 | 142.77409740747066 | OCCUPATION LANE, THE SISTERS. | 32055108 | TRG002 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Severe | 2 | 9.2 | 13891 | 20180321PWA_04 | Emergency services reported that there was a number of fires in the south west of Victoria. One of these fires was in the Garvoc area. The attending crew found evidence of broken pole. The site was left undisturbed and referred to Victoria Police prior to any restoration works. Fire damage and response activities undertaken as part of response to 4 fires in the area. Address approximate.
1514 | Powercor 17/199 | Powercor | 17/03/2018 | 0.875 | -38.23100986 | 142.95088219 | 20 SPRING DAM Rd., TERANG. | 32055460 | TRG001 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Severe | 2 | 9.2 | 13899 | 20180322PWA_03 | Emergency services reported that there was a number of fires in the south west of Victoria. One of these fires was in the Terang (Spring Dam road) area. An off duty Powercor worker was part of the CFA crew attending. He subsequently reported that there was a large gum tree in contact with the 22kV line between poles 2 and 3 of the spring dam spur. There was a ground fire of some 300m x 500 m that was extinguished by the CFA prior to them mobilising to the nearby Terang fire. This fire has not (yet) been given a specific name. Fire damage and response activities undertaken as part of response to other fires in the area and may have initially been considered as advance spotting of another fire
1515 | Powercor 17/200 | Powercor | 17/03/2018 | 0 | -38.38667874 | 142.84634113 | 2450 COBDEN-WARRNAMBOOL Rd., LAANG. | 32056486 | TRG005 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Severe | 2 | 9.2 | 13902 | 20180322PWA_07 | Emergency services reported that there was a number of fires in the south west of Victoria. One of these fires was in the Laang Area (Warrnambool – Cobden Road) area. The information from fire investigators is that this fire originated where a large tree may have contacted a high voltage line. It is to be confirmed that a Powercor crew attended removed the tree and undertook repairs. Powercor crew attended removed the tree and undertook repairs.
1516 | Powercor 17/201 | Powercor | 17/03/2018 | 0.86458 | -38.23740028046317 | 142.92894065774158 | Oppossite 6695 Princess Hwy, Terang. | 32194776 | TRG004 | 22kV AC | Rural Short | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Severe | 2 | 9.2 | 13892 | 20180321PWA_03 | Emergency services reported that there was a number of fires in the south west of Victoria. One of these fires was in the Terang area. The attending crew found evidence of conductor clashing under strong winds the site was left undisturbed and referred to Victoria Police prior to any restoration works. Fire damage and response activities undertaken as part of response to 4 fires in the area.
1517 | Powercor 17/202 | Powercor | 17/03/2018 | 0 | -38.232913498476854 | 143.0798449841309 | CROSS FOREST Rd., NAROGHID. | 33037538 | CDN006 | 22kV AC | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Severe | 2 | 9.2 | 13893 | 20180321PWA_01 | Emergency services reported that there was a number of fires in the south west of Victoria. One of these fires was in the Gnotuk area. Preliminary investigations by the Arson squad have identified that this fire originated near the intersection of Cross Forrest road and Saddlers roads in Gnotuk ( Naroghid) The police information attributes this fire to a tree branch that had contacted power lines. Exact point of origin to be clarified. At this time this has not been verified by Powercor personnel.
1518 | Powercor 17/203 | Powercor | 17/03/2018 | 0.44861 | -38.51103073 | 143.55287019 | 90 Fry's Rd., Gellibrand. | 33039091 | CLC006 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within electric line construction area | 19.8 | Severe | 2 | 39.6 | 13883 | 20180319PWA_01 | Customer reported power lines down and had caused a fire. On arrival the crew found a tree had fallen and brought down a HV conductor between BLANC pole 5 and 6. There was a ground fire (30x10m) in the road reserve. Crew advised a large tree had fallen in high winds bring 1 conductor to ground and starting a fire. There were no reported shocks or injuries.
1519 | Powercor 17/204 | Powercor | 17/03/2018 | 0.86458 | -37.87584266 | 142.15078728 | BANEMORE 992 TWOMEYS BRIDGE Rd.,, YATCHAW. | 33058409 | HTN003 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Severe | 2 | 9.2 | 13890 | 20180321PWA_02 | Customer reported wires down had started a fire in paddock at the incident location. On arrival the crew found that a tree (Blue gum) had fallen on the line and brought down a HV conductor between ELLBURGER P1 & P2. The fire was at the northern edge of a large bushfire. Victoria police requested to attend. Crew attended. Tree cleared and line restored after site observed by Victoria Police as part of investigation into cluster of fires.
1520 | Powercor 17/205 | Powercor | 17/03/2018 | 0.97778 | -38.07172725 | 142.43978262 | 1209 HARRIS Rd., MINJAH. | 33102095 | KRT012 | 22kV AC | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Severe | 2 | 9.2 | 14016 | 20180423PWA_03 | Emergency services reported that there was a number of fires in the south west of Victoria. One of these fires was in the Minjah Hawkesdale area. The attending crew found damaged conductor near the intersection of Harris Road. Fire damage and response activities were undertaken as part of response to a number of fires in the area.
1521 | Powercor 17/206 | Powercor | 18/03/2018 | 0.49653 | -37.83138202 | 144.85071803 | 348 BLACKSHAWS Rd., ALTONA NORTH. | 30117064 | BLTS-SCI | 22kV AC | Unknown | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 13924 | 20180329PWA_01 | Powercor/Citipower Controller, Tony Speechley, @ 11:55 & 11:56 on 18/03/2018, emailed the NAO AH Ardeer to advise of a Pole Fire on the BLTS-SCI 66kV Pole 34 LIS-5873, Blackshaws Rd corner Mahon Ave, Altona North. NAO spoke to the field crew and PCA Operator, and they advised that the pole fire appeared to have started at the 22kV X-arm King-Bolt and 22kV Centre-Phase Insulator and tracked upwards and downwards along the pole. The MFB attended site and extinguished the fire. The pole was inspected on the day 18/03/2018 for damage and field crews undertook repairs to the damaged pole the very next day - 19/03/2018 @ approx. 17:00. There was no reported HVI, injury, shocks or ground fire as a result of this incident.
1522 | Powercor 17/207 | Powercor | 18/03/2018 | 0.017361 | -38.39037496 | 142.64088338 | 4350 COBDEN-WARRNAMBOOL, ALLANSFORD. | 30134052 | WBL002 | 22kV AC | Rural Short | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | Severe | 2 | 2 | 13900 | 20180323PWA_02 | Multiple customers called to report no supply in the area. On arrival the crew found that a large tree branch had contacted the HV conductors at the incident location. The subsequent clashing of the 22kV conductors resulted in a grass fire of approx. 4000m2 of road reserve and private property. There was damage to fences pasture and a tree plantation. There were no injuries.
1523 | Powercor 17/208 | Powercor | 18/03/2018 | 0.42014 | -38.19120171 | 144.47356768 | 2-4 CHRISTIES Rd., LEOPOLD. | 31012208 | DDL014 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 14055 | 20180515PWA_01 | Customer reported pole fire at incident location. There was no ground fire, no reported injuries or third party property damage.
1524 | Powercor 17/209 | Powercor | 18/03/2018 | 0.62917 | -37.83707143 | 144.80016870 | PRINCES FREEWAY, LAVERTON NORTH. | 31024388 | ATS-TYA | 66kV AC | Unknown | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 13884 | 20180319PWA_02 | A Powercor Line Worker advised of a grass fire in the road reserve of the Princes Freeway, Laverton North near the base of DBL CCT 66kV Pole 108. The pole appears to have burnt through and snapped at this point, just below the bottom 66kV x-arm. The resultant sparks from this have fallen to the ground below and caused a grass fire of approximately 8m x 5m near the base of Pole 108 LIS-3172. There was no reported HVI, injury or shocks as a result of this incident.
1525 | Powercor 17/210 | Powercor | 18/03/2018 | 0.12014 | -37.06899506 | 144.21684417 | 2A Greenhill Avenue, Castlemaine. | 32049313 | CMN003 | Low voltage AC (<1kV) | Rural Long | - overhead conductor (bare; copper) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 13905 | 20180326PWA_01 | Report of damaged powerline and grass fire, at the incident location. On arrival the crew found at Greenhill Ave, Castlemaine, between LIS 508022 & LIS 508023 trees making contact with LV, causing conductors to clash with a broken conductor making contact with the ground, causing a small 20m x 1.5m grass fire There were no reported shocks or injuries.
1526 | Powercor 17/211 | Powercor | 18/03/2018 | 0.48403 | -36.36537307 | 141.15880213 | WESTERN HIGHWAY, LILLIMUR. | 32122137 | NHL031 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very High | 1 | 1 | 13886 | 20180319PWA_04 | An customer reported a low conductor at the incident location. On arrival the crew found that a cross arm fire had occurred on a 22kV pole which burnt the cross arm only. No protection operated. There was no ground fire. There were no reported injuries or third party property damages.
1527 | Powercor 17/212 | Powercor | 18/03/2018 | 0.32708 | -37.52062781 | 142.04037186 | 10024 NATIMUK-HAMILTON Rd., CAVENDISH. | 32125402 | HTN004 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Severe | 2 | 9.2 | 13944 | 20180405PWA_03 | Vicfire reported a pole fire at the incident location. On arrival the crew found that a Strain cross-arm had burnt off at one end, allowing the conductor and insulators to fall onto a service cable below. There was no ground fire, and further tests showed that there was no apparent HVI. There was no reported third party damage or any injuries.
1528 | Powercor 17/213 | Powercor | 18/03/2018 | 0.48333 | -37.82846633 | 144.78915811 | 105-121 DOHERTYS Rd., LAVERTON NORTH. | 32176040 | LVN032 | 22kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 13887 | 20180320PWA_01 | Powercor/Citipower Controller reported there is a fire burning at the top of the pole Pole 95 LIS-30506 (BLTS-SCI & BLTS-LVN DBL CCT 66kV) & (LVN032 22KV feeder). There was no reported HVI, injury, shocks or ground fire as a result of this incident. Upon isolation crew carried out repairs and made site safe.
1529 | Powercor 17/214 | Powercor | 19/03/2018 | 0.66319 | -37.00015299 | 141.80886013 | Digger Jims Rd., Toolondo. | 30082900 | HOTS-CHM | 66kV AC | Unknown | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 13897 | 20180322PWA_04 | Customers reported a supply outage in the Charam area and there was a loss of supply to the Charam Zone Substation at 15:51 hours on 19/03/18. There was also a subsequent report of a ground fire at the incident location. On arrival the crew found that a pole fire on a wooden 66 kV pole had resulted in the pole top structure including a steel x arm falling to the ground. There was a ground fire of approximately 150m². There were no injuries.
1530 | Powercor 17/215 | Powercor | 19/03/2018 | 0.97153 | -36.33683382 | 141.70002591 | 7165 WESTERN HIGHWAY, NHILL. | 32112322 | NHL015 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 13898 | 20180322PWA_05 | VicFire reported a pole fire at the incident location. On arrival the crew found that a wooden crossarm required replacement due to the pole fire. There was a small ground fire in private property of approximately 10x3m in the vicinity of the base of the pole. There were no injuries.
1531 | Powercor 17/216 | Powercor | 19/03/2018 | 0.017361 | -37.52740733 | 144.47687362 | 1328 BACCHUS MARSH Rd., BULLENGAROOK. | 33075101 | BMH006 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very High | 1 | 1 | 13907 | 20180326PWA_02 | A PCA fault crew attended a fault at the incident location. On arrival they noticed a grass fire had started (10 x 5 mtrs). They found a burnt EDO fuse tube in the burnt area. There were no reported injuries, there was minor damage to the customers fence and service pit.
1532 | Powercor 17/217 | Powercor | 20/03/2018 | 0.13889 | -36.41235122 | 143.61264590 | 21 TANTALLA STREET, WEDDERBURN. | 30018807 | CTN002 | 22kV AC | Rural Long | - overhead conductor (bare; copper) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13908 | 20180326PWA_03 | Customers reported damaged powerline and sparking, at the incident location. On arrival the crew found at 21 Tantalla Street Wedderburn, between LIS 852793 & LIS 610343 a tree had made contact with HV, broken conductors making contact with the ground, causing a small 1m x 1m grass fire. There were no reported shocks or injuries.
1533 | Powercor 17/218 | Powercor | 20/03/2018 | 0.026389 | -37.16632311 | 142.86737484 | GARDEN GULLY VINEYARD, 1477 WESTERN HIGHWAY, GREAT WESTERN. | 31014142 | ART-STL | 66kV AC | Unknown | - pole (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 13904 | 20180323PWA_06 | VicFire reported a pole fire at the incident location. On arrival the crew found that a wooden 66/22 kV pole was slightly damaged between the steel crossarms on the centre and bottom circuits. There was no ground fire. There were no injuries.
1534 | Powercor 17/219 | Powercor | 21/03/2018 | 0.86875 | -36.20442159 | 144.94812329 | 171 HENDERSON Rd., TONGALA. | 33107920 | KYM006 | 22kV AC | Rural Short | - overhead conductor (bare; copper) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13909 | 20180326PWA_04 | Report of grass fire at incident location. On arrival the crew found at 171 Henderson Road Tongala, LIS 953084, two dead birds were found at base of pole and a 10m x 10m burnt area of grass. There was no reported shocks, injuries or property damage.
1535 | Powercor 17/220 | Powercor | 24/03/2018 | 0.4875 | -36.05379999 | 143.10217699 | BIRCHIP-WYCHEPROOF Rd., NARRAPORT. | 30023395 | CTN001 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very High | 1 | 4.6 | 13925 | 20180329PWA_02 | SCADA alarm advised that Birchip P29 ACR had tripped to lockout, shortly after customer reported a conductor down at the incident location. On arrival the crew found that a wooden angle-strain cross-arm had burnt through at the roadside disc / bridging insulator, causing the conductor to fall to ground. There was no ground fire, no reported injuries, no 3rd party damage, protection operated.
1536 | Powercor 17/221 | Powercor | 24/03/2018 | 0.59653 | -36.30104308 | 144.47983647 | 1845 PRAIRIE-ROCHESTER Rd., LOCKINGTON. | 30122637 | SHP012 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13912 | 20180327PWA_02 | Vicfire reported a pole fire at the incident location. On arrival the crew found that a single phase intermediate pole had caught on fire about 1.5M below the cross-arm, the embers which fell commenced a ground fire of approximately 6M x 40M in area, grass on the road side burnt, minor damage to a nearby fence occurred. CFA in attendance to extinguish ground fire & pole fire. There was no reported injuries.
1537 | Powercor 17/222 | Powercor | 24/03/2018 | 0.43125 | -37.80459845 | 144.76370731 | 161 AUSTRALIS DRIVE, DERRIMUT. | 30266247 | TNA024 | Low voltage AC (<1kV) | Urban | - services pit | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 14002 | 20180418PWA_06 | “P & N ENGINEERING PTY LTD, phoned in on 24/03/2018 @ 10:21 to advise Rain went into pit and caught on fire. It is still on fire. No supply. Cust haven’t called 000 but adv to. Currently raining.” On arrival @ 11:41 on 24/03/2018 the PCA ATL advised that the LV Service Pit in the road reserve between No. 161 & 163 Australis Drive, Derrimut, 3030 was smoking and there was flames coming out of the pit. Eric advised that he then proceeded to Australis-Westpark 750kVA Kiosk s/stn and isolated the LV Street circuit supplying this pit. Eric advised that he has organised civils and the UG field crew Cameron McCallum Serle to attend site for repairs. On arrival @ 13:46 on 24/03/2018 the UG field crew Cameron McCallum Serle has advised that, what appears to be a fault in the pit, has caused the whole pit to melt, including 1-2m of 4/C 35mm LV Service Cable, 4 x LV Pit Connectors and approx. 150-300mm of consumers lv mains to 161 and 163 Australis Drive, Derrimut, 3030. There was no reported ground fire, injury or shocks as a result of this incident. The crew made the site safe and replaced the LV Service Pit, installed a new LV SJ and ran a new section of 35mm² 4/c lv service cable into the new pit. A defect notice was issued to No. 161 & 163 Australis Drive, Derrimut, 3030.
1538 | Powercor 17/223 | Powercor | 24/03/2018 | 0.57292 | -38.16460561 | 144.40924902 | 8 WATTLEPARK AVENUE, MOOLAP. | 31011967 | GLE031 | 22kV AC | Rural Short | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13928 | 20180329PWA_05 | A customer reported to Powercor a pole fire at the incident location. On arrival the crew found that a wooden pole with HV wood cross arm had sustained significant damage due to a pole fire. The top of the pole structure had collapsed onto itself resulting in the HV assets resting in close proximity to the LV conductors. Initially is was suspected that a HVI may of also occurred however no evidence of a HVI has been found. There was no ground fire, no reported injuries, no 3rd party damage, protection operated as expected.
1539 | Powercor 17/224 | Powercor | 24/03/2018 | 0.425 | -38.20277449 | 144.33786652 | 24 PIONEER Rd., GROVEDALE. | 32084603 | WPD012 | 22kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13927 | 20180329PWA_04 | Vic Fire report to Powercor advising of a pole smoking at the incident location. On arrival the crew found that a wooden pole with HV steel cross arms appeared to be burning internally, at approx. ¾ distance up the pole. The pole was still intact and supply remained on with no wires falling to ground. A controlled interruption was undertaken in the area to allow fire brigade crews safe access to extinguish the fire. The pole was found to be extensively damaged and required replacement. There was no ground fire, no reported injuries, no 3rd party damage.
1540 | Powercor 17/225 | Powercor | 24/03/2018 | 0.91181 | -36.24667864 | 142.51649380 | 3117 BORUNG HIGHWAY, WARRACKNABEAL. | 32111009 | HSM003 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 14056 | 20180515PWA_03 | Customer reported a pole fire at incident location. There was no ground fire, no reported injuries or third party property damage.
1541 | Powercor 17/226 | Powercor | 24/03/2018 | 0.70417 | -35.26263951 | 143.50244132 | 94 MCKENZIE Rd., TYNTYNDER SOUTH VIC. | 32155814 | SHL004 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 13926 | 20180329PWA_03 | Customer reported a pole had exploded and it was smoking / smouldering at the incident location. On arrival the crew found that a wooden termination cross-arm had burnt through at the disc insulator string, causing the conductor to fall to ground. There was no ground fire, no reported injuries, no 3rd party damage, protection operated.
1542 | Powercor 17/227 | Powercor | 25/03/2018 | 0.94583 | -36.38403348 | 143.29302865 | 1422 CHARLTON-ST ARNAUD Rd., YEUNGROON. | 32027217 | CTN006 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very High | 1 | 4.6 | 13931 | 20180329PWA_08 | Vicfire reported a pole fire at the incident location. On arrival the crew found that a wooden support ( for ISO single phase side HV fuse units ) cross-arm was fire damaged but supply remained on. There was no ground fire, no reported injuries, no 3rd party damage.
1543 | Powercor 17/228 | Powercor | 25/03/2018 | 0.98958 | -35.15574032 | 141.19054870 | 1198 MURRAYVILLE NORTH Rd., MURRAYVILLE. | 32147691 | OYN001 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very High | 1 | 1 | 13936 | 20180403PWA_04 | Following customer calls, a patrol found pole fire at incident location. There was no ground fire or third party property damage.
1544 | Powercor 17/229 | Powercor | 25/03/2018 | 0.91875 | -35.33030418 | 141.24865349 | 759 GUNAMALARY Rd., MURRAYVILLE. | 32153230 | OYN001 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very High | 1 | 1 | 13940 | 20180403PWA_09 | Following customer calls, a patrol found pole fire at incident location (Gunmalary 15 ). There was no ground fire or third party property damage.
1545 | Powercor 17/230 | Powercor | 25/03/2018 | 0.98403 | -35.50430711 | 142.84043490 | 19 HANNON STREET, SEA LAKE. | 32157793 | OYN005 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very High | 1 | 1 | 13930 | 20180329PWA_07 | Vicfire reported a pole fire at the incident location. On arrival the crew found that a wooden angle-strain cross-arm failed due to fire damage but conductors remained suspended by cross-arm braces. There was no ground fire, no reported injuries, no 3rd party damage.
1546 | Powercor 17/231 | Powercor | 26/03/2018 | 0.66597 | -37.96333751 | 144.69539813 | 535 OCONNORS Rd., WERRIBEE SOUTH. | 30110190 | WBE034 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13941 | 20180403PWA_10 | Report of a pole fire at the incident location. On arrival the field crew has advised that there was a burnt out HV Inter X-arm. There was no reported Ground fire, HVI, injury, shock or third party damage as a result of this incident.
1547 | Powercor 17/232 | Powercor | 26/03/2018 | 0.38889 | -36.18476792 | 142.39861534 | 772 HENTY HIGHWAY, WARRACKNABEAL. | 32107264 | HSM003 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 13929 | 20180329PWA_06 | A passer-by reported a pole fire at the incident location. On arrival the Powercor fault crew found that a HV cross arm burnt through. The crew made the place safe and the repairs have been completed. There were no injuries, HVI or ground fire
1548 | Powercor 17/233 | Powercor | 26/03/2018 | 0.28611 | -36.11297130 | 141.52061257 | 831 YANAC-NETHERBY Rd., YANAC. | 32113215 | NHL031 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 13914 | 20180327PWA_04 | Customers reported a power outage and dim lights at the incident location. On arrival the Powercor fault crew found that the HV cross arm and pole top burnt through. Protection operated. There was no ground fire, no injuries or third party property damage.
1549 | Powercor 17/234 | Powercor | 26/03/2018 | 0.039583 | -35.16033494 | 141.42572258 | 867 SUNSET Rd., COWANGIE. | 32145257 | OYN001 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 13937 | 20180403PWA_05 | Following customer calls, a patrol found pole fire at incident location. There was no ground fire or third party property damage.
1550 | Powercor 17/235 | Powercor | 26/03/2018 | 0.039583 | -35.15189015 | 141.41934155 | 867 SUNSET Rd., COWANGIE. | 32145306 | OYN001 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 13938 | 20180403PWA_06 | Following customer calls, a patrol found pole fire at incident location. There was no ground fire or third party property damage.
1551 | Powercor 17/236 | Powercor | 26/03/2018 | 0.039583 | -35.14955231 | 141.42001506 | 867 SUNSET Rd., COWANGIE. | 32145320 | OYN001 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 13939 | 20180403PWA_08 | Following customer calls, a patrol found pole fire at incident location (Tyalla P43). There was no ground fire or third party property damage.
1552 | Powercor 17/237 | Powercor | 26/03/2018 | 0.17222 | -35.24020757 | 141.04125053 | 7332 MALLEE HIGHWAY, PANITYA. | 32153749 | OYN001 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 13935 | 20180403PWA_03 | Following customer calls, a patrol found pole fire at Murrayville 988. There was no ground fire or third party property damage.
1553 | Powercor 17/238 | Powercor | 26/03/2018 | 0.41597 | -35.28645765 | 141.14337444 | 431 NGALLO Rd., MURRAYVILLE. | 32153983 | OYN001 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 14058 | 20180515PWA_05 | Customer reported a pole fire at the incident location. There was no ground fire, no reported injuries or third party property damage.
1554 | Powercor 17/239 | Powercor | 26/03/2018 | 0.66667 | -35.39013900 | 142.66317821 | 4723 PATCHEWOLLOCK-SEA LAKE Rd., NYARRIN. | 32158659 | OYN005 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 14059 | 20180515PWA_06 | Customer reported pole fire at incident location. There was no ground fire, no reported injuries or third party property damage.
1555 | Powercor 17/240 | Powercor | 26/03/2018 | 0.13958 | -35.69224368 | 142.58103786 | 1463 HOPETOUN-SEA LAKE Rd., HOPETOUN. | 32159080 | OYN005 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 14057 | 20180515PWA_04 | Customer reported pole fire at incident location. There was no ground fire, no reported injuries or third party property damage.
1556 | Powercor 17/241 | Powercor | 26/03/2018 | 0.74306 | -35.39065932 | 142.69452810 | 4780 PATCHEWOLLOCK-SEA LAKE Rd., NYARRIN. | 33069395 | OYN005 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 14060 | 20180515PWA_07 | Customer reported pole fire at incident location. There was no ground fire, no reported injuries or third party property damage.
1557 | Powercor 17/242 | Powercor | 30/03/2018 | 0.48125 | -38.31537603 | 142.40539477 | 931 TOWER HILL Rd., ILLOWA. | 32195786 | KRT013 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 13947 | 20180406PWA_02 | Vicfire reported a pole smoking at the incident location. On arrival the crew found the pole had burnt around the bolts of an LA bracket. There were no reported injuries, ground fire or third party damage.
1558 | Powercor 17/243 | Powercor | 31/03/2018 | 0.95347 | -37.27168363 | 142.92032719 | 13 Golf Links Rd., Ararat. | 30081982 | ART034 | Low voltage AC (<1kV) | Rural Short | - fuse (any other type) | single phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 14026 | 20180501PWA_01 | Vic Fire reported a pole fire at the incident location. On arrival the crew found that the 3 phase LV Fused Junction Box had melted and dropped from its mounting position, and wiring in the Underground Service Pit at the base of this pole were running hot. There was no pole fire, no ground fire or any other damage caused by this incident. The cause of the melted Junction Box appears to be the high electrical loading in the domestic installation connected via this U/G Service Pit. Investigations by the fault crew revealed illegal wiring at the meter box; with wiring connected to bypass the meters. Police on site found a hydroponics set up inside the installation, and later TV reports showed vision of Police removing in the order of 200 leafy green plants from this property. Police advised the fault crew not to restore supply to this installation. The fault crew cut the U/G service tails to isolate the installation at the Service Pit.
1559 | Powercor 17/244 | Powercor | 2018-04-04 | 0.73889 | -37.82717473 | 144.86712449 | 48 NEW STREET, SOUTH KINGSVILLE. | 33072189 | BLT022 | 22kV AC | Urban | - overhead conductor (bare; copper) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13942 | 20180405PWA_01 | Jemena Dispatch advised, MFB had reported that balloons went through powerlines near LIS 28296 and the sub on the pole blown at the incident location. On arrival the crew found HV has tracked through insulator and fuse unit through to conductive pole and LV earth which is now also damaged. The crew suspects possible HVI. The fallen debris caused very minor grass fire (2m x 1m) at the pole base.
1560 | Powercor 17/245 | Powercor | 2018-07-04 | 0.98819 | -38.33537530737897 | 143.05592306613153 | 16 L GRAYLANDS Rd., COBDEN. | 30149427 | COB012 | 22kV AC | Urban | - connector / termination | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 13951 | 20180409PWA_05 | Vicfire reported “grass fire, powerline and pole sparking may be the possible cause.” On arrival the crew found a grass fire near the base of the cable head pole which burnt an area of around 20m by 3 m. The crew identified some evidence of flashover on the cable terminations but were unable determine a cause. There were no reported injuries.
1561 | Powercor 17/246 | Powercor | 2018-08-04 | 0.41319 | -36.43975730 | 145.22597169 | 91 Hogan St., Tatura. | 30140525 | MNA021 | 22kV AC | Rural Short | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 14119 | 20180529PWA_02 | CFA called to advise that sparks were coming from the pole. Upon arrival crew found that an EDO fuse had candled on (LIS-931068), supply had not been interrupted however. EDO fuse was changed like for like and supply was restored after a brief interruption to change the fuse. There were no emergency services onsite, no police. There was no shock, no injury, no damage to private property or any additional damage to PCA property recorded.
1562 | Powercor 17/247 | Powercor | 2018-08-04 | 0.70486 | -37.79165936 | 144.77877617 | 61 CASTRO WAY, DERRIMUT. | 30244805 | SU013 | 22kV AC | Urban | - switch (disconnector/isolator) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 13957 | 20180410PWA_02 | A flashover occured due to bird contact at HV SW# 23203 (HV isolators at pole LIS-726276), sparking a small grass fire (5m x 2m) in the nature strip below outside 61 Castro Way. ESV was notified of the small grass fire per the details within this report. No shock, third party damage or injuries to report.
1563 | Powercor 17/248 | Powercor | 2018-08-04 | 0.59792 | -38.38767019965601 | 143.0697075238037 | 645 COBDEN-PORT CAMPBELL Rd., GLENFYNE. | 33036052 | COB011 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | Very High | 1 | 1 | 13952 | 20180409PWA_04 | Emergency services reported a tree pulled wires down, started grass fire in Cobden-port Campbell Rd., Cobden. On arrival the crew found a large gum tree had fallen bringing down conductors on the opposite side of the road. There was a grass fire initiated which then burnt an area of around 300m by 5 m, largely along road reserve. Some farm fencing was damaged. There were no reported injuries.
1564 | Powercor 17/249 | Powercor | 2018-08-04 | 0.70486 | -37.7916 | 144.784 | 159 Studley Court, Derrimut | PA0128151 | SU013 | 22kV AC | Urban | - transformer (kiosk mounted) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 14266 | 20180723PWA_05 | Fire at kiosk substation due to bird induced fault at HV SW# 23203 (HV isolators at pole LIS-726276) (refer incident #13957). Secondary faults occurred and caused fire. Kiosk substation ignited during re-energisation.
1565 | Powercor 17/250 | Powercor | 2018-12-04 | 0.85278 | -37.18007555 | 144.36180059 | 1243 CALDER HIGHWAY, DRUMMOND NORTH. | 30033573 | CMN001 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very High | 1 | 4.6 | 13989 | 20180416PWA_08 | CFA reported a grass fire caused by Powercor assets at the incident location. On arrival the crew found that a possum had flashed over on a single phase substation structure, the exact location of the flashover has not been confirmed, causing the possum to fall to the ground and ignite a small grass fire, approximately 10M x 20M square was burnt. CFA extinguished the fire, and doused the pole also at its base. There were no reported injuries, no 3rd party damage.
1566 | Powercor 17/251 | Powercor | 2018-12-04 | 0.37639 | -36.33131433 | 145.68670595 | 55 DOOKIE STREET, DOOKIE. | 33090594 | STN024 | Low voltage AC (<1kV) | Rural Long | - overhead service conductor (residential) | two phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 13977 | 20180412PWA_07 | A customer, Suzanne Hall advised a wire had come down and resulted in fire on the nature strip. On arrival the crew found that a catenary and service cable had faulted and come to ground. This caused a ground fire of approximately 10m X 5m. There was no injury or third party damage reported.
1567 | Powercor 17/252 | Powercor | 14/04/2018 | 0.69444 | -37.02795026 | 143.87086764 | 636 BARINGHUP Rd., CARISBROOK. | 30017729 | MRO007 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 13985 | 20180416PWA_03 | Vicfire reported a low conductor and pole fire at the incident location. On arrival the crew found that a wooden intermediate cross-arm failed due to fire damage at the kingbolt, resulting in the conductors being suspended approximately 2m above the ground. There was no ground fire, no reported injuries, no 3rd party damage,
1568 | Powercor 17/253 | Powercor | 14/04/2018 | 0.69444 | -34.64633733 | 142.85342769 | 585B TOL TOL Rd., TOL TOL. | 30097375 | RVL008 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very High | 1 | 1 | 13990 | 20180417PWA_01 | Customer reported a low conductor and pole fire at the incident location. On arrival the crew found that a wooden intermediate cross-arm failed due to fire damage at the cross-arm strap, conductor remained suspended above the ground. There was no ground fire, no reported injuries, no 3rd party damage.
1569 | Powercor 17/254 | Powercor | 14/04/2018 | 0.64583 | -35.33952971 | 143.55095721 | 132 STRADBROKE AVENUE,, SWAN HILL. | 30101023 | SHL008 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 13988 | 20180416PWA_07 | SCADA alarm for SHL008 feeder lockout initiated a fault crew investigating the outage cause, discovering a pole fire at the incident location. On arrival the crew found that a wooden intermediate cross-arm failed due to fire damage at a cross-arm strap resulting in the conductor falling onto the LV circuit below, contacting the red phase. There was no ground fire, no reported injuries, no 3rd party damage, no evidence of HV injection was found by LEI.
1570 | Powercor 17/255 | Powercor | 14/04/2018 | 0.91389 | -35.22062577 | 143.44629765 | 1764 MURRAY VALLEY HIGHWAY, BEVERFORD. | 30546795 | SHL004 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very High | 1 | 1 | 14061 | 20180517PWA_01 | Pole fire reported at incident location. There was no ground fire, no reported injuries and no third party property damage.
1571 | Powercor 17/256 | Powercor | 14/04/2018 | 0.65 | -36.50447960 | 142.92369183 | 863 WELLS Rd., AVON PLAINS. | 32021671 | CTN006 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very High | 1 | 4.6 | 13983 | 20180416PWA_01 | SCADA alarm from Swanwater ACR initiated fault crew response who discovered a pole fire at the incident location. On arrival the crew found that a three phase intermediate pole had burnt off at the pole top. The embers which fell commenced a ground fire of approximately 6m x 5m in area, grass on the road side burnt, fire self extinguished. There was no reported injuries, no 3rd party property damage.
1572 | Powercor 17/257 | Powercor | 14/04/2018 | 0.99931 | -35.57988087 | 143.93105296 | KERANG-MURRABIT Rd., CAPELS CROSSING. | 32030396 | KGT003 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very High | 1 | 1 | 13991 | 20180417PWA_02 | Customer reported a low conductor at the incident location. On arrival the crew found that a wooden intermediate cross-arm failed due to fire damage at a grey fog pin insulator, conductor was adrift but remained suspended above the ground. There was no ground fire, no reported injuries, no 3rd party damage, no protection operated.
1573 | Powercor 17/258 | Powercor | 14/04/2018 | 0.58333 | -36.65676301 | 144.52131288 | 1541 AXEDALE-GOORNONG Rd., BARNADOWN. | 32038909 | EHK023 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very High | 1 | 4.6 | 14014 | 20180423PWA_01 | A nearby customer reported a fire on a pole at the incident location. On arrival the crew found that a cross arm fire had occurred on a 22kV pole which burnt the cross arm only. Protection operated. There was no ground fire. There were no reported injuries or third party property damages.
1574 | Powercor 17/259 | Powercor | 14/04/2018 | 0.69444 | -34.62251284 | 142.78660588 | 54B DAMASCUS Rd., ROBINVALE. | 32141555 | RVL001 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 13984 | 20180416PWA_02 | Vicfire reported a low conductor and pole fire at the incident location. On arrival the crew found that a wooden intermediate cross-arm failed due to fire damage at the kingbolt, conductors remained suspended above the ground. There was no ground fire, no reported injuries, no 3rd party damage.
1575 | Powercor 17/260 | Powercor | 14/04/2018 | 0.81319 | -34.17578555 | 142.03143223 | 444 COWANNA AVENUE, MERBEIN. | 32145013 | MBN031 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 13986 | 20180416PWA_05 | Customer called reporting a pole fire at the incident location. On arrival the crew found that a wooden termination cross-arm failed due to fire damage at the bridging insulator / disc string hardware mounting points, the overhead conductor remained suspended held up by the bridge. There was no ground fire, no reported injuries, no 3rd party damage
1576 | Powercor 17/261 | Powercor | 14/04/2018 | 0.69444 | -34.18980573 | 141.62194082 | 3584 OLD MAIL Rd., CULLULLERAINE. | 32147375 | MBN031 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very High | 1 | 4.6 | 13987 | 20180416PWA_06 | SCADA alarm for Lake Cullulleraine P264 ACR lockout initiated a fault crew investigating the outage cause, subsequently a customer with specific location details called reporting a pole fire at the incident location. On arrival the crew found that a wooden termination cross-arm failed due to fire damage at a EDO fuse unit mounting location, resulting in the conductor falling onto the ground below. There was no ground fire, no reported injuries, no 3rd party damage.
1577 | Powercor 17/262 | Powercor | 16/04/2018 | 0.35694 | -36.31446196 | 141.11655896 | BRIMBLE Rd., LILLIMUR. | 32094204 | NHL031 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 14008 | 20180419PWA_02 | Following a line outage, a crew reported a fire on a pole at the incident location. On arrival the crew found that a pole fire had occurred on a 12.7kV pole which burnt the pole top only. Protection operated. There was no ground fire. There were no reported injuries or third party property damages.
1578 | Powercor 17/263 | Powercor | 18/04/2018 | 0.34236 | -36.03307494 | 142.03668265 | 5125 DIMBOOLA-RAINBOW Rd., RAINBOW. | 32121639 | NHL015 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 14007 | 20180419PWA_01 | Following a feeder outage, a crew reported a fire on a pole at the incident location. On arrival the crew found that a cross arm fire had occurred on a 22kV pole which burnt the cross arm only. Protection operated. There was no ground fire. There were no reported injuries or third party property damages.
1579 | Powercor 17/264 | Powercor | 19/04/2018 | 0.59931 | -36.34749784 | 145.41737168 | 145 FORD Rd., GRAHAMVALE. | 33088530 | SHTS-STN | 66kV AC | Unknown | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 14013 | 20180420PWA_01 | Customer rang to advise he heard a loud bang and reports ground fire at the incident location. There was a reclose of the SHTS-STN 66kV line at that time. A crew attended and found a 3mx3m grass fire had start at the base of S/S P13 Ford Tie S/L, Fire had self-extinguished when crew arrived. Crew advise a pair of birds had flashed over on the 66kV pole SHTS-STN P9 on the cnr of Verney Rd and Ford Rd., resulting in a HVI into a street lighting CCT that was fed from the Ford Rd P13 S/S. This flash over caused damage to a 66kV insulator on P9, 9 damaged street lights and a melted fuse box on P13, that started the ground fire. An LEI attended. No damage to customer installation identified. The crew replaced the fuse box and left the street lighting CCT off supply awaiting repairs. Damaged 66kV insulator listed for replacement. There were no reported shocks or injuries.
1580 | Powercor 17/265 | Powercor | 21/04/2018 | 0.69653 | -37.58447995 | 143.84104908 | 29 Albert St., Sebastopol. | 30013047 | BAS034 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 14033 | 20180503PWA_03 | A broken HV Xarm was reported . A crew attended and found a HV conductor with attached insulator and portion of burnt wooden Xarm was hanging above the LV conductor on pole.
1581 | Powercor 17/266 | Powercor | 22/04/2018 | 0.90347 | -36.63783629 | 144.52476218 | AXEDALE-GOORNONG Rd., GOORNONG. | 33021748 | EHK023 | 22kV AC | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 14017 | 20180426PWA_01 | Vic Fire reported wires down and grass fire at incident location. On arrival at LIS 425449, Axedale-Goornong Road Barnadown, crew found a HV conductor had failed, starting a 120m² grass fire, where a 3m section of 6/1/093 conductor had been spliced into the 3/4/093 line during previous works, crew made safe returning the line to service with temporary repairs with final repairs completed the next day. There was no reported shocks, injuries or property damage.
1582 | Powercor 17/267 | Powercor | 23/04/2018 | 0.56111 | -34.66520474 | 142.71060840 | 156 HOCKING Rd., HAPPY VALLEY. | 32147929 | WMN014 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 14062 | 20180517PWA_02 | Report of pole fire at incident location. There was no ground fire, no reported injuries and no third part property damage.
1583 | Powercor 17/268 | Powercor | 24/04/2018 | 0.65208 | -38.27637767 | 144.24278498 | 1360 BLACKGATE Rd., FRESHWATER CREEK. | 30067860 | WPD014 | 22kV AC | Rural Short | - transformer (pole mounted) | three phase | Started by lightning striking a distribution system or a part of a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 14022 | 20180427PWA_02 | A customer called regarding a supply interruption. The crew attended and found failed transformers in the area. Harrison F’Water Ck transformer had been hit by lightning and this resulted in a ground fire. The fire was approximately 1 X 2 meters. No injury or third party damage had occurred.
1584 | Powercor 17/269 | Powercor | 25/04/2018 | 0.32083 | -36.19499213 | 144.91210740 | 7840 MURRAY VALLEY HIGHWAY, KOYUGA. | 30125482 | ECA005 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 14018 | 20180426PWA_02 | Police reported wires sparking and explosion at incident location. On arrival the crew found Magpies had caused a HV fault, starting a 15m x 60m grass fire. There was no reported shocks, injuries or property damage.
1585 | Powercor 17/270 | Powercor | 28/04/2018 | 0.99375 | -38.44991933 | 144.097913 | 96 Bambra Rd., AIREYS INLET. | 33045917 | WPD014 | Low voltage AC (<1kV) | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 14032 | 20180503PWA_02 | CFA reported a pole fire at Bambra Rd., Aireys Inlet. A crew was dispatched to investigate. Upon arrival, the crew found evidence of a LV crossarm fire and a burnt LV service fuse mount. The crew made safe and made necessary repairs. There was evidence of a small ground fire at the base of pole.
1586 | Powercor 17/271 | Powercor | 2018-01-05 | 0.17778 | -36.34748529 | 145.59662461 | 205 COSGROVE-LEMNOS Rd., COSGROVE. | 30132664 | STN024 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 14079 | 20180522PWA_06 | Following a supply interruption there was a report of fallen conductors and a small ground fire at incident location.There was a ground fire, no reported injuries or third party property damage.
1587 | Powercor 17/272 | Powercor | 2018-02-05 | 0.14583 | -37.8214951 | 144.7868 | 144 Fitzgerald Rd., Laverton North. | 30112356 | LVN034 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 14031 | 20180503PWA_01 | Truck contacted pole and ground fire some distance away was attributed to fault current damage. A ground fire was reported at the address in this reportand crews found a HV cable termination requires repair. A separate report of a truck contacting a pole, twisting cross-arm and dislodging conductor was also received . This pole is on the same feeder and downstream of the ground fire location by some 2.1 Km.
1588 | Powercor 17/273 | Powercor | 2018-03-05 | 0.975 | -36.35414593 | 145.40550622 | 19-23 HAWKINS STREET, SHEPPARTON. | 32189058 | SHN012 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 14080 | 20180522PWA_07 | Vicfire reported pole fire on Hawkins Street, near Allen Street, Shepparton. Crew attended and found HV Intermediate crossarm had burnt the end of and was laying on LV crossarm of the substation. There was no ground fire, no injuries or third party property damage.
1589 | Powercor 17/274 | Powercor | 2018-04-05 | 0.42222 | -35.93991673 | 143.85841370 | 2126 LODDON RIVER Rd., APPIN SOUTH. | 32037296 | KGT004 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 14037 | 20180508PWA_01 | All supply failure reported, crew attended at incident location. They walked an inaccessible area and found SWER Intermediate Pole 6 Appin South had burnt off. An area of 100m Square was reported as burnt. There was no reported shocks, no injuries reported. No CFA in attendance.
1590 | Powercor 17/275 | Powercor | 2018-04-05 | 0.35556 | -36.47317657 | 145.32737911 | 350 POGUE Rd., TOOLAMBA. | 32188653 | MNA034 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 14038 | 20180509PWA_01 | A Powercor fault crew attending a feeder outage on MNA034 found that a pole top burnt through at Pogue P3E. There were shocks, no injuries or ground fire start.
1591 | Powercor 17/276 | Powercor | 2018-05-05 | 0.73958 | -37.56352500 | 144.56352500 | 107 LA COTE Rd., GREENDALE. | 30112192 | BMH003 | Low voltage AC (<1kV) | Rural Long | - fuse (any other type) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 14133 | 20180601PWA_01 | Customer called in to advise transformer is on fire and the fire brigade has been called and are on the way. On arrival the crew has advised that a Three-Phase FOLCB had overheated and burnt out on LV Service Pole. As a result of this, the burnt out FOLCB has fallen onto the ground below. There was no reported ground fire, third party damage, injury or shocks as a result of this incident.
1592 | Powercor 17/277 | Powercor | 2018-06-05 | 0.74306 | -37.59818410 | 143.69400501 | 205 HADDON SCHOOL Rd., HADDON. | 32013728 | BAS011 | Low voltage AC (<1kV) | Rural Long | - fuse (any other type) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 14036 | 20180507PWA_01 | A report was received from a customer of sparks coming from our pole at the above location. On arrival the crew found that the 100A FOLCB had overheated and caught fire. Molten plastic and metal had dropped to the ground and caused a small grass fire which burnt an area 5 x 1 metres. The CFA were onsite and had extinguished the fire. There was no injury, shock or third party damage.
1593 | Powercor 17/278 | Powercor | 2018-09-05 | 0.99375 | -37.70509973 | 144.55265570 | 2 MAPLEWOOD CLOSE, BROOKFIELD. | 31024012 | MLN013 | Low voltage AC (<1kV) | Rural Short | - fuse (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 14081 | 20180522PWA_08 | Customer called in to advise. Pole is on fire directly outside. Weather is raining customer is calling the Fire Brigade. On arrival the crew has advised that an FSD/Krone box has overheated and burnt out on transformer pole. The resultant heat has also caused the insulation to melt off the LV UG Street cct mains cable. There was no reported ground fire, third party damage, injury or shocks as a result of this incident
1594 | Powercor 17/279 | Powercor | 2018-10-05 | 0.11458 | -34.36673871 | 141.91747028 | MILLEWA Rd., MERRINEE. | 32140161 | RCT023 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 14048 | 20180510PWA_06 | Following on from a line patrol the crew found pole fire. There was no ground fire, no reported injuries or third party property damage. On arrival crew isolated supply and carried out repairs.
1595 | Powercor 17/280 | Powercor | 2018-11-05 | 0.53264 | -38.24997380 | 142.69077540 | 89 STUARTS Rd., FRAMLINGHAM. | 30047279 | TRG004 | Low voltage AC (<1kV) | Rural Short | - fuse (any other type) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 14084 | 20180522PWA_11 | Customer reported a fire on a pole at the incident location. On arrival, the crew found that a pole mounted LV fuse box had overheated, causing the box to melt and catch fire. There was no ground fire. There were no reported injuries or third party property damages.
1596 | Powercor 17/281 | Powercor | 17/05/2018 | 0.79514 | -37.24817646 | 144.76204451 | 21 WOODVALE CRESCENT, LANCEFIELD. | 33030123 | WND013 | Low voltage AC (<1kV) | Rural Long | - fuse (any other type) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 14064 | 20180518PWA_01 | Customer advised there appears to be a pole fire at incident location. On arrival the crew has advised that an FSD/Krone box has overheated and burnt out. There was no ground fire, no reported injuries and no third party property damage.
1597 | Powercor 17/282 | Powercor | 18/05/2018 | 0.34236 | -35.83217292 | 144.24728117 | 6134 MURRAY VALLEY HIGHWAY, COHUNA. | 32033895 | CHA003 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 14065 | 20180518PWA_02 | Vicfire reports pole fire at the incident location. A crew attended and found a pole top fire had occurred, damaging top of pole and Xarm. CFA attended. There were shocks, no injuries or ground fire start.
1598 | Powercor 17/283 | Powercor | 20/05/2018 | 0.60139 | -38.64077912 | 143.13356916 | 2310 PRINCETOWN Rd., PRINCETOWN. | 33037378 | COB011 | Low voltage AC (<1kV) | Rural Long | - fuse (any other type) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 14134 | 20180601PWA_02 | A customer reported pole on fire in the middle below transformer. On arrival the crew found a fuse box had been on fire and extinguished from the rain. No ground fire, injuries, 3rd party property damage was reported. On arrival crew isolated supply and carried out repairs.
1599 | Powercor 17/284 | Powercor | 23/05/2018 | 0.98958 | -36.41048686 | 145.24951414 | 6065 MIDLAND HIGHWAY, TATURA. | 30138758 | SHTS-SHP | Low voltage AC (<1kV) | Unknown | - fuse (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 14114 | 20180528PWA_03 | CFA reported transformer explosion and grass fire at incident location. On arrival crew found a FOLCB had failed. There was a 15x10 metre grass fir There was no reported injuries or third party property damage.
1600 | Powercor 17/285 | Powercor | 29/05/2018 | 0.86944 | -37.10183762 | 144.20551485 | 3 ELEANOR DRIVE, CAMPBELLS CREEK. | 30255740 | CMN001 | 22kV AC | Rural Long | - overhead conductor (insulated) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 14203 | 20180705PWA_02 | Customer reported transformer was on fire but still sparking and another neighbour had heard a loud bang. Crew attended and found that two of the HV insulated leads between HV fuse and HV bushings on transformer had crossed over on two of the phases and melted. There were no injuries, no ground fire, no third party property damage.
1601 | Powercor 17/286 | Powercor | 29/05/2018 | 0.58056 | -35.06657612 | 142.03510836 | WAKEFIELD Rd., WALPEUP. | 32147316 | OYN001 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started by lightning striking a distribution system or a part of a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 14130 | 20180531PWA_05 | A Powercor fault crew attending a feeder fault found that a burnt pole. Crew believed the pole was hit by lightning. The pole fell on to ground and burnt through. There was no injuries or third party property damage. On arrival crew arranged for isolation and pole was replaced.
1602 | Powercor 17/287 | Powercor | 29/05/2018 | 0.58056 | -35.06356516 | 142.03450703 | WAKEFIELD Rd., WALPEUP. | 32147329 | OYN001 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started by lightning striking a distribution system or a part of a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 14131 | 20180531PWA_06 | A Powercor fault crew attending a feeder fault found that a burnt pole. Crew believed the pole was hit by lightning. The pole fell on to ground and burnt through. There was no injuries or third party property damage. On arrival crew arranged for isolation and pole was replaced.
1603 | Powercor 17/288 | Powercor | 29/05/2018 | 0.63681 | -35.48458078 | 142.84699668 | CALDER HIGHWAY, SEA LAKE. | 32160325 | OYN005 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 14132 | 20180531PWA_07 | A Powercor fault crew attending an outage found a partially burnt pole top. There was no ground fire, no injuries or third party property damage. On arrival crew isolated supply and carried out repairs.
1604 | Powercor 17/289 | Powercor | 2018-07-06 | 0.16667 | -37.83921635 | 144.74575281 | 231 LEAKES Rd., TRUGANINA. | 30233147 | ATS-WBE | 66kV AC | Unknown | - insulators | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 14143 | 20180612PWA_02 | Multiple members of the public reported outages, flickering/low volts and hearing explosions. 22kV feeder CB tripped disconnecting 7630 customers. While patrolling the feeder, Powercor electrical operator Joel Guy observed a 66KV clamp top insulator detached, and suspended below its pole top structure. The polymeric, 66kV insulator had broken/sheared clear of its insulator stud mount on the pole’s centre phase, steel, P bracket The 37/3.75 AAC, centre phase, 66KV conductor had displaced to the roadside and came to rest on the 66kV steel crossarm. The centre phase has discharged through the cross arm, crossarm braces, into the 22kV arm and down through its braces, and into a 22kV cable head termination beneath. The discharge caused the pole to catch alight and the 22kV cable head termination to sustain some damage. The 66kV and 22kV was confirmed as de-energised and the Fire Brigade were instructed to hose the pole down. The fault appears to have originated at pole LIS 990959 ATS-WBE P67 Powercor crews attended and made the site safe. Powercor crews were dispatched to other sites along LV003 were other explosions were reported – as secondary faults to LIS 990959 The repair activity was transferred to a Lendlease day crew to replace the damaged assets. At LIS 990959 ATS-WBE P67 the three polymeric 66kV insulators were replaced with porcelain units, as well as three 22kV surge diverters and connections on the cable head. There were no shocks, reported injuries or ground fire.
1605 | Powercor 17/290 | Powercor | 2018-08-06 | 0.26389 | -35.50062546 | 142.84950254 | 121 HORACE STREET, SEA LAKE. | 31022293 | OYN005 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 14142 | 20180612PWA_01 | Vicfire reported a low conductor and pole fire at the incident location. On arrival the crew found that a wooden intermediate pole failed due to fire damage at the LV kingbolt position, resulting in the pole top assembly being suspended above the LV circuit below. There was no ground fire, no reported injuries, no 3rd party damage
1606 | Powercor 17/291 | Powercor | 20/06/2018 | 0.69722 | -37.69639282 | 144.56605598 | 64 Coburns Rd., Brookfield. | 30103173 | MLN013 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 14196 | 20180704PWA_01 | Burnt crossarm found replaced under EAP.
1607 | Powercor 17/292 | Powercor | 28/11/2017 | 0.76806 | -34.299 | 142.2209 | 166 Pumps Road, Red Cliffs | 33064221 | RCTS-MBN | 66kV AC | Unknown | - overhead conductor (bare; all aluminium conductor) | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13518 | 20171204PWA_02 | Report of lightning strike at the incident location. On arrival the crew found there had been a lighting strike to centre phase of RCTS-MBN 66/22KV had caused a small 300mm x 300mm grass fire around the earth stake of the customer installation. There were no reported shocks or injuries. LEI inspected installation and found no damage had been caused.
1608 | Powercor 17/293 | Powercor | 2018-09-06 | 0.79375 | -38.2941 | 143.2207 | 540 Purrumbete Estate, Koallah. | 32059366 | CDN002 | Low voltage AC (<1kV) | Rural Long | - fuse (any other type) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 14144 | 20180612PWA_04 | Vicfire reported a transformer fire at the incident location. On arrival the crew found that a 480V LV fuse box had burnt out at one end. There was no ground fire. There was no reported third party damage or any injuries.
1609 | Jamena 17/18 | Jamena | 2017-07-07 | 0.57431 | -37.7383 | 144.9488 | 12 SUSSEX STREET, PASCOE VALE SOUTH VIC 3044 | A048681 | CS 02 | 22kV AC | Urban | - crossarm (wood) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | SAP 10269353 | 20180817JEM_01 | Pole top fire
1610 | Jamena 17/19 | Jamena | 13/07/2017 | 0.37292 | -37.6684 | 144.9683 | 94 BARRY ROAD, CAMPBELLFIELD VIC 3061 | A025000 | BD16 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 151286 | 20170713JEM_01 | Broken tree branch started a fire when contacting the 22kv HV conductor
1611 | Jamena 17/20 | Jamena | 25/07/2017 | 0.47014 | -37.7687 | 145.0411 | 4 LIVINGSTONE STREET, IVANHOE | A109445 | FF90 | Low voltage AC (<1kV) | Urban | - underground cable | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 151805 | 20170727JEM_01 | LV UG cable was smouldering due to fault current
1612 | Jamena 17/21 | Jamena | 27/07/2017 | 0.77083 | -37.65 | 144.9616 | UNIT 7, 177-181 NORTHBOURNE ROAD, CAMPBELLFIELD VIC 3061 | A132829 | ST34 | Low voltage DC (<1.5kV) | Urban | - transformer (ground outdoor mounted) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 151940 | 20170728JEM_01 | High resistance connection caused overheating and resulted in the area around the transformer LV bushing to ignite
1613 | Jamena 17/22 | Jamena | 2017-07-08 | 0.76528 | -37.5666 | 144.9158 | 330 MT RIDLEY ROAD, MICKLEHAM VIC 3064 | A145352 | KLO22 | 22kV AC | Urban | - transformer (pole mounted) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 152676 | 20170808JEM_01 | Bird nest caught fire at top of transformer
1614 | Jamena 17/23 | Jamena | 29/10/2017 | 0.69444 | -37.7954 | 144.8874 | 30A ADELAIDE STREET, FOOTSCRAY VIC 3011 | A064775 | FE09 | Low voltage AC (<1kV) | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 155833 | 20171101JEM_01 | Small grass fire due to optus cable hitting LV conductors and causing sparks.
1615 | Jamena 17/24 | Jamena | 30/01/2018 | 0.41806 | -37.817 | 144.8497 | 551 GEELONG ROAD BROOKLYN VIC 3012 | A101771 | FW05 | 22kV AC | Urban | - crossarm (wood) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 159778 | 20180130JEM_02 | Pole top fire
1616 | Jamena 17/25 | Jamena | 2018-07-02 | 0.47431 | -37.7793 | 144.852 | 310 BALLARAT ROAD BRAYBROOK VIC 3019 | A073308 | BY11 | Low voltage AC (<1kV) | Urban | - switch (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 160105 | 20180315JEM_02 | Small grass fire due to failure of the LV ABC switch
1617 | Jamena 17/26 | Jamena | 22/02/2018 | 0.55 | -37.7242 | 144.9692 | 59-61 TRADE PLACE, COBURG NORTH VIC 3058 | A066643 | CN02 | 22kV AC | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 160887 | 20180222JEM_02 | small grass fire caused by molten conductor particles from a hot connection between the dropper and UG cable terminal.
1618 | Jamena 17/27 | Jamena | 28/02/2018 | 0.62153 | -37.773 | 144.8563 | 57 BARBARA CRESCENT, AVONDALE HEIGHTS VIC, 3034 | A094363 | BY14 | Low voltage AC (<1kV) | Urban | - switch (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 159551 | 20180816JEM_01 | Small grass fire due to failure of the LV ABC switch
1619 | Jamena 17/28 | Jamena | 28/02/2018 | 0.9652 | -37.7187 | 144.8898 | 23-27 VICTORY ROAD, AIRPORT WEST VIC 3042 | A087267 | AW05 | 22kV AC | Urban | - crossarm (wood) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | SAP 10278115 | 20180314JEM_01 | Pole top fire
1620 | Jamena 17/29 | Jamena | 2018-01-03 | 0.36042 | -37.6973 | 144.8805 | 83-85 MICKLEHAM ROAD, TULLAMARINE VIC 3043 | A031140 | AW09 | 22kV AC | Urban | - crossarm (wood) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 161223 | 20180309JEM_01 | Pole top fire
1621 | Jamena 17/30 | Jamena | 2018-01-03 | 0.30208 | -37.8028 | 144.9291 | 172-184 DYNON RD, WEST MELBOURNE VIC 3003 | A010091 | WMTSFE2 | 66kV AC | Urban | - crossarm (wood) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 161177 | 20180309JEM_02 | Pole top fire
1622 | Jamena 17/31 | Jamena | 2018-01-03 | 0.31389 | -37.6474 | 144.9443 | 8-10 SCAMMEL STREET, CAMPBELLFIELD VIC 3061 | A100460 | ST12 | 22kV AC | Urban | - crossarm (wood) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 161165 | 20180314JEM_03 | Pole top fire
1623 | Jamena 17/32 | Jamena | 2018-01-03 | 0.33125 | -37.7672 | 144.8551 | 26 BROWN STREET, AVONDALE HEIGHTS VIC 3034 | A047650 | BY11 | 22kV AC | Urban | - crossarm (wood) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 161167 | 20180314JEM_04 | Pole top fire
1624 | Jamena 17/33 | Jamena | 2018-01-03 | 0.67093 | -37.8057 | 144.8805 | 275 GEELONG ROAD, KINGSVILLE VIC 3012 | A052011 | FW08 | 22kV AC | Urban | - crossarm (wood) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 161219 | 20180314JEM_02 | Pole top fire
1625 | Jamena 17/34 | Jamena | 2018-02-03 | 0.52292 | -37.670219 | 144.7964 | 285 LOEMANS ROAD, BULLA VIC 3428 | A056421 | KTSSBY | 66kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 161256 | 20180302JEM_02 | Small grass fire resulting from bird coming into contact with 66kV across the bridging insulator.
1626 | Jamena 17/35 | Jamena | 17/03/2018 | 0.51111 | -37.728 | 145.0458 | 46 CRISSANE ROAD, BUNDOORA VIC 3083 | A031466 | NH16 | 22kV AC | Urban | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 161840 | 20180317JEM_02 | Fault current induced connection failure resulted in small grass fire
1627 | Jamena 17/36 | Jamena | 2018-10-05 | 0.50903 | -37.702 | 145.025 | 33 ARGYLE STREET, RESERVOIR VIC 3073 | A033475 | TT 03 | 22kV AC | Urban | - crossarm (wood) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 163801 | 20180510JEM_01 | Pole top fire
1628 | Jamena 17/37 | Jamena | 2018-01-06 | 0.45694 | -37.8306 | 144.8817 | 598 MELBOURNE ROAD, SPOTSWOOD | A059775 | YVE012 | 22kV AC | Urban | - crossarm (wood) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | SAP 10281595 | 20180817JEM_02 | Pole top fire
1629 | CitiPower 17/18 | CitiPower | 27/07/2017 | 0.29861 | -37.79215818 | 145.00015339 | 18 Kiewa St., Clifton Hill. | 30169158 | F029 | Low voltage AC (<1kV) | Urban | - fuse (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 13259 | 20170728PWA_01 | A passer-by reported that the pole is on fire at the incident location. On arrival the fault crew found that a krone box had overheated caught fire and debris had fallen onto the footpath at the incident location. The krone box fire self-extinguished.
1630 | CitiPower 17/19 | CitiPower | 14/07/2017 | 0.57083 | -37.82894203 | 144.92291095 | 115 Salmon St., Port Melbourne. | 30218476 | PM004 | Low voltage AC (<1kV) | Urban | - fuse (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 13268 | 20170731PWA_03 | MFB reported a fire on building wall at the incident location. Upon arrival, the CitiPower crew found that the 3Ph meter board caught fire. The crew believe overheated connections/fuses ignited the box. There were no injuries, third party damages or ground fire. The repairs arranged. MFB attended.
1631 | CitiPower 17/20 | CitiPower | 2017-06-08 | 0.98889 | -37.79809268 | 144.97472982 | 1 Barkly St., Carlton. | 30180584 | BQ041 | Low voltage AC (<1kV) | Urban | - luminaires (minor road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 13290 | 20170807PWA_01 | MFB reported a street light pole on fire at the above incident location. On arrival, the crew found that MFB had extinguish the fire out of a Public Lighting head unit as it had faulted and caught on fire. There was no ground fire nor third party damaged. There were no reported injuries.
1632 | CitiPower 17/21 | CitiPower | 2017-04-08 | 0.27222 | -37.85700177 | 145.02074312 | 3A Hume St., Armadale. | 30166655 | AR011 | Low voltage AC (<1kV) | Urban | - luminaires (minor road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 13323 | 20170817PWA_02 | MFB reports a pole fire at the above address. A crew attended and found a PE cell in a 80 MV public light had over heated and caught fire. MFB where onsite and extinguished fire. Crew replaced PE cell. Lantern still serviceable. No ground fire start. There were no reported shocks, injuries or 3rd party damage.
1633 | CitiPower 17/22 | CitiPower | 2017-09-11 | 0.13056 | -37.83048 | 144.992233 | 131 Cubitt St., Cremorne. | 30187885 | R031 | Low voltage AC (<1kV) | Urban | - fuse (any other type) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13523 | 20171207PWA_02 | MFB reported a garage fire at incident location. On arrival it was found that the fire affected customer’s garage. The fire appears to have started at the meter board position. There was a small ground fire (3x2 m). On arrival supply isolated. Repairs where to be co-ordinated with customer REC for the customer to resume supply. There were no injuries reported.
1634 | CitiPower 17/23 | CitiPower | 28/12/2017 | 0.55 | -37.84368992 | 144.99064922 | 58A Osborne St., South Yarra. | 30217304 | BC024 | Low voltage AC (<1kV) | Urban | - fuse (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13554 | 20180103PWA_02 | The MFB notified the CitiPower report room of a pole box fire . Upon attendance the CitiPower faults crew found the FOLCB supplying customers at 58A, 58B, 51 and 53 Osborne St, South Yarra had been damaged
1635 | CitiPower 17/24 | CitiPower | 26/12/2017 | 0.86319 | -37.78554194 | 145.08690298 | 430 Balwyn road, Balwyn North. | 30186091 | WD021 | Low voltage AC (<1kV) | Urban | - fuse (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13557 | 20180102PWA_07 | MFB reported a pole fire at the above incident location. On arrival, the crew found that the overhead line fuse box unit had overheated and caught on fire.
1636 | CitiPower 17/25 | CitiPower | 2017-03-12 | 0.92153 | -37.77266954 | 144.99825060 | 257 High St., Northcote. | 30190763 | NC005 | Low voltage AC (<1kV) | Urban | - luminaires (minor road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13588 | 20180115PWA_04 | Street light fire outside 257 High st Northcote. There was no ground fire, no reported injuries and no third party property damage.
1637 | CitiPower 17/26 | CitiPower | 19/01/2018 | 0.083333 | -37.83218392 | 145.00637820 | 159 Alexandra Ave., Toorak. | 30216322 | TK001 | Low voltage AC (<1kV) | Urban | - fuse (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 13606 | 20180119PWA_04 | The MFB reported a pole fire at the incident location. On arrival the fault crew found that a FMJB had overheated burning material fell to the ground igniting a small grass fire at the base of the pole , fire self-extinguished. There was no injury as a result of this incident.
1638 | CitiPower 17/27 | CitiPower | 24/03/2018 | 0.46667 | -37.80961 | 145.099258 | 9 FITZGERALD STREET, BALWYN. | 30176449 | WD032 | Low voltage AC (<1kV) | Urban | - overhead service conductor (residential) | two phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13913 | 20180327PWA_03 | Vicfire reported a small grass fire in the front yard of 9 Fitzgerald Street, Balwyn. On Arrival the CitiPower crew found a private tree within the yard of 9 Fitzgerald St, Balwyn had bought down the overhead service to the property. The crew found the insulation of the service wire had been damage by the tree and a 15m2 charring mark was found on the grass. There was no reported injuries, no third party damage, no shocks.
1639 | CitiPower 17/28 | CitiPower | 19/03/2018 | 0.69792 | -37.84241276 | 144.95008367 | 229 BRIDPORT STREET W, ALBERT PARK. | 30173056 | AP003 | 11kV AC | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 13923 | 20180328PWA_05 | A customer reported that there is a grass fire adjacent the incident location. On arrival the fault crew found that fault current had caused overheating of a high voltage connection which ejected hot debris onto the ground igniting a small grass fire approximately 3m by 2m in area. The fire self-extinguished. There was no injury as a result of this incident.
1640 | CitiPower 17/29 | CitiPower | 17/04/2018 | 0.0020833 | -37.82184765 | 144.96572042 | 70 City Rd., Southbank. | 30160563 | SO022 | Low voltage AC (<1kV) | CBD | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 14063 | 20180517PWA_03 | MFB reported pole fire at incident location. There was no ground fire, no reported injuries or third property damages.
1641 | Ausnet 17/18 | Ausnet | 2017-01-07 | 42917.559 | -38.0961 | 146.5491 | 19 HAKEA COURT, GLENGARRY NORTH VIC 3854 | 2602078 | TGN31 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | HBRA only | 1 | NO FORECAST | 0.1 | 0.1 | 228880 | 20170824SPN_01 | EDO fuse tube burnt off
1642 | Ausnet 17/19 | Ausnet | 2017-01-07 | 42917.6507 | -37.9847 | 145.4638 | 80 BLUE RIDGE ROAD, DEWHURST VIC 3808 | 521902 | BWN14 | Low voltage AC (<1kV) | RURAL SHORT | - connection box | three phase | Otherwise started by a distribution system | HBRA only | 1 | NO FORECAST | 0.1 | 0.1 | 228875 | 20170824SPN_02 | suspected loose connection within the FOLCB
1643 | Ausnet 17/20 | Ausnet | 2017-06-07 | 42922.3674 | -37.8937 | 145.2919 | 61 GLENFERN ROAD, FERNTREE GULLY VIC 3156 | 1302470 | FGY22 | 22kV AC | URBAN | Other | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | 229035 | 20170706SPN_03 | Investigation completed with following findings: The root cause of the intermittent internal capacitor can failure is believed to be due to insulation failure between capacitor foils within the can. Intermittent nature of the capacitor fault does not last long enough to trigger the circuit breaker to trip. The non-operation of the No2 Cap Bank protection relay was confirmed to be correct and as expected for an intermittent type fault. The Cap Bank protection relay was subsequently tested and found to operate as designed.
1644 | Ausnet 17/21 | Ausnet | 2017-08-07 | 42924.3167 | -36.2329 | 147.8476 | 234 WATERS LANE, COLAC COLAC VIC 3707 | 5215357 | WOTS24 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | NO FORECAST | 0.1 | 0.46 | 229085 | 20170713SPN_02 | EDO fuse hung up
1645 | Ausnet 17/22 | Ausnet | 19/07/2017 | 42935.4208 | -36.3649 | 146.4863 | 501 RUSHOLME ROAD, TARRAWINGEE VIC 3678 | 5111668 | WN5 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | NO FORECAST | 0.1 | 0.46 | 229279 | 20170911SPN_02 | EDO fuse candling. Maybe attributable to bird found nearby.
1646 | Ausnet 17/23 | Ausnet | 2017-02-08 | 42949.2361 | -38.287 | 146.1907 | 1159 MORWELL-THORPDALE ROAD, THORPDALE VIC 3835 | 2207558 | MOE31 | 22kV AC | RURAL LONG | - dropper / bridge | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | NO FORECAST | 0.1 | 0.46 | 229555 | 20170803SPN_01 | Defective dropper.
1647 | Ausnet 17/24 | Ausnet | 2017-02-08 | 42949.7743 | -38.4765 | 145.9465 | 2 BAIR STREET, LEONGATHA VIC 3953 | 2003702 | LGA22 | Low voltage AC (<1kV) | RURAL SHORT | - connection box | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | 229563 | 20170803SPN_02 | There were no visible causes for krone box failing. Probable high customer volts or/and poor connection.
1648 | Ausnet 17/25 | Ausnet | 2017-03-08 | 42950.8264 | -38.1808 | 147.0901 | 10 ANDREWS ROAD, LONGFORD VIC 3851 | 2505283 | SLE31 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | NO FORECAST | 0.1 | 0.46 | 229580 | 20170807SPN_01 | On arrival - fault crew observed candling BA on SL245 LIs No 2505283, Nil fire damage to ground. Note blown EDO fuse also at Sub pole LIS 1614360 WELLINGTON COBB SUB. Cause of Fault determined to be defective Surge Divertor on Wellington Cobb Substation.
1649 | Ausnet 17/26 | Ausnet | 14/08/2017 | 42961.4535 | -35.9999 | 146.4948 | 445 UP RIVER ROAD, CARLYLE VIC 3685 | 5209079 | BWA23 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | NO FORECAST | 0.1 | 0.46 | 229737 | 20170911SPN_01 | EDO fuse hung up - moisture ingress and incorrect type (fixed fire chokes) previously fitted.
1650 | Ausnet 17/27 | Ausnet | 25/08/2017 | 42972.8104 | -37.8885 | 145.2945 | CAR YARD, 1097 BURWOOD HIGHWAY, FERNTREE GULLY VIC 3156 | 1312538 | FGY23 | Low voltage AC (<1kV) | URBAN | - lamps (major road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | 229982 | 20170830SPN_01 | the street light PE cell had failed and caught fire
1651 | Ausnet 17/28 | Ausnet | 2017-02-09 | 42980.2743 | -36.6631 | 145.471 | 1549 ARCADIA TWO CHAIN ROAD, MIEPOLL VIC 3666 | 3904466 | BN1 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | NO FORECAST | 0.1 | 0.46 | 230120 | 20170904SPN_02 | EDO fuse hung up. Likely interference of bird - no photo to support.
1652 | Ausnet 17/29 | Ausnet | 2017-03-09 | 42981.5868 | -37.0525 | 148.8086 | 1900 BONANG ROAD, DELEGATE RIVER VIC 3888 | 5768315 | BM8B31 | 22kV AC | RURAL SHORT | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | NO FORECAST | 0.1 | 0.1 | 230123 | 20170904SPN_01 | Fault crew observed evidence of fire onsite but extinguished. Tree fell over mains and conductor fell to the ground in the area.
1653 | Ausnet 17/30 | Ausnet | 2017-04-09 | 42982.9958 | -37.8609 | 148.0344 | 45 LAKE BUNGA BEACH ROAD, LAKE BUNGA VIC 3909 | 1902793 | NLA34 | Low voltage AC (<1kV) | RURAL SHORT | - connection box | two phase | Otherwise started by a distribution system | HBRA only | 1 | NO FORECAST | 0.1 | 0.1 | 230171 | 20170905SPN_03 | likely caused by polluted insulator (salt )
1654 | Ausnet 17/31 | Ausnet | 2017-05-09 | 42983.6271 | -38.5609 | 145.7132 | 590 INVERLOCH-KONGWAK ROAD, WATTLE BANK VIC 3995 | 5656096 | WGI22 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | NO FORECAST | 0.1 | 0.46 | 230177 | 20171023SPN_02 | BA fuse candled.
1655 | Ausnet 17/32 | Ausnet | 2017-07-09 | 42985.7083 | -38.1002 | 146.0325 | 1965 OLD SALE ROAD, SHADY CREEK VIC 3821 | 2706751 | WGL24 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | HBRA only | 1 | NO FORECAST | 0.1 | 0.1 | 230207 | 20170912SPN_01 | BA fuse candling
1656 | Ausnet 17/33 | Ausnet | 2017-11-09 | 42989.7819 | -37.6721 | 145.1265 | 311 YAN YEAN ROAD, PLENTY VIC 3090 | 926107 | ELM15 | Low voltage AC (<1kV) | RURAL SHORT | - overhead conductor (bare; copper) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | NO FORECAST | 0.1 | 0.46 | 230242 | 20171023SPN_03 | Heat generated from the poor connection caused the cable to fail and fall to the ground. The hot particles of the IPC and/ or copper cable could have made contact with the ground. no photo is available.
1657 | Ausnet 17/34 | Ausnet | 19/09/2017 | 42997.3556 | -38.493 | 145.2968 | 128 MCFEES ROAD, RHYLL VIC 3923 | 2805565 | PHI11 | 22kV AC | RURAL SHORT | - overhead conductor (bare; aluminium core steel reinforced) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | NO FORECAST | 0.1 | 0.1 | 230386 | 20171024SPN_01 | vegetation contact
1658 | Ausnet 17/35 | Ausnet | 2017-08-10 | 43016.6687 | -38.0775 | 145.2857 | 46 MARINER CLOSE, CRANBOURNE NORTH VIC 3977 | 594816 | CRE23 | 22kV AC | URBAN | - transformer (kiosk mounted) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | 230654 | 20171020SPN_01 | The root cause could not be determined.
1659 | Ausnet 17/36 | Ausnet | 2017-10-10 | 43018.4444 | -36.1362 | 146.9018 | 169 CHAPPLE STREET, WODONGA VIC 3690 | 5219216 | WOTS12 | 22kV AC | RURAL SHORT | - fuse (powder filled) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | 230691 | 20171129SPN_02 | Fuse candling
1660 | Ausnet 17/37 | Ausnet | 2017-12-10 | 43020.7361 | -37.948 | 145.4873 | 8 FERN GULLY ROAD, COCKATOO VIC 3781 | 417489 | BGE22 | 22kV AC | RURAL SHORT | - fuse (boric acid) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | 230730 | 20171129SPN_03 | candled fuse no photo available
1661 | Ausnet 17/38 | Ausnet | 15/10/2017 | 43023.4167 | -37.7247 | 147.8019 | 1881 GREAT ALPINE ROAD, WISELEIGH VIC 3885 | 1604421 | BDL8 | 22kV AC | RURAL LONG | - switch (disconnector/isolator) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | NO FORECAST | 0.1 | 0.46 | 230752 | 20171023SPN_01 | 22kV Blade isolator failed with fixed jaw burnt out.
1662 | Ausnet 17/39 | Ausnet | 19/10/2017 | 43027.4701 | -38.0379 | 145.2486 | 108-110 ROBJANT STREET, HAMPTON PARK VIC 3976 | 505186 | HPK23 | 22kV AC | URBAN | - switch (disconnector/isolator) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | 230821 | 20171114SPN_03 | bird nest on the gas switch open point
1663 | Ausnet 17/40 | Ausnet | 24/10/2017 | 43032.4271 | -37.6316 | 145.0454 | QUARRY ROAD, EPPING VIC 3076 | 914098 | EPG32 | 22kV AC | RURAL SHORT | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | 230893 | 20171114SPN_02 | bird strike, conductor down.
1664 | Ausnet 17/41 | Ausnet | 24/10/2017 | 43032.4861 | -38.0172 | 147.0048 | 36 COBAINS ROAD, BUNDALAGUAH VIC 3851 | 2511666 | MFA23 | 22kV AC | RURAL SHORT | - overhead conductor (bare; steel) | single phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | 230896 | 20171102SPN_02 | bird likely killed by a flashover fell to the ground and started the fire
1665 | Ausnet 17/42 | Ausnet | 27/10/2017 | 43035.8542 | -37.7988 | 147.8772 | 197 CUNNINGHAM ROAD, SWAN REACH VIC 3903 | 1911236 | BDL41 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | 230961 | 20171128SPN_01 | Burnt EDO fuse tube.
1666 | Ausnet 17/43 | Ausnet | 2017-10-11 | 43049.8444 | -36.0954 | 146.32 | 1447 LILLIPUT-NORONG ROAD, NORONG VIC 3682 | 5235554 | WN3 | 12.7kV AC (SWER) | RURAL LONG | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | 231154 | 20171114SPN_01 | A tree on the customer's property fell over and contacted the overhead HV conductor.
1667 | Ausnet 17/44 | Ausnet | 16/11/2017 | 43055.7729 | -38.152 | 145.5741 | 165 BUNYIP RIVER ROAD, NAR NAR GOON VIC 3812 | 512440 | PHM33 | Low voltage AC (<1kV) | RURAL LONG | - connection box | single phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | 231255 | 20171117SPN_01 | Burnt out pole junction box.
1668 | Ausnet 17/45 | Ausnet | 21/11/2017 | 43060.3056 | -37.6064 | 145.4125 | 35 LORIMERS LANE, DIXONS CREEK VIC 3775 | 1007063 | LDL14 | Low voltage AC (<1kV) | RURAL SHORT | - underground service cable (residential) | two phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | 231317 | 20171123SPN_03 | Underground service cable fault.
1669 | Ausnet 17/46 | Ausnet | 21/11/2017 | 43060.4271 | -37.7165 | 145.0986 | 152 ELDER STREET, GREENSBOROUGH VIC 3088 | 928045 | WT15 | Low voltage AC (<1kV) | URBAN | - overhead conductor (bare; aluminium core steel reinforced) | two phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | 231318 | 20171127SPN_02 | A truck contacted Telstra overhead assets which caused them to make contact with AusNet Services' overhead LV distribution conductors.
1670 | Ausnet 17/47 | Ausnet | 22/11/2017 | 43061.2937 | -37.4367 | 144.9778 | 20 MACSFIELD ROAD, WALLAN VIC 3756 | 912838 | KLO24 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | 231358 | 20171220SPN_01 | Candled EDO fuse tube.
1671 | Ausnet 17/48 | Ausnet | 22/11/2017 | 43061.7708 | -37.6742 | 145.8598 | 20 UPPER YARRA DAM ROAD, REEFTON VIC 3799 | 1409238 | WYK13 | Low voltage AC (<1kV) | RURAL SHORT | - overhead service conductor (residential) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | 231367 | 20171123SPN_04 | Street light service cable fell to ground due to burnt through wrap-on preform termination.
1672 | Ausnet 17/49 | Ausnet | 25/11/2017 | 43064.5069 | -36.4404 | 146.374 | MIRANDA HIGH COUNTRY WINE, 1019 SNOW ROAD, OXLEY VIC 3678 | 5103451 | WN5 | 22kV AC | RURAL LONG | - fuse (boric acid) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | 231400 | 20180111SPN_04 | Candled BA fuse tube.
1673 | Ausnet 17/50 | Ausnet | 26/11/2017 | 43065.4167 | -38.4336 | 146.0371 | 105 STRZELECKI HWY, BOOROOl VIC 3953 | 2002447 | LGA11 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | 231401 | 20171220SPN_04 | Burnt EDO fuse tube.
1674 | Ausnet 17/51 | Ausnet | 27/11/2017 | 43066.4694 | -36.8929 | 145.2075 | ROSEDALE FARM, 729 AERODROME ROAD, AVENEL VIC 3664 | 4706126 | SMR8 | 22kV AC | RURAL LONG | - overhead conductor (bare; steel) | single phase | Started by any other thing forming part of or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | 231422 | 20171204SPN_01 | A tip truck trailer made contact with overhead 22kV line.
1675 | Ausnet 17/52 | Ausnet | 28/11/2017 | 43067.2715 | -38.5519 | 146.1267 | 20 BUTTERWORTHS ROAD, STONY CREEK VIC 3957 | 2013243 | LGA13 | 12.7kV AC (SWER) | RURAL LONG | - fuse (EDO fuse) | single wire earth return (SWER) | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | 231444 | 20180111SPN_06 | EDO fuse tube candled.
1676 | Ausnet 17/53 | Ausnet | 28/11/2017 | 43067.5729 | -37.8264 | 145.4511 | 90 MONBULK-SEVILLE ROAD, WANDIN EAST VIC 3139 | 1012337 | LDL13 | 22kV AC | RURAL SHORT | - transformer (pole mounted) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | 231451 | 20171129SPN_01 | Transformer internal fault. Oil leak - Mechanical damage (leaking gasket/broken bushing etc.).
1677 | Ausnet 17/54 | Ausnet | 29/11/2017 | 43068.6146 | -37.6285 | 145.0968 | 1079 PLENTY ROAD, SOUTH MORANG VIC 3752 | 917432 | DRN11 | 22kV AC | RURAL SHORT | - underground cable | three phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | 231481 | 20171130SPN_01 | Underground asset failure - fault at the Cable Head Pole (CHP).
1678 | Ausnet 17/55 | Ausnet | 29/11/2017 | 43068.6701 | -38.2946 | 146.5977 | 55 WHITELAWS TRACK, CALLIGNEE VIC 3844 | 2605775 | TGN23 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | single phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | 231480 | 20171130SPN_02 | Bird flew into EDO fuse unit on concrete pole resulting in a flashover and deceased bird.
1679 | Ausnet 17/56 | Ausnet | 30/11/2017 | 43069.8868 | -37.0643 | 146.0756 | 82 STONELEIGH ROAD, MANSFIELD VIC 3722 | 3918752 | MSD1 | 22kV AC | RURAL LONG | - fuse (boric acid) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | 231500 | 20171204SPN_02 | Bird caused a flashover. No photos are available.
1680 | Ausnet 17/57 | Ausnet | 2017-01-12 | 43070.1521 | -38.4779 | 146.0207 | 15 PORS ROAD, NERRENA VIC 3953 | 2008120 | LGA14 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | 231499 | 20180115SPN_03 | EDO fuse candled.
1681 | Ausnet 17/58 | Ausnet | 2017-02-12 | 43071.8187 | -38.1332 | 145.7361 | 105 KNIGHTS ROAD, LONGWARRY VIC 3816 | 2716128 | WGL12 | Low voltage AC (<1kV) | RURAL LONG | - connection box | single phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | 231507 | 20180116SPN_02 | Cause not identified but most likely due to high impedance fault.
1682 | Ausnet 17/59 | Ausnet | 2017-04-12 | 43073.4826 | -37.7808 | 145.4272 | 7 UNION ROAD, WANDIN NORTH VIC 3139 | 1002142 | LDL23 | Low voltage AC (<1kV) | RURAL LONG | - lamps (minor road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | 231520 | 20180117SPN_01 | Burnt out street light fitting. The damage was contained within the light head.
1683 | Ausnet 17/60 | Ausnet | 2017-08-12 | 43077.3812 | -38.6307 | 146.3491 | 465 SILCOCKS HILL ROAD, TOORA NORTH VIC 3962 | 2014437 | FTR12 | 12.7kV AC (SWER) | RURAL LONG | - pole (wood) | single wire earth return (SWER) | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | 231603 | 20180117SPN_02 | Broken pole stay wire.
1684 | Ausnet 17/61 | Ausnet | 2017-09-12 | 43078.5479 | -37.7565 | 145.2253 | 254 Gold Memorial Rd, Warrandyte VIC 3113 | 1224905 | RWN33 | 22kV AC | RURAL SHORT | - overhead conductor (bare; steel) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | 231784 | 20171213SPN_01 | Tree fell onto overhead HV line.
1685 | Ausnet 17/62 | Ausnet | 13/12/2017 | 43082.6444 | -38.1966 | 146.3253 | Haunted Hills Road, Newborough VIC 3825 | 5614362 | MOE31 | Low voltage AC (<1kV) | RURAL LONG | - switch (disconnector/isolator) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | 231688 | 20171214SPN_01 | Loose fuse in LV fuse isolator.
1686 | Ausnet 17/63 | Ausnet | 13/12/2017 | 43082.9069 | -38.0184 | 145.2998 | Magid Drive, Narre Warren VIC 3805 | 593824 | HPK12 | Low voltage AC (<1kV) | URBAN | - lamps (major road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | 231963 | 20180201SPN_01 | HPS street lantern head caught fire due to faulty capacitor.
1687 | Ausnet 17/64 | Ausnet | 14/12/2017 | 43083.4681 | -37.6006 | 145.0956 | 575 BRIDGE INN ROAD, MERNDA VIC 3754 | 917516 | DRN12 | Low voltage AC (<1kV) | RURAL SHORT | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | 231699 | 20171215SPN_01 | Broken LV copper conductor.
1688 | Ausnet 17/65 | Ausnet | 18/12/2017 | 43087.6799 | -38.1343 | 147.0954 | Sale Common Nature Reserve | 1613390 | SLE-LFD 66kV | 66kV AC | UNCLASSIFIED | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | 231768 | 20171219SPN_02 | An Eagle caused a flashover to earth on a 66kV pole structure.
1689 | Ausnet 17/66 | Ausnet | 18/12/2017 | 43087.7681 | -38.2002 | 146.3168 | 3-7 HAUNTED HILLS ROAD, NEWBOROUGH VIC 3825 | 596942 | MOE13 | Low voltage AC (<1kV) | RURAL SHORT | - fuse (any other type) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | 231769 | 20171219SPN_03 | Loose LV fuse hinge at pole.
1690 | Ausnet 17/67 | Ausnet | 18/12/2017 | 43087.9431 | -37.6905 | 145.1036 | 2 GOONYAH COURT, GREENSBOROUGH VIC 3088 | 5720887 | ELM31 | Low voltage AC (<1kV) | URBAN | - LV pillar | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | 231770 | 20171219SPN_04 | Root cause not designated in IMS but appears to be a 3 phase short circuit. Request made to Engineering to investigate.
1691 | Ausnet 17/68 | Ausnet | 19/12/2017 | 43088.7708 | -37.7758 | 145.3375 | 456-458 HULL ROAD, MOOROOLBARK VIC 3138 | 1014723 | LDL24 | 22kV AC | URBAN | - pole (concrete) | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | VERY HIGH | 1 | 0.2 | 231792 | 20171221SPN_02 | Lightning strike to concrete HV pole
1692 | Ausnet 17/69 | Ausnet | 26/12/2017 | 43095.6042 | -36.3831 | 146.2575 | 235 GRAVEL PIT ROAD, WANGARATTA SOUTH VIC 3678 | 5121021 | WN4 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | 231819 | 20180102SPN_01 | EDO fuse candling
1693 | Ausnet 17/70 | Ausnet | 27/12/2017 | 43096.4826 | -38.1355 | 146.5577 | 675 TRARALGON-MAFFRA ROAD, GLENGARRY VIC 3854 | 2601158 | TGN31 | 22kV AC | RURAL LONG | - dropper / bridge | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | 231820 | 20180102SPN_02 | Bird strike
1694 | Ausnet 17/71 | Ausnet | 27/12/2017 | 43096.4986 | -37.7817 | 145.2097 | 2-4 DRAYTON CRESCENT, PARK ORCHARDS VIC 3114 | 1205256 | RWN26 | 22kV AC | RURAL SHORT | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | 231822 | 20180102SPN_03 | trees brought down HV line and caused HV to contact LV lines
1695 | Ausnet 17/72 | Ausnet | 29/12/2017 | 43098.884 | -37.9877 | 147.0769 | 71 AIRLY ROAD, STRATFORD VIC 3862 | 2511827 | MFA21 | 22kV AC | RURAL LONG | - transformer (pole mounted) | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | 231828 | 20180102SPN_05 | Lightning strike to substation transformer.
1696 | Ausnet 17/73 | Ausnet | 31/12/2017 | 43100.4729 | -37.8566 | 145.2376 | 20 MARIEMONT AVENUE, WANTIRNA VIC 3152 | 5804164 | BRA32 | Low voltage AC (<1kV) | URBAN | - LV pillar | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | 231962 | 20180214SPN_02 | Electrical breakdown of old HRC fuse fittings inside LV pillar.
1697 | Ausnet 17/74 | Ausnet | 2018-04-01 | 43104.5618 | -38.1006 | 145.7447 | 260 COOK ROAD, LONGWARRY VIC 3816 | 2709198 | WGL12 | 22kV AC | RURAL LONG | - insulators | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | 231845 | 20180111SPN_03 | Bird caused a flashover at pole top.
1698 | Ausnet 17/75 | Ausnet | 2018-04-01 | 43104.7326 | -38.1609 | 145.6139 | 215 NUMBER SEVEN DRAIN ROAD, CORA LYNN VIC 3814 | 512759 | PHM33 | 22kV AC | RURAL LONG | - fuse (boric acid) | three phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | 231839 | 20180214SPN_04 | Burnt BA fuse tube / candled.
1699 | Ausnet 17/76 | Ausnet | 2018-04-01 | 43104.766 | -37.3784 | 144.9636 | LAURENVALE, 1935 OLD SYDNEY ROAD, WALLAN VIC 3756 | 4718426 | SMTS-KMS 66kV | 66kV AC | UNCLASSIFIED | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | 231863 | 20180111SPN_02 | Tree leaning on 66 kV overhead conductors.
1700 | Ausnet 17/77 | Ausnet | 2018-06-01 | 43106.3917 | -37.7356 | 145.2224 | 2 KANGAROO GROUND-WARRANDYTE ROAD, NORTH WARRANDYTE VIC 3113 | 1206325 | RWN34 | 22kV AC | RURAL SHORT | - overhead conductor (ABC) | three phase | Otherwise started by a distribution system | within electric line construction area | 19.8 | EXTREME | 3.5 | 69.3 | 231899 | 20180108SPN_01 | The catenary wire shorted to HVABC conductor.
1701 | Ausnet 17/78 | Ausnet | 2018-12-01 | 43112.2653 | -37.9253 | 145.4975 | 137 WOORI YALLOCK ROAD, COCKATOO VIC 3781 | 420317 | BGE22 | 22kV AC | RURAL SHORT | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | VERY HIGH | 1 | 0.2 | 231978 | 20180112SPN_01 | A large branch failed from a large gum tree due to decay from an old wound fell into overhead HV and LV conductors.
1702 | Ausnet 17/79 | Ausnet | 2018-12-01 | 43112.6847 | -37.6918 | 144.9605 | metropolitan ring road | 5642607 | SMTS-KMS 66kV | 66kV AC | UNCLASSIFIED | - pole (wood) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | 231993 | 20180205SPN_01 | insulator tracking
1703 | Ausnet 17/80 | Ausnet | 15/01/2018 | 43115.7139 | -38.5868 | 146.0123 | 100 MCILWAINE STREET, MEENIYAN VIC 3956 | 2001927 | LGA14 | 22kV AC | RURAL LONG | - overhead conductor (bare; steel) | three phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | 232036 | 20180116SPN_01 | HV conductor on ground. Some signs of corrosion.
1704 | Ausnet 17/81 | Ausnet | 16/01/2018 | 43116.8569 | -36.6932 | 146.8635 | 457 MOUNT BUFFALO ROAD, POREPUNKAH VIC 3740 | 4505257 | BRT22 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | 232052 | 20180220SPN_01 | Burnt EDO Fuse Tube
1705 | Ausnet 17/82 | Ausnet | 19/01/2018 | 43119.7757 | -37.6786 | 145.1443 | 1 PLEASANT VIEW COURT, DIAMOND CREEK VIC 3089 | 924181 | ELM32 | Low voltage AC (<1kV) | URBAN | - switch (disconnector/isolator) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | SEVERE | 2 | 0.4 | 232087 | 20180122SPN_02 | Hot connections at crossarm mounted LV fuse isolator.
1706 | Ausnet 17/83 | Ausnet | 20/01/2018 | 43120.8889 | -37.9372 | 145.4889 | 10 NEVILLE STREET, COCKATOO VIC 3781 | 417268 | BGE22 | 22kV AC | RURAL SHORT | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | 232090 | 20180122SPN_01 | Tree branch fell onto overhead HV line.
1707 | Ausnet 17/84 | Ausnet | 21/01/2018 | 43121.9486 | -37.8144 | 145.2545 | 32 VICTORIA STREET, RINGWOOD EAST VIC 3135 | 1217471 | RWT32 | Low voltage AC (<1kV) | URBAN | - fuse (any other type) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | 232095 | 20180202SPN_01 | Burnt out LV FSD Krone box.
1708 | Ausnet 17/85 | Ausnet | 23/01/2018 | 43123.0833 | -38.2339 | 146.2926 | 60 YASMIN DRIVE, HERNES OAK VIC 3825 | 2208544 | MOE31 | Low voltage AC (<1kV) | RURAL LONG | - connection box | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | 232114 | 20180123SPN_01 | Burnt out LV fuse Mains box. High impedance fault.
1709 | Ausnet 17/86 | Ausnet | 24/01/2018 | 43124.8465 | -38.5761 | 145.8457 | 965 KOONWARRA-INVERLOCH ROAD, LEONGATHA SOUTH VIC 3953 | 2010941 | LGA23 | 22kV AC | RURAL LONG | - connector / termination | three phase | Otherwise started by a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | 232136 | 20180125SPN_01 | Corroded and loose PG clamps on bridges lead to arcing.
1710 | Ausnet 17/87 | Ausnet | 28/01/2018 | 43128.2208 | -37.726 | 145.1404 | 32 ELY STREET, ELTHAM VIC 3095 | 900437 | ELM34 | Low voltage AC (<1kV) | RURAL SHORT | - overhead conductor (covered uninsulated) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | VERY HIGH | 1 | 0.2 | 232161 | 20180129SPN_02 | LV transformer lead burned through IPC which dripped hot metal which started a small fire.
1711 | Ausnet 17/88 | Ausnet | 28/01/2018 | 43128.5451 | -36.2229 | 147.2575 | 201 YABBA ROAD, TALLANGATTA EAST VIC 3700 | 5211158 | WOTS24 | 22kV AC | RURAL LONG | - insulators | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | 232160 | 20180129SPN_01 | Broken HV insulator.
1712 | Ausnet 17/89 | Ausnet | 28/01/2018 | 43128.8403 | -37.7747 | 145.2404 | 3 DELATITE COURT, WARRANWOOD VIC 3134 | 1218137 | RWN31 | Low voltage AC (<1kV) | RURAL SHORT | - connector / termination | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | VERY HIGH | 1 | 0.2 | 232162 | 20180129SPN_03 | Red phase conductor D burn through connection (loose connection) and lead from isolator at substation pole.
1713 | Ausnet 17/90 | Ausnet | 29/01/2018 | 43129.0958 | -36.0841 | 146.7338 | 998 PLUNKETTS ROAD, BARNAWARTHA NORTH VIC 3691 | 5208299 | BWA22 | 22kV AC | RURAL LONG | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | 232163 | 20180129SPN_04 | A bat caused a flashover between a steel crossarm and a HV conductor.
1714 | Ausnet 17/91 | Ausnet | 29/01/2018 | 43129.2326 | -38.5083 | 145.5925 | 430 KOETSVELDT ROAD, RYANSTON VIC 3992 | 2809269 | WGI22 | Low voltage AC (<1kV) | RURAL LONG | - connection box | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | VERY HIGH | 1 | 4.6 | 232174 | 20180130SPN_01 | Pole mounted FOLCB caught fire. High impedance fault.
1715 | Ausnet 17/92 | Ausnet | 30/01/2018 | 43130.0708 | -37.8173 | 147.7368 | 910 PRINCES HIGHWAY, NICHOLSON VIC 3882 | 1611151 | BDL6 | 22kV AC | RURAL SHORT | - fuse (boric acid) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | 232190 | 20180130SPN_03 | A burnt bird was found at base of pole which indicates a flashover at the pole.
1716 | Ausnet 17/93 | Ausnet | 31/01/2018 | 43131.641 | -36.1592 | 146.5159 | 88 BENNETTS ROAD, LILLIPUT VIC 3682 | 5105092 | WN3 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | 232237 | 20180308SPN_08 | Candled BA fuse.
1717 | Ausnet 17/94 | Ausnet | 31/01/2018 | 43131.8764 | -38.2242 | 146.0614 | 1 SAND PIT ROAD, YARRAGON VIC 3823 | 2203792 | MOE22 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | 232238 | 20180313SPN_04 | Candled EDO fuse tube.
1718 | Ausnet 17/95 | Ausnet | 2018-06-02 | 43137.75 | -36.3873 | 147.0414 | DUNDEE, 3162 KIEWA VALLEY HIGHWAY, KERGUNYAH VIC 3691 | 5200908 | WOTS11 | 22kV AC | RURAL LONG | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | 232306 | 20180207SPN_01 | Raised trailer of a fertiliser truck has allegedly contacted overhead HV conductors.
1719 | Ausnet 17/96 | Ausnet | 2018-07-02 | 43138.7667 | -37.6626 | 145.0152 | 18 KIAMA DRIVE, LALOR VIC 3075 | 911324 | EPG31 | Low voltage AC (<1kV) | URBAN | - connector / termination | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | 232325 | 20180208SPN_01 | LV ABC connector failed.
1720 | Ausnet 17/97 | Ausnet | 2018-07-02 | 43138.8271 | -37.6832 | 144.9873 | 58 SHERWOOD DRIVE, THOMASTOWN VIC 3074 | 907631 | TT6 | Low voltage AC (<1kV) | URBAN | - switch (disconnector/isolator) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | 232327 | 20180208SPN_03 | Failed / burnt out LV isolator on pole.
1721 | Ausnet 17/98 | Ausnet | 2018-10-02 | 43141.8326 | -37.8307 | 145.6762 | 85 BLACKSANDS ROAD, THREE BRIDGES VIC 3797 | 1411451 | WYK23 | 22kV AC | RURAL SHORT | - overhead conductor (bare; steel) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | VERY HIGH | 1 | 4.6 | 232381 | 20180212SPN_03 | Tall tree fell into overhead HV conductor.
1722 | Ausnet 17/99 | Ausnet | 2018-12-02 | 43143.9153 | -38.649 | 146.2195 | 5 JACKSONS ROAD, FOSTER VIC 3960 | 2024724 | FTR21 | 22kV AC | RURAL LONG | - transformer (pole mounted) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | 232394 | 20180213SPN_01 | A possum made contact with live HV on transformer which resulted in a small ground fire.
1723 | Ausnet 17/100 | Ausnet | 14/02/2018 | 43145.3056 | -37.6906 | 145.0101 | 19 HIGH STREET, THOMASTOWN VIC 3074 | 907481 | TT7 | 22kV AC | URBAN | - overhead conductor (bare; all aluminium conductor) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | VERY HIGH | 1 | 0.2 | 232493 | 20180222SPN_01 | Burnt HV lead on pole mounted Gas Switch.
1724 | Ausnet 17/101 | Ausnet | 14/02/2018 | 43145.4014 | -38.2212 | 145.5922 | 185 OBRIENS ROAD, BAYLES VIC 3981 | 513344 | LLG11 | 22kV AC | RURAL SHORT | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | VERY HIGH | 1 | 4.6 | 232492 | 20180307SPN_01 | Large tree branch fell into overhead HV conductor.
1725 | Ausnet 17/102 | Ausnet | 14/02/2018 | 43145.4187 | -38.3242 | 146.4603 | 36 DUSTING ROAD, HAZELWOOD SOUTH VIC 3840 | 2614828 | MWT24 | 22kV AC | RURAL SHORT | - overhead conductor (bare; steel) | single phase | Otherwise started by a distribution system | HBRA only | 1 | VERY HIGH | 1 | 1 | 232416 | 20180215SPN_01 | Cause is possibly due to corrosion
1726 | Ausnet 17/103 | Ausnet | 14/02/2018 | 43145.5403 | -38.2557 | 146.4898 | 582 FIRMINS LANE, HAZELWOOD NORTH VIC 3840 | 2577249 | TGN23 | 22kV AC | RURAL SHORT | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | VERY HIGH | 1 | 1 | 233532 | 20180511SPN_02 | private tree failed at root base (below ground) from extreme winds and brought down HV line. Investigation confirms • Tree outside clearance space – span is compliant re vegetation – trunk was approximately 7 metres west of the nearest overhead conductors • Species of tree – Radiata/Monterey Pine (Pinus radiata). • Height approximately 21 metres – Diameter at Breast Height (DBH) 700mm wide • No obvious structural hazards with tree • Tree failed at root base via root shearing below ground level from extreme winds. • Tree located on Private property.
1727 | Ausnet 17/104 | Ausnet | 14/02/2018 | 43145.8438 | -38.2413 | 145.8756 | 1729 LARDNERS TRACK, LARDNER VIC 3821 | 2705277 | WGL23 | 22kV AC | RURAL SHORT | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | VERY HIGH | 1 | 1 | 232421 | 20180215SPN_02 | Tree branch fell into overhead HV line.
1728 | Ausnet 17/105 | Ausnet | 18/02/2018 | 43149.6333 | -37.8607 | 148.0328 | 33 LAKE BUNGA BEACH ROAD, LAKE BUNGA VIC 3909 | 1902792 | NLA34 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | 232467 | 20180219SPN_01 | Suspect lightning strike caused LA to fail with subsequent mal-operation of an EDO fuse which candled, burnt in half with a section falling to ground.
1729 | Ausnet 17/106 | Ausnet | 19/02/2018 | 43150.7917 | -37.7257 | 145.4002 | 86 KILLARA ROAD, COLDSTREAM VIC 3770 | 1009667 | LDL23 | 22kV AC | RURAL LONG | - overhead conductor (bare; steel) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | VERY HIGH | 1 | 4.6 | 232489 | 20180221SPN_01 | Large tree branch into overhead HV line.
1730 | Ausnet 17/107 | Ausnet | 20/02/2018 | 43151.6937 | -38.6691 | 145.6159 | 18 SPEAR STREET, CAPE PATERSON VIC 3995 | 2810983 | WGI33 | Low voltage AC (<1kV) | RURAL SHORT | - overhead service conductor (residential) | two phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | VERY HIGH | 1 | 0.2 | 232491 | 20180221SPN_02 | Customer's tree branch rubbed through overhead service cable.
1731 | Ausnet 17/108 | Ausnet | 23/02/2018 | 43154.6972 | -37.8132 | 145.3241 | 95 CHERYLNNE CRESCENT, KILSYTH VIC 3137 | 1004182 | CYN21 | Low voltage AC (<1kV) | URBAN | - connector / termination | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | VERY HIGH | 1 | 0.2 | 232545 | 20180226SPN_03 | Loose LV bridge clamp.
1732 | Ausnet 17/109 | Ausnet | 23/02/2018 | 43154.9146 | -38.7038 | 145.8192 | 90 JUPITER BOULEVARD, VENUS BAY VIC 3956 | 2804943 | WGI14 | Low voltage AC (<1kV) | RURAL SHORT | - connection box | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | 232547 | 20180226SPN_02 | The root cause not determined but considered to be an overheated connection at FOLCB.
1733 | Ausnet 17/110 | Ausnet | 24/02/2018 | 43155.291 | -37.6417 | 144.9778 | 480 COOPER STREET, EPPING VIC 3076 | 928777 | EPG35 | 22kV AC | URBAN | - overhead conductor (bare; steel) | single phase | Otherwise started by a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | 232692 | 20180308SPN_04 | Investigation has shown that the HV line has not been constructed as per any of the plans stored in our system. The pole stay was not lowered as per the work instruction when the HV line was extended.
1734 | Ausnet 17/111 | Ausnet | 24/02/2018 | 43155.734 | -37.7441 | 148.4043 | BURRAGAH, 138 JOINERS ROAD, NEWMERELLA VIC 3886 | 1905975 | NLA34 | 22kV AC | RURAL SHORT | - dropper / bridge | three phase | Started by lightning striking a distribution system or a part of a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | 232554 | 20180226SPN_05 | 22kV insulator holding a bridge to Drop Out Fuse broke and the bridge became free and clashed with another phase of the 22kV network.
1735 | Ausnet 17/112 | Ausnet | 25/02/2018 | 43156.4688 | -37.2782 | 146.1315 | 42 OLD EILDON ROAD, JAMIESON VIC 3723 | 3919353 | MSD1 | 22kV AC | RURAL LONG | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | 232548 | 20180226SPN_08 | Tree into overhead HV conductors.
1736 | Ausnet 17/113 | Ausnet | 26/02/2018 | 43157.5674 | -36.6365 | 145.5195 | 59 MOGLONEMBY HALL ROAD, MOGLONEMBY VIC 3666 | 3901466 | BN1 | 12.7kV AC (SWER) | RURAL LONG | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any other thing forming part of or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | 232571 | 20180227SPN_01 | Tip truck driver caused the rear trailer to make contact with a SWER line.
1737 | Ausnet 17/114 | Ausnet | 28/02/2018 | 43159.5076 | -37.1014 | 145.9744 | 185 BANUMUM ROAD, MANSFIELD VIC 3722 | 3918933 | MSD2 | 22kV AC | RURAL LONG | - overhead conductor (bare; steel) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | VERY HIGH | 1 | 4.6 | 232621 | 20180307SPN_02 | Tree fell into overhead HV conductor.
1738 | Ausnet 17/115 | Ausnet | 28/02/2018 | 43159.5389 | -37.8513 | 145.2507 | 1 STRATTON COURT, BAYSWATER VIC 3153 | 1218733 | BRA11 | Low voltage AC (<1kV) | URBAN | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | VERY HIGH | 1 | 0.2 | 232626 | 20180306SPN_01 | Broken LV crossarm.
1739 | Ausnet 17/116 | Ausnet | 28/02/2018 | 43159.7056 | -38.2415 | 145.8859 | 54 MAXWELLS ROAD, LARDNER VIC 3821 | 2705329 | WGL23 | 22kV AC | RURAL SHORT | - overhead conductor (bare; steel) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | VERY HIGH | 1 | 1 | 232633 | 20180301SPN_04 | In strong wind conditions a tree branch broke and fell into overhead HV conductors.
1740 | Ausnet 17/117 | Ausnet | 28/02/2018 | 43159.7188 | -38.4333 | 145.7923 | 200 BENA ROAD, KORUMBURRA VIC 3950 | 2006456 | LGA12 | 22kV AC | RURAL SHORT | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | VERY HIGH | 1 | 1 | 232627 | 20180301SPN_01 | A tall tree fell into a HV line.
1741 | Ausnet 17/118 | Ausnet | 28/02/2018 | 43159.7458 | -38.1382 | 146.2948 | 200 PURVIS ROAD, TANJIL SOUTH VIC 3825 | 2210545 | MOE14 | 22kV AC | RURAL SHORT | - overhead conductor (bare; steel) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | VERY HIGH | 1 | 4.6 | 232631 | 20180301SPN_02 | Tree fell into HV conductor during windy conditions.
1742 | Ausnet 17/119 | Ausnet | 28/02/2018 | 43159.7708 | -38.0409 | 147.1013 | 288 HAGANS ROAD, AIRLY VIC 3851 | 2503668 | SLE32 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | VERY HIGH | 1 | 0.2 | 232630 | 20180328SPN_01 | Burnt EDO fuse tube.
1743 | Ausnet 17/120 | Ausnet | 28/02/2018 | 43159.8271 | -38.0759 | 146.8918 | 604 NAMBROK HALL ROAD, NAMBROK VIC 3847 | 2509549 | MFA22 | 22kV AC | RURAL LONG | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | VERY HIGH | 1 | 0.2 | 232632 | 20180301SPN_03 | In windy conditions a HV conductor was brought down by a fallen tree.
1744 | Ausnet 17/121 | Ausnet | 2018-02-03 | 43161.1229 | -38.2516 | 145.658 | 1060 WESTERNPORT ROAD, LANG LANG EAST VIC 3984 | 519170 | LLG11 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | 232664 | 20180412SPN_01 | Candled EDO fuse tube.
1745 | Ausnet 17/122 | Ausnet | 2018-02-03 | 43161.7174 | -37.9707 | 145.3872 | Duffys Road, Narre Warren East VIC 3804 | 523041 | BGE12 | Low voltage AC (<1kV) | RURAL SHORT | - switch (disconnector/isolator) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | 232690 | 20180411SPN_01 | Poor LV (high impedance) connection at LV fuse isolator.
1746 | Ausnet 17/123 | Ausnet | 2018-02-03 | 43161.8354 | -38.1583 | 146.2357 | L1 WALSHES ROAD, WESTBURY VIC 3825 | 2201653 | MOE22 | 22kV AC | RURAL LONG | - crossarm (steel) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | 232689 | 20180308SPN_03 | Appears a bird caused a flashover between a HV conductor to a LA and a steel crossarm/concrete pole causing the bird to catch fire and resulting in a ground fire.
1747 | Ausnet 17/124 | Ausnet | 2018-07-03 | 43166.4431 | -36.3166 | 146.368 | 25 MORRISON ROAD, BOWSER VIC 3678 | 5103947 | WN3 | 22kV AC | RURAL LONG | - pole (concrete) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | 232756 | 20180308SPN_05 | A magpie nest in a ACR pole resulted in flashover.
1748 | Ausnet 17/125 | Ausnet | 2018-07-03 | 43166.8438 | -37.0633 | 146.0844 | 7 GRIFFIN AVENUE, MANSFIELD VIC 3722 | 3917722 | MSD4 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | 232770 | 20180313SPN_02 | A magpie has caused a flashover between EDO fuses at pole substation.
1749 | Ausnet 17/126 | Ausnet | 2018-09-03 | 43168.9479 | -36.3004 | 147.231 | 1077 OMEO HIGHWAY, TALLANGATTA SOUTH VIC 3701 | 5211317 | WOTS24 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | 232791 | 20180416SPN_03 | Arcing and burnt EDO fuse tube.
1750 | Ausnet 17/127 | Ausnet | 2018-10-03 | 43169.3986 | -38.5069 | 146.1176 | 1315 MEENIYAN-MIRBOO NORTH ROAD, DUMBALK VIC 3956 | 2002195 | LGA13 | Low voltage AC (<1kV) | RURAL LONG | - overhead conductor (insulated) | single phase | Otherwise started by a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | 232793 | 20180313SPN_03 | Damaged LV transformer leads cable.
1751 | Ausnet 17/128 | Ausnet | 15/03/2018 | 43174.0653 | -36.2408 | 147.0958 | 1522 MURRAY VALLEY HIGHWAY, HUON VIC 3695 | 5214098 | WOTS13 | 22kV AC | RURAL LONG | - transformer (pole mounted) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | 232843 | 20180315SPN_01 | A bat was between EDO fuse unit and earth system on a substation pole.
1752 | Ausnet 17/129 | Ausnet | 16/03/2018 | 43175.4604 | -37.9535 | 145.5043 | 1 LISHEEN ROAD, COCKATOO VIC 3781 | 408391 | OFR23 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | 232869 | 20180416SPN_04 | Candled BA fuse tube.
1753 | Ausnet 17/130 | Ausnet | 17/03/2018 | 43176.5694 | -38.4618 | 145.6439 | 1415 LOCH-WONTHAGGI ROAD, GLEN ALVIE VIC 3979 | 2008155 | LGA23 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | HBRA only | 1 | SEVERE | 2 | 2 | 232874 | 20180417SPN_01 | Faulty substation transformer resulted in EDO fuse operation with one EDO fuse hung-up and candled.
1754 | Ausnet 17/131 | Ausnet | 17/03/2018 | 43176.6667 | -38.6249 | 146.6351 | FEN FARM, 7890 SOUTH GIPPSLAND HIGHWAY, ALBERTON VIC 3971 | 2608311 | FTR23 | 12.7kV AC (SWER) | RURAL LONG | - overhead conductor (bare; aluminium core steel reinforced) | single wire earth return (SWER) | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | VERY HIGH | 1 | 1 | 232875 | 20180319SPN_02 | Bird caused a flashover at pole, fell to ground and started a small grass fire.
1755 | Ausnet 17/132 | Ausnet | 17/03/2018 | 43176.7771 | -37.6565 | 145.5171 | 15 VIEW STREET, HEALESVILLE VIC 3777 | 1403271 | WYK24 | Low voltage AC (<1kV) | RURAL SHORT | - connector / termination | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | SEVERE | 2 | 0.4 | 232876 | 20180319SPN_01 | Burnt off LV bushing on transformer - faulty connection.
1756 | Ausnet 17/133 | Ausnet | 18/03/2018 | 43177.4375 | -37.8391 | 146.6931 | LICOLA ROAD, GLENMAGGIE VIC 3858 | 2510936 | MFA22 | 22kV AC | RURAL LONG | - pole (wood) | single phase | Otherwise started by a distribution system | HBRA only | 1 | VERY HIGH | 1 | 1 | 232878 | 20180319SPN_03 | Lightning strike on HV wood pole.
1757 | Ausnet 17/134 | Ausnet | 18/03/2018 | 43177.459 | -37.3794 | 145.4362 | 437 LARRITTS LANE, GLENBURN VIC 3717 | 1401222 | KLK1 | 12.7kV AC (SWER) | RURAL SHORT | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within electric line construction area | 19.8 | VERY HIGH | 1 | 19.8 | 232883 | 20180319SPN_06 | Tree branch fell into overhead SWER line.
1758 | Ausnet 17/135 | Ausnet | 18/03/2018 | 43177.4993 | -38.0722 | 145.4759 | 1 MAIN STREET, PAKENHAM VIC 3810 | 500606 | PHM32 | Low voltage AC (<1kV) | URBAN | - crossarm (wood) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | SEVERE | 2 | 0.4 | 232880 | 20180417SPN_02 | Burnt LV cross arm due to voltage / current tracking from polluted LV insulator
1759 | Ausnet 17/136 | Ausnet | 18/03/2018 | 43177.5326 | -36.281 | 145.819 | ALMARU, 2365 BENALLA-TOCUMWAL ROAD, YUNDOOL VIC 3727 | 3911226 | BN2 | 22kV AC | RURAL LONG | - overhead conductor (bare; copper) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | VERY HIGH | 1 | 4.6 | 232877 | 20180319SPN_05 | During gusty wind conditions a large tree limb fell into overhead HV conductors.
1760 | Ausnet 17/137 | Ausnet | 18/03/2018 | 43177.7361 | -38.2196 | 145.9779 | 906 BONA VISTA ROAD, GAINSBOROUGH VIC 3822 | 2705515 | WGL23 | 22kV AC | RURAL SHORT | - overhead conductor (bare; steel) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | VERY HIGH | 1 | 1 | 232881 | 20180319SPN_04 | Tree into overhead HV line.
1761 | Ausnet 17/138 | Ausnet | 19/03/2018 | 43178.5076 | -38.6091 | 146.4857 | 327 Hedley Range Rd BINGINWARRA VIC 3966 | 2611459 | FTR12 | 12.7kV AC (SWER) | RURAL LONG | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | 232913 | 20180320SPN_01 | Tree fell into SWER conductor.
1762 | Ausnet 17/139 | Ausnet | 19/03/2018 | 43178.5146 | -38.2099 | 146.3251 | Hernes Oak Vic 3825 | 7700545 | MWTS-YPS1 | 66kV AC | UNCLASSIFIED | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | 232898 | 20180319SPN_08 | HV conductor on ground.
1763 | Ausnet 17/140 | Ausnet | 21/03/2018 | 43180.5292 | -38.1928 | 145.3458 | 2470 SOUTH GIPPSLAND HIGHWAY, DEVON MEADOWS VIC 3977 | 517096 | CRE33 | 22kV AC | RURAL SHORT | - overhead conductor (bare; steel) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | VERY HIGH | 1 | 1 | 232936 | 20180326SPN_01 | A large tree branch fell into overhead HV conductor.
1764 | Ausnet 17/141 | Ausnet | 21/03/2018 | 43180.6646 | -38.5185 | 145.7218 | 105 KORUMBURRA-INVERLOCH ROAD, KONGWAK VIC 3951 | 2804133 | WGI22 | 22kV AC | RURAL LONG | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | 232941 | 20180322SPN_02 | Tree fell into overhead HV conductors.
1765 | Ausnet 17/142 | Ausnet | 21/03/2018 | 43180.7271 | -38.5921 | 145.7976 | 6870 BASS HIGHWAY, POUND CREEK VIC 3996 | 5725063 | LGA23 | 22kV AC | RURAL LONG | - dropper / bridge | three phase | Otherwise started by a distribution system | HBRA only | 1 | VERY HIGH | 1 | 1 | 232938 | 20180326SPN_02 | Flexible HV T-off dropper at 5725063 was blowing in strong wind and contacting base of insulator on steel x-arm & concrete pole causing arcing and burnt spiral dampers on conductors.
1766 | Ausnet 17/143 | Ausnet | 21/03/2018 | 43180.7333 | -38.3799 | 146.5319 | 2225 TRARALGON CREEK ROAD, KOORNALLA VIC 3844 | 2605374 | TGN23 | 22kV AC | RURAL SHORT | - overhead conductor (bare; all aluminium conductor) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | HIGH | 0.5 | 0.5 | 232942 | 20180322SPN_03 | During extreme winds a large tree fell into the single phase overhead HV conductors.
1767 | Ausnet 17/144 | Ausnet | 21/03/2018 | 43180.8396 | -37.9001 | 145.3142 | 28 ALBERT STREET, UPPER FERNTREE GULLY VIC 3156 | 1032892 | FGY33 | Low voltage AC (<1kV) | URBAN | - overhead service conductor (other) | single phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | VERY HIGH | 1 | 4.6 | 232937 | 20180322SPN_01 | Service cable damaged by cockatoos chewing insulation causing a short circuit.
1768 | Ausnet 17/145 | Ausnet | 22/03/2018 | 43181.5181 | -38.0206 | 146.9624 | 696 RIVERSDALE ROAD, RIVERSLEA VIC 3860 | 2511542 | MFA34 | Low voltage AC (<1kV) | RURAL SHORT | - overhead conductor (bare; all aluminium conductor) | two phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | HIGH | 0.5 | 0.1 | 232960 | 20180322SPN_04 | Tractor contacted overhead LV line / pole stay.
1769 | Ausnet 17/146 | Ausnet | 24/03/2018 | 43183.4583 | -38.4142 | 147.1092 | 295 COSTELLOS ROAD, GIFFARD VIC 3851 | 2504316 | SLE31 | 12.7kV AC (SWER) | RURAL LONG | - fuse (boric acid) | single wire earth return (SWER) | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | 232998 | 20180507SPN_04 | Burnt Boric Acid HV fuse tube.
1770 | Ausnet 17/147 | Ausnet | 24/03/2018 | 43183.75 | -37.9154 | 145.2995 | 351 LYSTERFIELD ROAD, LYSTERFIELD VIC 3156 | 1302523 | FGY21 | Low voltage AC (<1kV) | URBAN | - overhead conductor (insulated) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | 233000 | 20180326SPN_04 | A 4 core LV service mains to a FOLCB on pole for a customer's UG service was worn through and faulted phase to phase.
1771 | Ausnet 17/148 | Ausnet | 24/03/2018 | 43183.7972 | -36.4871 | 146.1431 | 677 Glenrowan Rd, Wangaratta South VIC 3678 | 3909511 | WN6 | 66kV AC | UNCLASSIFIED | - pole (wood) | three phase | Started by lightning striking a distribution system or a part of a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | 233001 | 20180507SPN_03 | Lightning strike to pole.
1772 | Ausnet 17/149 | Ausnet | 27/03/2018 | 43186.5 | -37.7467 | 147.6773 | 80 WATERHOLES ROAD, GRANITE ROCK VIC 3875 | 1600885 | BDL8 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | 233044 | 20180508SPN_02 | Burnt Boric Acid fuse tube.
1773 | Ausnet 17/150 | Ausnet | 28/03/2018 | 43187.3639 | -38.2516 | 145.658 | 1060 WESTERNPORT ROAD, LANG LANG EAST VIC 3984 | 519170 | LLG11 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | 233053 | 20180508SPN_03 | Burnt EDO fuse tube.
1774 | Ausnet 17/151 | Ausnet | 2018-04-04 | 43194.8424 | -37.9266 | 145.5086 | 32 MOUNTAIN ROAD, COCKATOO VIC 3781 | 420555 | BGE22 | Low voltage AC (<1kV) | RURAL SHORT | - connection box | two phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | 233125 | 20180515SPN_02 | Pole FMB burnt out. Fire on pole.
1775 | Ausnet 17/152 | Ausnet | 2018-05-04 | 43195.4132 | -36.8235 | 145.1111 | MULLERS ROAD, TABILK VIC 3607 | 4705544 | SMR8 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | 233134 | 20180510SPN_01 | EDO fuse candling
1776 | Ausnet 17/153 | Ausnet | 2018-06-04 | 43196.2729 | -37.6894 | 145.42 | 717 MAROONDAH HIGHWAY, COLDSTREAM VIC 3770 | 1409569 | LDL23 | Low voltage AC (<1kV) | RURAL LONG | - connection box | two phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | 233147 | 20180406SPN_02 | LV fuse box.
1777 | Ausnet 17/154 | Ausnet | 2018-09-04 | 43199.0188 | -37.7372 | 145.1277 | 38 ROSEHILL ROAD, LOWER PLENTY VIC 3093 | 905963 | ELM34 | Low voltage AC (<1kV) | RURAL SHORT | - lamps (major road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | 233155 | 20180529SPN_01 | Street light head caught fire. Exact cause uncertain but it is common for such older street lights to fail due to either faulty ignitors with repetitive striking or failed plastic clad capacitors.
1778 | Ausnet 17/155 | Ausnet | 14/04/2018 | 43204.7083 | -37.7541 | 148.3242 | MEKKENVILLE, 4301 PRINCES HIGHWAY, WAYGARA VIC 3888 | 1905903 | NLA34 | 22kV AC | RURAL SHORT | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | VERY HIGH | 1 | 1 | 233218 | 20180416SPN_01 | Tree branch into conductors.
1779 | Ausnet 17/156 | Ausnet | 17/04/2018 | 43207.5389 | -37.6492 | 145.0253 | 763 HIGH STREET, EPPING VIC 3076 | 915175 | EPG32 | Low voltage AC (<1kV) | RURAL SHORT | - connection box | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | LOW-MODERATE | 0.2 | 0.04 | 233230 | 20180517SPN_01 | Burnt out LV Fuse Switch Disconnector on the load side.
1780 | Ausnet 17/157 | Ausnet | 20/04/2018 | 43210.5472 | -38.0652 | 146.6238 | 1 SEMMENS STREET, TOONGABBIE VIC 3856 | 2602911 | TGN31 | Low voltage AC (<1kV) | RURAL LONG | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | HBRA only | 1 | LOW-MODERATE | 0.2 | 0.2 | 233305 | 20180420SPN_01 | Contact with overhead LVconductor by an excavator.
1781 | Ausnet 17/158 | Ausnet | 24/04/2018 | 43214.4604 | -37.8917 | 147.6762 | 4 FORGE CREEK ROAD, EAGLE POINT VIC 3878 | 1610710 | BDL42 | 22kV AC | RURAL SHORT | - fuse (boric acid) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | HIGH | 0.5 | 2.3 | 233328 | 20180426SPN_01 | It appears a magpie shorted out on a BA fuse unit and earth.
1782 | Ausnet 17/159 | Ausnet | 27/04/2018 | 43217.7417 | -37.6717 | 145.5071 | 20 ARGOON ROAD, HEALESVILLE VIC 3777 | 1402987 | LDL23 | 22kV AC | RURAL LONG | - overhead conductor (bare; all aluminium conductor) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | 233378 | 20180430SPN_01 | The incident is currently under investigation.
1783 | Ausnet 17/160 | Ausnet | 30/04/2018 | 43220.4167 | -36.3254 | 146.2969 | 68 WALDARA DRIVE, WALDARA VIC 3678 | 5106454 | WN2 | Low voltage AC (<1kV) | RURAL LONG | - connection box | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | LOW-MODERATE | 0.2 | 0.92 | 233388 | 20180528SPN_03 | Melted and burnt out three phase LV connection box.
1784 | Ausnet 17/161 | Ausnet | 2018-01-05 | 43221.4667 | -37.3249 | 147.7775 | 5870 GREAT ALPINE ROAD, ENSAY VIC 3895 | 1602484 | BDL8 | Low voltage AC (<1kV) | RURAL LONG | - overhead service conductor (residential) | single phase | Started by any other thing forming part of or coming into contact with a distribution system | within electric line construction area | 19.8 | NO FORECAST | 0.1 | 1.98 | 233408 | 20180502SPN_01 | A truck contacted a POEL.
1785 | Ausnet 17/162 | Ausnet | 2018-01-05 | 43221.5965 | -37.8681 | 148.021 | 36 OCEAN VIEW PARADE, LAKES ENTRANCE VIC 3909 | 5622581 | BDL41 | 22kV AC | RURAL LONG | - dropper / bridge | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | 233413 | 20180502SPN_02 | HV dropper lead termination burnt off transformer bushing.
1786 | Ausnet 17/163 | Ausnet | 2018-10-05 | 43230.4194 | -38.0282 | 145.8019 | 100 ALCORN ROAD, LABERTOUCHE VIC 3816 | 2716712 | WGL21 | 22kV AC | RURAL LONG | - fuse (boric acid) | three phase | Otherwise started by a distribution system | HBRA only | 1 | NO FORECAST | 0.1 | 0.1 | 233507 | 20180605SPN_02 | Candled Boric Acid fuse tube.
1787 | Ausnet 17/164 | Ausnet | 14/05/2018 | 43234.3229 | -38.502 | 145.9555 | 50 CARMODYS ROAD, LEONGATHA SOUTH VIC 3953 | 2001147 | LGA14 | 22kV AC | RURAL LONG | - overhead conductor (bare; steel) | single phase | Otherwise started by a distribution system | HBRA only | 1 | NO FORECAST | 0.1 | 0.1 | 233540 | 20180515SPN_05 | Corroded steel conductor broke at existing sleeve on conductor which fell to ground & burnt small area of grass on nature strip
1788 | Ausnet 17/165 | Ausnet | 19/05/2018 | 43239.991 | -37.8729 | 145.4064 | 538 MONBULK ROAD, MONBULK VIC 3793 | 1321115 | LDL13 | Low voltage AC (<1kV) | RURAL SHORT | - lamps (major road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | 233644 | 20180628SPN_01 | Failed light identified as an older style unit where the igniter/starter has failed resulting in fire.
1789 | Ausnet 17/166 | Ausnet | 2018-04-06 | 43255.2215 | -37.6898 | 145.0052 | 13 CHAFFEY STREET, THOMASTOWN VIC 3074 | 907501 | TT7 | 22kV AC | URBAN | - fuse (powder filled) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | 233830 | 20180626SPN_03 | Bird made contact with Overhead 22kV resulting in fuse operation
1790 | Ausnet 17/167 | Ausnet | 19/06/2018 | 43270.7903 | -38.224 | 145.3135 | 23 KALLARA ROAD, WARNEET VIC 3980 | 517474 | CRE33 | Low voltage AC (<1kV) | RURAL SHORT | - connection box | three phase | Otherwise started by a distribution system | HBRA only | 1 | NO FORECAST | 0.1 | 0.1 | 234031 | 20180620SPN_01 | Krone box failure resulting from overload
1791 | Ausnet 17/168 | Ausnet | 26/06/2018 | 43277.5417 | -37.7574 | 145.3522 | 250 MAIN STREET, LILYDALE VIC 3140 | 1006146 | LDL12 | Low voltage AC (<1kV) | URBAN | - overhead conductor (ABC) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | NO FORECAST | 0.1 | 0.02 | 234128 | 20180628SPN_02 | Fault crew attended to find faulty/failed IPC connection on LV ABC mains
1792 | United 16/17 | United | 2016-07-09 | 0.68317 | -37.9476 | 145.1562 |  | 635790 | SV 32 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 4962 | 20160711UTD_01 | Birds nest on dressing down arm , made with bits of wire . LIS#0635790. Small fire started at base of pole in rubbish. It was extinguished prior to our arrival.
1793 | United 16/18 | United | 2016-07-11 | 0.70301 | -37.9528 | 145.012 |  | 1822914 | SR 11 | Low voltage AC (<1kV) | Urban | - connector / termination | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 4992 | 20160819UTD_01 | repaired active service connection to thew street light
1794 | United 16/19 | United | 2016-07-13 | 0.77137 | -37.8989 | 145.2233 |  | 8808747 | MGE21 | 22kV AC | Urban | - surge diverter | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 4993 | 20160819UTD_02 | Lis 8808747, LA on B phase found blowen clear. All three cut clear. Notification ##1000537547
1795 | United 16/20 | United | 2016-07-22 | 0.69792 | -38.3094 | 145.1457 |  | 1110545 | HGS22 | Low voltage AC (<1kV) | Rural Short | - underground service cable (residential) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 4981 | 20160725UTD_02 | It was reported that tight bandit tape compressed LV ABC and the shorted - Linesman witness flame on cable
1796 | United 16/21 | United | 2016-07-26 | 0.75311 | -37.8008 | 145.1923 |  | 7067507 | NW 22 | Low voltage AC (<1kV) | Urban | - lamps (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 4986 | 20160727UTD_03 | Replaced 150 hp sodium head that had caught fire1 pole south of the bridge over eastlink on the east side
1797 | United 16/22 | United | 2016-07-27 | 0.33251 | -38.0175 | 145.215 |  | 9360948 | DSH31 | 22kV AC | Urban | - fuse (boric acid) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 4988 | 20160728UTD_02 | UE B/A fuse was on fire/out by the time crew arrived, no other damage sustained, fuse fire only. LIS 9360948, Fire Report Ref 01870
1798 | United 16/23 | United | 2016-08-11 | 0.60087 | -37.9777 | 145.017 |  | 1811878 | BR 04 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 4996 | 20160819UTD_04 | Replaced burnt out 3ph fmb at lis1811878 fire report 04002 completed as jb had caught fire but had been put out by mfb before crew arrived
1799 | United 16/24 | United | 2016-08-25 | 0.54444 | -37.8505 | 145.1467 |  | 7040186 | EB 14 | Low voltage AC (<1kV) | Urban | - connection box | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5007 | 20160830UTD_01 | A faulty UE contactor has started a fire on cust meterboard, crew has isolated supply for safety at pole lis # 7040186, issue defect to cust REC require.
1800 | United 16/25 | United | 2016-08-25 | 0.93388 | -38.1456 | 145.1207 |  | 8819378 | FSH31 | Low voltage AC (<1kV) | Urban | - lamps (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5005 | 20160826UTD_02 | SL burnt out/caught on fire, cover missing, caused by moisture and salt/corrosion. Loca SL head/350watt lantern LIS 8819378.
1801 | United 16/26 | United | 2016-09-04 | 0.97014 | -38.1706 | 145.2038 |  | 3301085 | FSH21 | Low voltage AC (<1kV) | Rural Short | - connection box | two phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 5013 | 20160907UTD_01 | At 330 centre rd reports of a fire on pole o/s property, Crew attended and @ Lis 3301085 replaced 3w JB & 3w fmb for UG on serv pole. Possible loose connection
1802 | United 16/27 | United | 2016-09-13 | 0.16528 | -37.7671 | 145.0866 |  | 7056808 | WD 36 | 22kV AC | Urban | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5021 | 20160914UTD_01 | EDO Fuse Candled Lis # 7056808 - Tx at WESTMINSTER-SUMMIT
1803 | United 16/28 | United | 2016-09-21 | 0.22674 | -38.3649 | 145.2038 |  | 8826905 | HGS31 | Low voltage AC (<1kV) | Rural Short | - lamps (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5030 | 20161006UTD_01 | CFA advised pole lis # 8826905 correct address is 216 Stony point rd - isolated and replaced 150w sodium street light
1804 | United 16/29 | United | 2016-09-22 | 0.81405 | -37.7973 | 145.1827 |  | 9279455 | NW 13 | Low voltage AC (<1kV) | Urban | - lamps (minor road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5031 | 20161006UTD_02 | Crew pulled fuse at base of street light. head to be replaced. (special Head) its o/s number 12 Woodhal Wynd. LIS # 9279455.
1805 | United 16/30 | United | 2016-09-25 | 0.82873 | -38.3738 | 145.1212 |  | 1108209 | MTN32 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5028 | 20160927UTD_01 | At Ftn-Flinders Rd Balnarring , replaced 3ph FMB and j/box, rehashed 3 ph U/G to #3080, fire report # 6582, lis # 1108209
1806 | United 16/31 | United | 2016-10-01 | 0.97223 | -38.1464 | 145.1292 |  | 8819096 | LWN35 | Low voltage AC (<1kV) | Urban | - switch (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5033 | 20161007UTD_02 | Krone switch burntout. replaced. LIS# 8819096
1807 | United 16/32 | United | 2016-10-02 | 0.50426 | -37.9486 | 145.0422 |  | 1819291 | CM 25 | Low voltage AC (<1kV) | Urban | - connection box | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5052 | 20161026UTD_02 | Poles appear to have fire damage, removed hanging j/box at lis # 1819291.
1808 | United 16/33 | United | 2016-10-02 | 0.65439 | -37.8507 | 145.0435 |  | 2311940 | K 03 | Low voltage AC (<1kV) | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5032 | 20161007UTD_01 | LV assets were clashing due to high winds, LV spreader fitted to prevent clashing, no follow up required, LIS 2311940
1809 | United 16/34 | United | 2016-10-10 | 0.15859 | -38.1346 | 145.2284 |  | 9657245 | LWN21 | 22kV AC | Rural Short | - capacity balancing units | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 5068 | 20161108UTD_01 | CAP DNG-HASTINGS CRANBOURNE failed and caught fire. Fire brigade called to extinguish pole. Lis # 9657245
1810 | United 16/35 | United | 2016-10-11 | 0.68766 | -37.9095 | 145.2345 |  | 8808792 | FGY31 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5040 | 20161014UTD_01 | Replace 3ph FMB which had caught fire on Lis # 8808792.
1811 | United 16/36 | United | 2016-10-15 | 0.59472 | -38.216 | 145.124 |  | 1122093 | MTN22 | 22kV AC | Rural Short | - overhead conductor (ABC) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 5046 | 20161019UTD_01 | HV ABC cable down from Switch pole LIS #1122093, eramosa rd west/moorooduc - Evidence of grass fire 2m x 6m area opp on road reserve - fire out on arrival
1812 | United 16/37 | United | 2016-10-22 | 0.73972 | -37.9217 | 145.0054 |  | 1804512 | NB 12 | 11kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5078 | 20161116UTD_01 | Crew isolated the O/Head so as to remove tree branch from the Conductor at pole Lis#1804512. Branch came from private tree at # 733 Hampton St.
1813 | United 16/38 | United | 2016-10-22 | 0.91097 | -37.9545 | 145.023 |  | 1822972 | SR 12 | 11kV AC | Urban | - insulators | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5059 | 20161031UTD_03 | Crew found sub pole Lis#1822972, damaged by pole fire. Centre Phase Disc eye bolt and Xarm King bolt burned out and pole requiring replacement.
1814 | United 16/39 | United | 2016-10-28 | 0.25253 | -38.0501 | 145.2168 |  | 9953514 | DVY34 | Low voltage AC (<1kV) | Urban | - lamps (major road) | single phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 5061 | 20161031UTD_05 | As per mfb 150 HPS Lantern has caught fire, LIS #9953514
1815 | United 16/40 | United | 2016-11-03 | 0.41875 | -38.3628 | 145.0744 |  | 1107312 | MTN32 | 22kV AC | Rural Short | - overhead conductor (ABC) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 5067 | 20161104UTD_02 | Linesman witnessed flame on LIS# 1107312 . The fire started on restoration of supply from a planned shutdown on the connection to the HV droppers which the linesman suspects were disturbed during the works.
1816 | United 16/41 | United | 2016-11-04 | 0.69301 | -37.7969 | 145.1698 |  | 7066298 | NW 23 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5070 | 20161108UTD_02 | Blue phase tee off conductor contacted the red phase through line because of sloose hardware.Burnt grass 5cm x1.5 mtrs long on naturestrip o/s cnr Clems Rd & Tunstall Rd Donvale. LIS# 7066298
1817 | United 16/42 | United | 2016-11-06 | 0.12377 | -37.9347 | 145.0496 |  | 1824862 | HTS-MR HTS - SR | 66kV AC | Urban | - insulators | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5072 | 20161109UTD_03 | Address is actually 589 South Rd, LIS 1824862 66KV Pole to be replaced burnt thru.
1818 | United 16/43 | United | 2016-11-06 | 0.25141 | -38.1332 | 145.1277 |  | 3308414 | FTN21 | 22kV AC | Urban | - insulators | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5073 | 20161111UTD_01 | Broken cross arm at NEW TOOYAL S/S. LIS 3308414. Crew confirmed xarm fire caused by tracking at xarm strap. replaced xarm, fuse units and HV droppers. fire report 00083
1819 | United 16/44 | United | 2016-11-07 | 0.31153 | -38.2407 | 145.0298 |  | 1102056 | MTN31 | 22kV AC | Urban | - insulators | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5075 | 20161114UTD_02 | HV termination x-arm burnt through at x-arm strap bolt at FOOTWAY ESPLANADE S/S. LIS 1102056. Arm replaced under access permit.
1820 | United 16/45 | United | 2016-11-07 | 0.93789 | -37.8954 | 145.0583 |  | 2321820 | OR 25 | Low voltage AC (<1kV) | Urban | - connection box | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5079 | 20161116UTD_02 | Fuse base for unit 1 had melted/on fire when crews arrived - fire report created by crew - replaced 2 x 100a fuse bases at meterpanle for unit 1 and 2 - tested ande cofiremd supply restored to both units. LIS 2321820
1821 | United 16/46 | United | 2016-11-17 | 0.24644 | -37.9709 | 145.1755 |  | 618397 | NP 25 | 22kV AC | Urban | - capacity balancing units | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5083 | 20161121UTD_01 | Cap bank blown up on pole - no fire damage to pole - centre phase HV dropper burnt off at the Vac Switch. LIS 0618397
1822 | United 16/47 | United | 2016-11-22 | 0.46184 | -38.1296 | 145.1299 |  | 3308361 | FTN21 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5085 | 20161124UTD_01 | Replaced 3 ph FMB on lis # 3308361, cause overloaded, Fire Report # 01871, feeding FTN 4x4 and Light Commercial, tested and left on.
1823 | United 16/48 | United | 2016-11-22 | 0.51444 | -38.3721 | 144.8873 |  | 1311762 | RBD11 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5086 | 20161201UTD_01 | Tree in nature strip on HV O/H in Allambi Crescent outside #8 adjacent to LIS# 1311762. No damage to assets. Tree was cut back by crew and supply restored from SCADA.
1824 | United 16/49 | United | 2016-12-02 | 0.48542 | -38.1034 | 145.128 |  | 3305954 | CRM33 | Low voltage AC (<1kV) | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5098 | 20161214UTD_02 | LIS - 3305954 LV bundles terminat at pole, services IPC have caught fire, no fire at ground level.
1825 | United 16/50 | United | 2016-12-03 | 0.37847 | -38.2225 | 145.2449 |  | 9866573 | HGS33 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 5100 | 20161221UTD_01 | Conductor down - still sparking when crews arrived, burn marks on ground, no other grass ignition- Conductor on deck in the bay west of spur fuses (Lis 9866573) has burnt through splice.
1826 | United 16/51 | United | 2016-12-08 | 0.68894 | -38.0242 | 145.1002 |  | 3302312 | MC 01 | 22kV AC | Urban | - insulator tie wires / connections | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5107 | 20161220UTD_01 | Suspect: car hit pole at a prior date . HV ties broken , Conductor touching pole cap, Fire at LV king bolt. LIS#3302312, Pole replaced.
1827 | United 16/52 | United | 2016-12-09 | 0.37222 | -37.9581 | 145.1445 |  | 613176 | SS 13 | 22kV AC | Urban | - insulators | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5108 | 20161220UTD_02 | Pole fire on LIS # 0613176. HV LV tee off . Burnt at the arm strap for the HV tee xarm and burnt the LV inter.
1828 | United 16/53 | United | 2016-12-12 | 0.47102 | -37.8635 | 145.0806 |  | 2300413 | EM 05 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5142 | 20170117UTD_04 | 3 phase fmb on pole LIS 2300413 - likely loose connection
1829 | United 16/54 | United | 2016-12-18 | 0.56214 | -37.9874 | 145.0704 |  | 1809060 | M 35 | 11kV AC | Urban | - connector / termination | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5113 | 20161222UTD_02 | Customer reports of balloons into O/H line and this likely cause a conductor to fail due to wrappon burning and ampact connector failing at pole LIS 1809060. Conductor down at pole LIS1809059 (hv conductor started small grass fire)
1830 | United 16/55 | United | 2016-12-20 | 0.36274 | -37.9168 | 144.9893 |  | 1805954 | MR 32 | 11kV AC | Urban | - insulators | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5117 | 20161228UTD_02 | HV x-arm burnt through and HV conductor resting on LV x-arm. LIS 18059954, HV xarm replaced due to fire damage appears to have been caused by tracking.
1831 | United 16/56 | United | 2016-12-20 | 0.40139 | -37.9879 | 145.1991 |  | 634920 | KBH31 | 22kV AC | Urban | - insulators | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5118 | 20161228UTD_03 | Downer spotter confirmed pole fire at LIS#0634920 BENNET N40 VEREY S/S. Crew replaced pole and x-arms in area
1832 | United 16/57 | United | 2016-12-24 | 0.13786 | -37.8864 | 145.1418 |  | 602729 | GW 03 | 22kV AC | Urban | - dropper / bridge | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5122 | 20161229UTD_01 | Possum CAUSED FLASHOVER AT Pole tee to Coolarn Waverley S/S, Fire brigade attended, pole badly damaged, section had to be interrupted- pole lis # 0602729 pole HV & LV T-off /inter requires to be replaced 2
1833 | United 16/58 | United | 2016-12-24 | 0.50488 | -38.4007 | 144.9949 |  | 1313961 | DMA23 | Low voltage AC (<1kV) | Rural Short | - connector / termination | single phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 5120 | 20161228UTD_04 | lis: 1313961 - replaced blue phs ipc clamp for u/g supply - all ok now. - small grass fire - approx 1 sq meter at base of pole
1834 | United 16/59 | United | 2016-12-28 | 0.54139 | -37.9666 | 145.0808 |  | 1813390 | HT 01 | 22kV AC | Urban | - insulators | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 5136 | 20170113UTD_01 | LIS - 1813390 HV termination x-arm to be replaced. PM#1000574381 repairs carried out
1835 | United 16/60 | United | 2017-01-04 | 0.925 | -37.8873 | 145.0004 |  | 2308669 | EW 03 | 11kV AC | Urban | - dropper / bridge | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5161 | 20170206UTD_01 | Possum at CHP to Nepean-McMillan s/s possum damaged cable head, blew R Ph bridge at HV Tee off in Nepean Hwy cnr of Glendora Ave, Very small patch of grass (approx 3cm sq) had burn mark due to fallout from fuse bridge blowing.
1836 | United 16/61 | United | 2017-01-05 | 0.53497 | -38.3763 | 144.7886 |  | 8831884 | STO14 | Low voltage AC (<1kV) | Urban | - connection box | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5131 | 20170109UTD_05 | 501 AMI mtr caught fire at load tails, replaced mtr fire ign rep - LIS - 8831884
1837 | United 16/62 | United | 2017-01-18 | 0.28179 | -37.7981 | 145.1604 |  | 7066961 | NW 23 | 22kV AC | Urban | - insulators | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5144 | 20170119UTD_02 | End of Strain Xarm burnt off in Blackburn Rd Cnr Glenview..LIS#7066961. Grey porcelain disc insulators & Brown fog bridging insulators.
1838 | United 16/63 | United | 2017-01-19 | 0.54306 | -37.942 | 145.1219 |  | 611069 | SS 21 | Low voltage AC (<1kV) | Urban | - switch (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5145 | 20170124UTD_01 | Repalced burnt out krone box, new 160amp din fuses. cause unknown, krone box was melted. LIS3 0611069
1839 | United 16/64 | United | 2017-01-20 | 0.31061 | -37.9477 | 145.0743 |  | 1816379 | HT 13 | 22kV AC | Urban | - connector / termination | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5162 | 20170206UTD_02 | A Possum caused a Hv fuse to blow bl ph at cap bank blown off lead. LIS 1816379
1840 | United 16/65 | United | 2017-01-23 | 0.43678 | -38.1471 | 145.1443 |  | 3319689 | LWN24 | Low voltage AC (<1kV) | Urban | - connector / termination | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5148 | 20170124UTD_02 | MFB reported fire on pole top LIS 3319689, located in Ashelgh Ave, just north of Beach St burnt ipc on the blue phase to 95mil o/h service. -
1841 | United 16/66 | United | 2017-01-23 | 0.79839 | -38.0439 | 145.1339 |  | 3306941 | CRM35 | Low voltage AC (<1kV) | Urban | - connector / termination | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5150 | 20170202UTD_01 | Pole lis# 3306941 - looks like fire at base of pole - due to possible melted conn on the lv xarm - ampac to be redone - Small fire area about size of bin lid approx 2 sq meters - grass singed no fire when crew arrived
1842 | United 16/67 | United | 2017-01-24 | 0.36674 | -37.9449 | 145.0716 |  | 1816429 | HT 13 | 22kV AC | Urban | - insulators | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5149 | 20170124UTD_03 | X-arm burnt east of CH8142 requires replacment. lis 1816429. No other damage or any other fire observed in the vacinity at the time.
1843 | United 16/68 | United | 2017-01-29 | 0.14785 | -38.2147 | 145.113 |  | 8831026 | MTN22 | 22kV AC | Rural Short | - crossarm (steel) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | Very high | 1 | 1 | 5159 | 20170208UTD_02 | A Possum seems to have bridhes between the steel crossarm and to bridging bar on the HV ABC interface igniting a fire on the Raychem coverfuseon the fuse unit at MT0102 LIS#8831026.
1844 | United 16/69 | United | 2017-01-31 | 0.2934 | -37.9442 | 145.0581 |  | 1823700 | MR 33 | Low voltage AC (<1kV) | Urban | - overhead service conductor (residential) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5160 | 20170203UTD_06 | ABC service cable leads (150mm) cable caught fire (load) - passed on to construction crew to replace them. LIS 1823700
1845 | United 16/70 | United | 2017-02-01 | 0.42471 | -37.9168 | 145.1712 |  | 620680 | MGE22 | 22kV AC | Urban | - insulators | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5163 | 20170206UTD_03 | Change x-arm, LIS 0620680. Pole Fire
1846 | United 16/71 | United | 2017-02-08 | 0.63132 | -37.9266 | 145.1026 |  | 8804574 | CDA23 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5165 | 20170209UTD_01 | As per mfb fuse box on pole burnt out -- fault crew replaced 3phs FMJB at pole end LIS #8804574.
1847 | United 16/72 | United | 2017-02-08 | 0.70903 | -37.9779 | 145.166 |  | 619181 | NP Z/S | 22kV AC | Urban | - capacity balancing units | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5166 | 20170209UTD_02 | Reactor Capacitor Bank failed and caught fire at NP Zone Sub . No cap can ruptured. Closest LIS 0619181. Fire brigade attended site to extinguish.
1848 | United 16/73 | United | 2017-02-13 | 0.38174 | -38.1322 | 145.1246 |  | 3309074 | FTN14 | 22kV AC | Urban | - insulators | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5171 | 20170214UTD_02 | X arm fire at T pole lis 3309074 Nepean Hwy Allawah ave. CFA in attendance. HV Xarm replaced
1849 | United 16/74 | United | 2017-02-13 | 0.48194 | -37.9532 | 145.0756 |  | 1819881 | HT 11 | 22kV AC | Urban | - fuse (powder filled) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5172 | 20170214UTD_03 | HV fuse assembly faulted with pieces of porcelain making contact with vehicle, small grass fire started in private porperty around the ground type substation., 3x2m. Lis 1819881
1850 | United 16/75 | United | 2017-02-25 | 0.40155 | -37.926 | 145.2151 |  | 618004 | MGE32 | Low voltage AC (<1kV) | Urban | - switch (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5184 | 20170227UTD_01 | Burntout krone box on S/S, on west cct and also repl mtr of 95 ABC and installed 3 x 125amp fuses, krone box caught fire, fire report #03966, only krone box damaged by fire, lis 0618004
1851 | United 16/76 | United | 2017-03-03 | 0.71785 | -38.1188 | 145.1404 |  | 3304726 | FTN25 | Low voltage AC (<1kV) | Urban | - lamps (minor road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5190 | 20170306UTD_02 | isolated supply to pe cell and watchman light - burnt out - fire ignition report 04562 lis 3304726 - ref to SL to follow - Luke Baxter has taken photos
1852 | United 16/77 | United | 2017-03-04 | 0.64831 | -37.8619 | 145.1368 |  | 600806 | EB 22 | Low voltage AC (<1kV) | Urban | - overhead service conductor (residential) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5188 | 20170306UTD_01 | repl 2core service rubbed through by council tree, tree & service caught fire/MFB in attendance, fire out by time crew arrived, LIS 0600806, fire ignition report #02821
1853 | United 16/78 | United | 2017-03-05 | 0.63333 | -38.4224 | 144.8869 |  | 1312279 | RBD21 | Low voltage AC (<1kV) | Rural Short | - connection box | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5189 | 20170309UTD_01 | Red phase had burnt out at fmb at pole and started small grass fire at base of pole, due to loose connection, LIS 1312279. Fre already extinguished by CFA No damage to pole or other property, only grass at base of pole affected by fire.
1854 | United 16/79 | United | 2017-03-06 | 0.85208 | -37.8295 | 145.2005 |  | 7031323 | RWT24 | Low voltage AC (<1kV) | Urban | - connector / termination | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5191 | 20170309UTD_02 | Burnt LV lead/connection on white phase, requires replacement. No sign of firestart, no ground burn or assets showing sign of fire damage but MFB advised visible flames when they first arrived on site, firestart report #2704, lis 7031323,
1855 | United 16/80 | United | 2017-03-09 | 0.56892 | -38.0525 | 145.1164 |  | 8817371 | CRM12 | Low voltage AC (<1kV) | Urban | - connector / termination | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5196 | 20170316UTD_01 | White phase ampact has been shorting on LV conductor on lis # 8817371, has dropped molten metal down on vehicles underneath. Fire ignition report 00342, 1 car damaged by melted metal.
1856 | United 16/81 | United | 2017-03-12 | 0.49693 | -37.98 | 145.1199 |  | 608434 | SS 23 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5197 | 20170317UTD_01 | Private tree at 47 Village Drive contacted HV conductors and caught alight briefly
1857 | United 16/82 | United | 2017-03-15 | 0.74951 | -38.3783 | 144.9253 |  | 1311305 | RBD12 | Low voltage AC (<1kV) | Rural Short | - connector / termination | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 5198 | 20170317UTD_02 | o/s #5 Goolgowie - lis 1311305. Fire ignition on the ground to some trees. fire was out on arrival by CFA. Crew replaced a red ph copper to ally d on the LV from the red ph transformer lead (Murawa Goolgowie s/s ) to the main.
1858 | United 16/83 | United | 2017-03-20 | 0.83744 | -37.9388 | 145.1628 |  | 8805944 | SVW55 | Low voltage AC (<1kV) | Urban | - lamps (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5200 | 20170322UTD_01 | lis # 8805944 - street light pole in ctr medium strip - MFB on site stated street light head was on fire - crew found and replaced blown 50a fuse restoring supply to all street lights - i) #8805944 - refer new t/o #1025737 to replace street light
1859 | United 16/84 | United | 2017-03-22 | 0.28109 | -37.9716 | 145.015 |  | 1817406 | BR 13 | Low voltage AC (<1kV) | Urban | - overhead service conductor (residential) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5207 | 20170329UTD_03 | replaced 3phs grey twisted service -lis: 1817406 -(fire was at clamp of old service, new style clamp fitted on old grey twisted service which is no-complient) - fire out when crew arrived - no damage to customers premise
1860 | United 16/85 | United | 2017-03-27 | 0.79896 | -38.4777 | 145.0239 |  | 1313402 | DMA 23 | 22kV AC | Rural Short | - insulators | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 5210 | 20170330UTD_03 | LIS # 1313402 - no fire visible when crew arrived on site, burnt pole top, insulators tracking caused pole to burn at eyebolts on centre phase, top of pole to be cut away and assets lowered, pole OK and does not require replacement -
1861 | United 16/86 | United | 2017-03-29 | 0.65287 | -37.9783 | 145.0395 |  | 1811906 | BR 15 | 11kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 5214 | 20170403UTD_01 | Ref to TO# 1030380, found and cleared private tree branches at #141 Pellatt St, Tree cause a fault current that melted bridges causing a small ground fire Fire ignition # 05626
1862 | United 16/87 | United | 2017-04-03 | 0.84063 | -38.1609 | 145.21 |  | 3312792 | LWN23 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 5215 | 20170405UTD_01 | Crew replaced a b ph service pole box which was also the tranny isolator. Fire report num is 04564. Whispir sent. LIS 3312792
1863 | United 16/88 | United | 2017-04-11 | 0.51736 | -37.9455 | 145.0224 |  | 1824943 | SR 24 | 11kV AC | Urban | - insulators | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5223 | 20170425UTD_04 | SR24 FDR exit sw CH1751 failed. Hv isolator failed on footpath failed/broke apart. 11kv tracked onto arm and created hotspot on pole which burnt. replaced 66kv pole, 66 inter arm, 11kv term with hv isolators, replaced all 66kv insulators.
1864 | United 16/89 | United | 2017-04-14 | 0.016134 | -37.825 | 145.1692 |  | 8800163 | NW 21 | 22kV AC | Urban | - fuse (boric acid) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5224 | 20170425UTD_05 | BA Fuse Candled at BH1074 Joyce St, cnr Central Rd LIS= 8800163
1865 | United 16/90 | United | 2017-04-25 | 0.32337 | -38.016 | 145.0937 |  | 3302271 | MC 01 | Low voltage AC (<1kV) | Urban | - LV pillar | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 5226 | 20170430UTD_04 | UG pillar burnt out at LIS 3302271, Fire start report no# 05281, fire was at pillar only no damage to anything external.
1866 | United 16/91 | United | 2017-05-28 | 0.56748 | -37.946 | 145.0675 |  | 1816401 | HT 06 | 22kV AC | Urban | - fuse (powder filled) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5238 | 20170601UTD_01 | Rph 31.5 PFF fuse candled and exploded with porcilan over the ground causes scorching of the grass below. No other damage to assets. Crew suspect fuse was already cracked and has finally failed. lis 1816401. Fire reprot 02522.
1867 | United 16/92 | United | 2017-06-13 | 0.77502 | -38.0125 | 145.1572 |  | 634631 | KBH34 | Low voltage AC (<1kV) | Urban | - overhead conductor (insulated) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5246 | 20170615UTD_02 | lis: 34631 - crew isolated supply at TX Hutton P13 Chapel - caused by short cct on Tx Lv leads - LV leads Krone box etc replaced.
1868 | United 16/93 | United | 2017-06-25 | 0.55404 | -37.9732 | 145.0143 |  | 1817994 | BR 13 | Low voltage AC (<1kV) | Urban | - underground service cable (residential) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5255 | 20170721UTD_04 | LIS# 1817994 - O/S 278 , as per MFB please check pole. Car crashed into pole has damaged LV u/g conductors and caused fire damage to pole. lv inter pole fire damage repot @ 05805
1869 | United 16/94 | United | 2017-06-30 | 0.38112 | -38.1058 | 145.1874 |  | 8814301 | FTN23 | Low voltage AC (<1kV) | Urban | - switch (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 5259 | 20170721UTD_08 | LV chrone box found burnt out at Woodvale-Strathearn S/Stn. S/Stn isolated LV and HV and customers restored via LV //s. krone box has been replaced and 315 amp fuses have been replaced on a all 3 phases lis# 8814301
1870 | Powercor 16/17 | Powercor | 2016-12-07 | 0.55139 | -36.3081 | 145.0319 |  | 33088654 | KYM004 | 66kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 12225 | 20160713PWA_02 | Customers report a tree over the lines at the above address. Reports of smoke/fire. CFA attended site. A Powercor crew attended and found a tree from outside clearance space had fallen across 66kV/22kV/LV conductors between P309 and 310 SHTS KYM 2 line. No conductors had broken. The 66kV protection operated. The 22kV was still alive when crew arrived. Crew observed possible tracking between 22kV conductors and LV conductors via tree. Operations isolated the 22kV feeder at Kyabram ZSS. Crew cut tree clear of lines. Crew inspected 66kV/22kV/LV conductors for damage. No conductor damage evident. LEI was not called to site and did not attend. No reports of damage from customers on the day. No shocks, injuries or ground fire starts.
1871 | Powercor 16/18 | Powercor | 13/07/2016 | 0.9625 | -37.0534 | 142.7767 |  | 30252068 | STL006 | Low voltage AC (<1kV) | Rural Long | - fuse (any other type) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 12229 | 20160715PWA_02 | The CFA reported the fuse box smouldering at the above location. When our crew arrived they found that the connections into an LV Service Fuse Base on the meter board had overheated and caused a small fire. The fire was contained to a small area of the meter board (4cm diameter hole). The crew isolated supply and carried out the necessary repairs. There was no ground fire or reported injuries.
1872 | Powercor 16/19 | Powercor | 15/07/2016 | 0.83333 | -35.9782 | 145.741 |  | 32182471 | CME014 | 22kV AC | Rural Short | - fuse (boric acid) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 12236 | 20160719PWA_01 | Customer reported sparking transformer at the incident location. On arrival the crew found that a Boric Acid HV fuse had candled, the fuse remained in the carrier intact. Crew pulled the 2 other fuses, which stopped the candling on the red phase. There were no reported injuries, no ground fire, no damage to 3rd party property.
1873 | Powercor 16/20 | Powercor | 15/07/2016 | 0.79375 | -36.5875 | 142.3889 |  | 32090075 | HSM001 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 12235 | 20160718PWA_02 | VicFire reported a pole fire at the incident location. On arrival the crew found that a high voltage wooden SWER s/s pole had burnt through approximately 4m above ground and had fallen to the ground. There was no ground fire. There were no reported injuries.
1874 | Powercor 16/21 | Powercor | 15/07/2016 | 0.19375 | -37.4144 | 143.1289 |  | 30005619 | BAS011 | Low voltage AC (<1kV) | Rural Long | - connection box | two phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 12233 | 20160715PWA_04 | VicFire reported a pole fire at the incident location. On arrival the crew found that a low voltage junction box mounted on Challicum 1 wooden SWER s/s pole had burnt through and required replacement. There was no ground fire. There were no reported injuries or third party property damage.
1875 | Powercor 16/22 | Powercor | 22/07/2016 | 0.45278 | -38.3024 | 142.3071 |  | 33102370 | KRT013 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 12283 | 20160802PWA_05 | A Fault crew attending an outage found that an EDO fuse had operated at the incident location, however the barrel of the EDO fuse stayed in position without dropping down. The barrel then caught fire. There was no ground fire. There were no reported injuries or third party property damages.
1876 | Powercor 16/23 | Powercor | 24/07/2016 | 0.77222 | -37.9232 | 141.2754 |  | 30089503 | PLD003 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 12289 | 20160803PWA_02 | A customer reported a small fire at the top of a pole. On arrival the attending crew found that a fire had burnt and significantly damaged substation pole Dartmoor town 18. There was no evidence of ground fire identifiable. There were no reported injuries. Crew identified termination/s of insulated HV dropper set (centre phase) was resting on step iron and fire had ignited at this point. Longer HV insulated lead set had been used and extended to reach HV fuse units. Attending crew isolated supply and made temporary repairs. Pole to be replaced 25 July 2016.
1877 | Powercor 16/24 | Powercor | 25/07/2016 | 0.86111 | -34.2908 | 142.1854 |  | 33109198 | RCT023 | 22kV AC | Rural Long | - transformer (pole mounted) | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 12298 | 20160804PWA_01 | VicFire Comms reports a transformer on fire at intersection of Avocat Avenue and Moonah St Red Cliffs. On arrival the crew found Moonah P1A ACR transformer on fire and lid had come off transformer. Isolated ACR and bypassed to restore supply. There was no ground fire. There were no reported injuries or third party property damages.
1878 | Powercor 16/25 | Powercor | 2016-01-08 | 0.96875 | -37.6086 | 144.5901 |  | 33077208 | MLN012 | Low voltage AC (<1kV) | Rural Short | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 12324 | 20160818PWA_04 | Customer reported fire at substation pole across the road. (Diggers Rest P1 substation is a 63kVA??? transformer on a 12.5m/8kN concrete pole) A Powercor crew attended and made the site safe by disconnecting the transformer LVABC FSD isolator and LV leads. LV Leads were re-dressed and a new transformer LVABC FSD isolator was fitted. There were no reported injuries. There was no ground fire.
1879 | Powercor 16/26 | Powercor | 2016-08-08 | 0.38958 | -38.2405 | 142.9159 |  | 30042402 | TRG004 | Low voltage AC (<1kV) | Rural Short | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 12340 | 20160822PWA_02 | CFA reported pole fire at the incident location. On arrival the crew found that a low voltage connection had overheated and caught fire resulting in damage to the connector. There was no ground fire. There were no reported injuries.
1880 | Powercor 16/27 | Powercor | 15/08/2016 | 0.425 | -36.3652 | 145.2999 |  | 33088545 | MNA014 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 12319 | 20160815PWA_03 | On arrival the fault crew found that a 22kV overhead conductor had broken off at the dead end and the conductor was hanging low about 1.5 meters. The conductor dead end appears to have broken as a result of a flashover involving two black ducks (both deceased) on the substation. The conductor fell and is hanging supported by the “live line clamp and flex” resting in fruit trees and trellis of the fruit trees some of which have been burnt. In addition it appears the galvanized wires supporting the fruit trees were ”ALIVE” at 22kV. The incident has caused damage to a section of polytube irrigation (20 meters) which was running along the ground near the fruit trees. Two areas have been burnt (9m by 1m & 8m by 1m). Total area burnt about 17 meters square. Also burning evident on some small trees. The crew prepared to isolate the area when the MNA14 22kV feeder circuit breaker tripped. There was no injury as a result of this incident.
1881 | Powercor 16/28 | Powercor | 19/08/2016 | 0.41181 | -34.1714 | 142.0654 |  | 30099608 | MBN021 | Low voltage AC (<1kV) | Rural Short | - overhead service conductor (residential) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 12335 | 20160819PWA_07 | A employee reported a service wire on the ground at the incident location. On arrival the crew found that a service cable had broken and came to the ground alive resulting in burnt a patch of ground approx. 0.5msq. No protection operated. There were no reported injuries, shocks or third party property damages.
1882 | Powercor 16/29 | Powercor | 21/08/2016 | 0.75833 | -37.9585 | 144.6864 |  | 30110409 | WBE034 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 12372 | 20160901PWA_04 | Customer called the incident in to Powercor. Customer reported a fire on a pole outside his house. He indicated that the fire was extinguished, but sparking was still occurring at the time of his call. There was no ground fire. A Powercor crew attended and discovered that a vehicle had collided into pole LIS 203209 in Diggers Rd. The collision impact had caused an outer phase HV conductor to break free from the HV insulator and fall below the HV crossarm making contact with a wet pole surface. The conductor to pole contact duration was sufficient enough to cause charring/burning of the pole section to require replacing the pole. A damaged vehicle was discovered approx. 100m further along the road, but the driver, or occupants were not present at the scene. There were no reported injuries.
1883 | Powercor 16/30 | Powercor | 2016-08-09 | 0.26389 | -37.9674 | 144.1308 |  | 30068949 | GL015 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 12406 | 20160913PWA_02 | A customer reported a small flame on the middle of cross arm at the incident location. On arrival the crew found that an EDO fuse had operated. And they also found evidence of smouldering, however the barrel of the EDO fuse stayed in position without dropping down. No ground fire. There were no reported injuries. No third party property damage.
1884 | Powercor 16/31 | Powercor | 2016-09-09 | 0.62014 | -38.3115 | 142.4293 |  | 33100239 | KRT031 | 22kV AC | Urban | - connection box | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 12420 | 20160915PWA_01 | A reclose occurred on the KRT031 CB at 1441 on 9/9/16. The customer at the incident location called to report they had no supply. On arrival the crew found a blown HV fuse on the substation, with a crow lodged on the Guthrie guard. The customer later reported that at the time of the outage, some of his cows fell down in the dairy, however they recovered quickly. The crew could see no indications of a HVI, they did however find a splash mark on the earth at the base of the concrete substation pole. After removal of the bird, the crew replaced the HV fuse, which resulted in a meter at the dairy catching fire, supply was quickly isolated. Minor damage was caused to the meter board, however the board remained serviceable. An LEI was called, and further tests revealed a burnt off neutral connection in a junction box. No third party damage, no injuries.
1885 | Powercor 16/32 | Powercor | 2016-10-09 | 0.79583 | -36.1442 | 144.7336 |  | 33083600 | ECA012 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 12415 | 20160914PWA_02 | Vic Fire reported a fire on a pole at the incident location. On arrival the crew found that a LV FOLCB had failed and caught on fire, no ground fire occurred as a result. There were no reported injuries, no third party damage.
1886 | Powercor 16/33 | Powercor | 2016-11-09 | 0.044444 | -36.4412 | 145.3626 |  | 33096154 | MNA024 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 12426 | 20160916PWA_01 | Vic Fire reported a fire on a pole at the incident location. On arrival the crew found that a LV FOLCB had failed and caught on fire, no ground fire occurred as a result. There were no reported injuries, no third party damage. Failure of FOLCB coincided with underfloor heating time-switch operation, validated by customer whom I spoke with whilst obtaining photos the following day ( schedule Shepparton visit ).
1887 | Powercor 16/34 | Powercor | 14/09/2016 | 0.59722 | -36.7725 | 144.4393 |  | 33031488 | BET005 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 13220 | 20170714PWA_03 | Crew attending outage found damaged and burnt SWER pole-top. Centre phase burnt off pole-top. Crew repaired and replaced with new 'P' bracket.
1888 | Powercor 16/35 | Powercor | 23/09/2016 | 0.37986 | -38.1846 | 144.3666 |  | 33040421 | GLE012 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 12456 | 20160927PWA_01 | A customer reported a transformer on fire at the incident location. Upon arrival, the Powercor crew found that an overheated FSD ignited and the fire self-extinguished. The crew made the place safe and repairs done. There were no injuries or ground fire.
1889 | Powercor 16/36 | Powercor | 2016-06-10 | 0.83681 | -38.0765 | 144.3692 |  | 30268929 | FNS021 | 22kV AC | Rural Short | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 12484 | 20161012PWA_05 | CFA reported wire crossing roadway on fire. Upon arrival, the Powercor fault crew found a car had hit the pole and left the scene. The centre phase HV conductor tie had broken and the HV was resting on the x-arm. The LV x-arm had burnt through at the neutral pin and broken off. No reported injuries or ground fire.
1890 | Powercor 16/37 | Powercor | 15/10/2016 | 0.60347 | -37.4896 | 144.5674 |  | 30034797 | GSB011 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 12493 | 20161017PWA_01 | Customer reported a tree over HV conductors at the incident location. On arrival the crew found that a HV conductor had been brought down by a large tree, resulting in a several small ground fires, 4m square in total. It is suspected that the conductor remained back-fed through transformer HV windings until the feeder protection eventually cleared the fault. Conductors were down over the Gisborne to Bacchus Marsh road also until crews arrived on site and made safe. There were no reported injuries.
1891 | Powercor 16/38 | Powercor | 15/10/2016 | 0.49306 | -37.4234 | 144.5202 |  | 32045417 | WND011 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 12494 | 20161017PWA_02 | Customer reported a fire at the incident location. On arrival the crew found that a HV conductor had been brought down by a tree, a ground fire of 1500m square resulted where the HV conductor broke and came to the ground. Protection operated, however a localised backfeed through transformer HV windings meant the downed conductor remained partially energised. There were no reported injuries.
1892 | Powercor 16/39 | Powercor | 15/10/2016 | 0.49097 | -37.5078 | 144.58 |  | 30034631 | GSB011 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 12507 | 20161021PWA_03 | Vic Fire reported HV conductors in contact with vegetation at the incident location. On arrival the crew found that a HV t/off cross-arm on Bundaleer P2 broke causing conductor to hang low and make contact with vegetation beneath, the arcing intermittently caused the vegetation to ignite, initial report made reference to flames and sparking. Spur was isolated and repairs carried out. There were no reported injuries, no ground fire & no 3rd party damage.
1893 | Powercor 16/40 | Powercor | 15/10/2016 | 0.42292 | -37.4158 | 144.5879 |  | 32043265 | GSB014 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 12530 | 20161102PWA_03 | SCADA alarm indicated supply had been lost beyond “Mt Macedon P130 ACR”. On arrival and subsequent line patrol the crew found that a branch from a cypress tree had fallen over conductors outside #9 Clarke Street, Macedon caused the ACR to trip to L/O, the branch had evidence of arcing and was heavily charred where it was in contact with the 22kV conductors. There were no reported injuries, no ground fire & no 3rd party damage.
1894 | Powercor 16/41 | Powercor | 15/10/2016 | 0.60764 | -34.1977 | 142.0373 |  | 33066831 | MBN014 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 12495 | 20161017PWA_03 | Customer reported a supply interruption and wires hanging low at the incident location. On arrival the crew found that a birds nest containing numerous pieces of wire had shorted out between the concrete pole and an LV isolator, resulting in the wooden LV crossarm burning through and failing. Falling combusting material also started a ground fire of approximately 10m square which self extinguished.
1895 | Powercor 16/42 | Powercor | 18/10/2016 | 0.87292 | -37.6339 | 143.5736 |  | 30000848 | BAS011 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | within electric line construction area | 19.8 | No forecast | 0.1 | 1.98 | 12499 | 20161019PWA_01 | Vic fire reported a pole fire at the incident location. On arrival the crew found that the connections in a 3 phase fused mains box (FOLCB) had overheated, resulting in the box catching fire. Crew made the site safe and performed repairs. There was a small ground fire. There were no reported injuries.
1896 | Powercor 16/43 | Powercor | 18/10/2016 | 0.80694 | -38.3464 | 143.7838 |  | 32062029 | CLC007 | Low voltage AC (<1kV) | Rural Long | - underground cable | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 12508 | 20161021PWA_04 | The CFA reported a pole fire at the incident location. On arrival the crew found that a Low Voltage underground cable had faulted and showed signs of burning. Talking to the crew there was no ground fire. No third party damage or injury was reported. The crew suspect moisture ingress as the cause of the cable faulting. The crew made the site safe, replaced the cable and supply was restored.
1897 | Powercor 16/44 | Powercor | 25/10/2016 | 0.575 | -38.0764 | 142.8706 |  | 32060489 | TRG002 | 12.7kV AC (SWER) | Rural Long | - fuse (any other type) | single wire earth return (SWER) | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 12522 | 20161027PWA_03 | A customer reported that she had heard a loud bang and had seen sparks from across the road at the incident location. On arrival the crew found that a large dead pine tree had fallen onto the 12.7kV SWER conductor and eventually caused the conductor to break and fall to the ground. The barrel of the SWER HV fuse on the ISO pole burnt through and part of it fell to the ground. There was no ground fire or injuries.
1898 | Powercor 16/45 | Powercor | 27/10/2016 | 0.48264 | -38.4182 | 144.1703 |  | 30061324 | WPD014 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 12537 | 20161108PWA_01 | The fire brigade reported a pole fire at the incident location. On arrival the crew found that a 3 phase fused mains box controlling two underground services had overheated and caught fire. There was no ground fire or injuries.
1899 | Powercor 16/46 | Powercor | 30/10/2016 | 0.70139 | -36.7941 | 144.2654 |  | 32053336 | BET007 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 12528 | 20161102PWA_01 | VicFire reported a tree over HV conductors ( as conductors smoking ) at the incident location. On arrival the crew found that a HV conductors had been brought down by a large tree from across the road, resulting in a small ground fire, 3m square in total. Cross arm on P15 had broken due to the impact and required replacing. There were no reported injuries or 3rd party damage. Protection operated.
1900 | Powercor 16/47 | Powercor | 30/10/2016 | 0.56597 | -37.7175 | 144.0334 |  | 30010307 | BAS022 | 12.7kV AC (SWER) | Rural Long | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 12527 | 20161031PWA_02 | A customer reported a tree was on an overhead conductor and a small grass fire has started at the incident location. On arrival the crew found that a tree had fallen onto the 12.7 KV SWER conductor causing it to break and fall to the ground, resulting in a ground fire. The crew made the site safe and performed repairs. There was a small ground fire approximately 60 Square metres. There were no reported injuries.
1901 | Powercor 16/48 | Powercor | 31/10/2016 | 0.72847 | -36.585 | 145.2366 |  | 33095223 | MNA034 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 12531 | 20161102PWA_04 | Vic Fire reported a fire on a pole at the incident location. On arrival the crew found that a LV FOLCB had failed and caught on fire, no ground fire occurred as a result. There were no reported injuries, no third party damage. Failure of FOLCB suspected to be load related, large dairy connected. Supply arrangement on pole appears to have altered since street view photo taken ( FOLCB was previously on support cross-arm ).
1902 | Powercor 16/49 | Powercor | 2016-02-11 | 0.59583 | -36.3149 | 145.4207 |  | 33091042 | SHN011 | 66kV AC | Rural Long | - insulators | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 12533 | 20161104PWA_02 | A customer called to advise of a grass fire at the above location. A crew attended and found a fire had started at the base of a concrete 66/22kV double CCT P27 SHTS-NKA No1 66kV line. Area burnt was approx. 1m sq. Fire had self-extinguished. No CFA in attendance. No cause for the fire start could be identified but OPS advise there was a 66kV flash over and grass fire at P123 SHT-NKA No2 6kV line at the same time as this reported ground fire start.
1903 | Powercor 16/50 | Powercor | 2016-06-11 | 0.24444 | -37.3372 | 141.07 |  | 32130701 | HTN004 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 12553 | 20161116PWA_03 | From 5:52am on Sunday 5 Nov 2016, Powercor started to receive calls from customers in the Dorodong area, reporting dim lights. Crews were dispatched to the area and found a HV fuse had operated on P1 Dorodong line. Crews patrolled the area and later in the morning found a HV conductor on the ground and evidence of a cross arm fire at angle pole P66 Dorodong (LIS 721655). There were no ground fires, injuries or 3rd party property damage reported.
1904 | Powercor 16/51 | Powercor | 2016-11-11 | 0.99861 | -36.8659 | 143.8042 |  | 32032402 | KGT004 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 12601 | 20161130PWA_02 | From 1.22am on Friday 11 Nov 2016, Powercor started to receive calls from customers in the Lake Meran area, reporting a pole fire. Crews were dispatched to the area and found a Xarm fire on P130 Boort line (LIS 708869). Crews isolated the line and made safe. There were no ground fires, injuries or 3rd party property damage reported.
1905 | Powercor 16/52 | Powercor | 2016-12-11 | 0.33194 | -35.5213 | 142.9845 |  | 32156207 | CTN003 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started by lightning striking a distribution system or a part of a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 12602 | 20161130PWA_03 | Powercor started to receive calls from customers in the Sea Lake area, reporting a pole fire. Crews were dispatched to the area and found a lightning strike/pole fire on P32 BOIGBEAT EAST. There were no ground fires, injuries or 3rd party property damage reported.
1906 | Powercor 16/53 | Powercor | 16/11/2016 | 0.45833 | -38.283 | 144.3152 |  | 33106443 | WPD022 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 12554 | 20161116PWA_04 | A customer reported loss of power to their residence near the incident location. On arrival the fault crew found that the FMJB mounted on the concrete pole had caught fire and burnt out at the incident location. The fire had self-extinguished. The crew replaced the FMJB. There was no ground fire and no injury as a result of this incident.
1907 | Powercor 16/54 | Powercor | 18/11/2016 | 0.41389 | -34.1838 | 142.1297 |  | 33064891 | MDA033 | 22kV AC | Urban | - fuse (any other type) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 12567 | 20161122PWA_05 | A customer reports grass smoking at base of a pole at the incident location. A crew attended and found a bird at the base of SW/P1 MDA Golf S/L and 2 blown HV fuses on the SW pole. One of the fuses had hung up and burnt, dropping debris to the ground starting a grass fire of approx. 1sqm at the base of the pole. CFA did not attend and the fire had self-extinguished before the crew arrived. All 3 HV fuses at P1 where removed and listed for FFU for another crew to replace a fuse unit and 3 fuses the next day. This left 2 substations at the golf club off supply overnight. Next day another crew attended and replaced a fuse unit and all 3 fuses. No shocks, injuries or 3rd party property damage.
1908 | Powercor 16/55 | Powercor | 19/11/2016 | 0.86319 | -36.7185 | 144.2535 |  | 30223654 | EHK031 | Low voltage AC (<1kV) | Rural Short | Public lighting | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 12606 | 20161201PWA_03 | CFA, reported street light lantern on fire Corner Victoria Street & High Street, Eaglehawk outside 48-48A High Street. When crew arrived onsite the fire had extinguished and CFA no longer present. The 150W HP Sodium lantern had burnt internally and required replacement. There was no ground fire, no reported property damage or reported injuries.
1909 | Powercor 16/56 | Powercor | 19/11/2016 | 0.8125 | -36.5368 | 145.3051 |  | 31035936 | MNA034 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 12562 | 20161121PWA_06 | A customer called to advise that they had lost supply to their pump and a grass fire had started that they attended to extinguish. A crew attended and found a fire had started at the base of a wood pole 11 Elliott Spur at 1375 River Road TOOLAMBA. Area burnt was approx. 10m X 8m. The cause was a burnt out blue phase connection in customers FOLCB on their underground supply. There were no reported injuries, shocks or third party damage.
1910 | Powercor 16/57 | Powercor | 19/11/2016 | 0.68264 | -36.3655 | 145.2987 |  | 33089756 | MNA014 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 12561 | 20161121PWA_05 | A customer called to advise that there was a fuse blow at the neighbours transformer and a grass fire had started that the CFA attended onsite. A crew attended and found a fire had started at the base of a concrete pole 3 Gag Spur at 420 Ardmona Road ARDMONA . A crow was found at the site of ignition. Area burnt was approx. 15m X 10m. CFA in attendance. There were no reported injuries, shocks or third party damage.
1911 | Powercor 16/58 | Powercor | 21/11/2016 | 0.77222 | -38.2628 | 144.3971 |  | 30063270 | WPD024 | 22kV AC | Rural Short | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very High | 1 | 4.6 | 12569 | 20161122PWA_02 | customer called to report tree branch on line sparking and on fire at the incident location. Powercor crew found multiple small burnt patches on ground, self-extinguished caused by branch falling on line and small pieces falling to the ground alight (largest approx.. 10cm²). HV may have contacted LV, LEI informed. No injury or third party damage.
1912 | Powercor 16/59 | Powercor | 21/11/2016 | 0.72917 | -38.151 | 144.366 |  | 32076201 | GCY012 | Low voltage AC (<1kV) | Urban | - overhead service conductor (commercial / industrial) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 12570 | 20161122PWA_03 | VicFire called to report sparking wires caused a grass fire at the incident location. Powercor crew found a tree branch had fallen on a 2 wire bare service causing it to spark which ignited a small tree near the line. Fire was approx.. 1m x 1.5m. Tree was in front yard of property.
1913 | Powercor 16/60 | Powercor | 21/11/2016 | 0.70556 | -38.132 | 144.2665 |  | 32084337 | GL012 | 22kV AC | Rural Long | - switch (disconnector/isolator) | three phase | Started by lightning striking a distribution system or a part of a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very High | 1 | 4.6 | 12568 | 20161122PWA_01 | A Powercor employee called to report a fire start at the base of our pole after noticing CFA activity at the incident location. A reclose was recorded on the feeder prior to this and may have been a lightning strike in the vicinity of the switch pole. Upon inspection the switch was black and the fire (1m x 10m) appears to have originated at or close to the switch earth. A fuse was also down on the substation 1 pole to the east but no other visible damage. No injury or third party damage.
1914 | Powercor 16/61 | Powercor | 21/11/2016 | 0.70208 | -36.5736 | 143.9373 |  | 32033600 | EHK024 | 22kV AC | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 12571 | 20161122PWA_04 | CFA reported a broken tree branch has fallen across the HV cables at 222 Bridgewater – Serpentine Road BRIDGEWATER and is burning. When crew arrived on site the 3/2.27 steel cable had burnt through and a small grass fire approximately 12 metres X 10 metres along the road reserve had been contained by the attending CFA. Isolations were established and repairs made after another crew were called to bring a crossarm and hardware to replace the damaged crossarm at Pole # 1 Morse Spur after shock of the falling cable. There was no injuries or third party property damage.
1915 | Powercor 16/62 | Powercor | 21/11/2016 | 0.60417 | -36.4702 | 145.6211 |  | 30130885 | STN011 | 12.7kV AC (SWER) | Rural Long | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 12565 | 20161123PWA_01 | Customers reported loss of supply near the incident location. On arrival the fault crew found that an old disused crane had been left under a SWER line. Due to hot weather the line had sagged, a bird (pigeon) perched on top of this crane has caused a flashover between line and the old disused crane. The flashover caused a small fire to be ignited at the base of the crane of approximately 1m by 1m. SWER was measured to be 5.9m above ground, the crane has been moved away from the line. There was no injury as a result of this incident.
1916 | Powercor 16/63 | Powercor | 24/11/2016 | 0.63333 | -38.5466 | 143.5057 |  | 32064661 | CLC006 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within electric line construction area | 19.8 | Low-moderate | 0.2 | 3.96 | 12610 | 20161206PWA_01 | An employee doing a line condition audit found a crossarm had caught fire and self-extinguished at the incident location some time previous to the audit. The crossarm was listed as a P1 item and changed later that evening. There was no ground fire. No third party damage or injury was reported.
1917 | Powercor 16/64 | Powercor | 24/11/2016 | 0.5 | -37.8628 | 142.5647 |  | 30043100 | TRG002 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 12617 | 20161208PWA_02 | The property owner reported a pole fire at the incident location. A crew attended and found the customers U/G CB and junction box mounted on the pole had overheated and burnt. Supply was isolated and an REC engaged to replace the customers CB. The crew replaced the junction box, damaged wiring and conduit. There was no ground fire start. No CFA attended. No shocks or injuries.
1918 | Powercor 16/65 | Powercor | 25/11/2016 | 0.44444 | -38.2557 | 143.6316 |  | 30050973 | CLC003 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 12583 | 20161128PWA_01 | The property owner reported a blown fuse and the line on the ground at the incident location. A crew attended and found 1 phase of a Single phase HV line on the ground and 1 HV fuse at the Tee Off blown. A tree branch had fallen across the conductor and broke the conductor approx. 10m from substation P2 Gerrard S/L. The 10m length of conductor hanging from the substation pole remained alive thru back feed from the transformer. The end of the live conductor came into contact with a portion of old wire fencing causing arcing resulting in a grass fire of approx. 1m/sq. The fire had self-extinguished by the time the crew had arrived. No CFA attended. The crew isolated the Gerrard S/L at Tee pole 6 and repaired the 3/12 conductor. No shocks, injuries or third party damage.
1919 | Powercor 16/66 | Powercor | 27/11/2016 | 0.41806 | -36.4055 | 145.3135 |  | 33088557 | MNA021 | 22kV AC | Rural Short | - voltage regulator | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 12584 | 20161128PWA_02 | VicFire reported a transformer “explosion” and ground fire at the incident location. On arrival the crew found that a bird had flashed over between a surge diverter and the HV regulator tank body, the remains of the bird was found on the foundation pad at the base of the regulator, a small ground fire resulted approximately 10M X 4M in area of grass burnt. Some minor damage to one of the HV bushings resulted, the surge diverter will also require replacement. It is unclear if material from the incinerated bird commenced the ground fire or the arc damage ejected material causing the ignition. There were no reported injuries or 3rd party damage. Protection operated ( MNA021 feeder reclosed ).
1920 | Powercor 16/67 | Powercor | 28/11/2016 | 0.34028 | -36.7385 | 142.2015 |  | 33052548 | HSM002 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 12585 | 20161128PWA_03 | Operation received system advise of a lock out of the HSM003 22kV feeder CB at the Horsham ZSS. A customer rang to advise an excavator had struck the overhead line at the above incident location. The attending crew found an excavator had struck the footpath side HV conductor. The excavator struck the O/H conductor while operating near the line. Conductor height was 5.9m over driveway. The line was isolated for repairs. There was a grass fire of approx. 1msq at the base of the excavator. No CFA attended. No shocks, injuries or third party damage. Note: this is the second time in 3yrs that an excavator from this company has struck this same span of conductor. This has been referred to the connections group to speak to the company about a recoverable works job to removing this span when the company builds their new office complex on the adjoining site.
1921 | Powercor 16/68 | Powercor | 30/11/2016 | 0.73611 | -36.9763 | 143.8954 |  | 33011872 | MRO007 | Low voltage AC (<1kV) | Rural Long | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 12603 | 20161201PWA_01 | Customer reported a transformer on fire and associated ground fire at the incident location. On arrival the crew found that a LV fused isolator connection was loose and overheated, dropping molten material to the ground, a small ground fire resulted approximately 7M X 16M in area of grass burnt. Customer advised that they couldn’t get through to the CFA & extinguished the fire, they were concerned about their bore pump as it was apparent that they had partial supply. There were no reported injuries or 3rd party damage. White phase 250A HRC fuse operated.
1922 | Powercor 16/69 | Powercor | 2016-03-12 | 0.38125 | -36.3294 | 145.4157 |  | 33096736 | SHTS-NKA2 | 66kV AC | Unknown | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 12612 | 20161206PWA_03 | SCADA reported protection operations on SHTS-NKA 66KV NO.2 and SHN11 22kV feeders. Crew patrolled between pole 1 and pole 50 of the SHTS-NKA 66KV NO.2 line. On arrival at P22 the crew found that a bird (corella), had flashed over between the centre phase 22kV stand of insulator and the outer phase. (Wø-Bø). The remains of the bird were found at the base of the pole appearing to be the catalyst of the small grass fire which had extinguished itself prior to the crew attending which was approximately 1m X 1m in area of grass burnt. Some minor damage to the stand-off 5 shed centre phase insulator 22kV HV insulator resulted which will require replacement, (top shed cracked in half) due to flashover. FFU has been raised to repair the damaged insulator. There were no reported injuries or 3rd party damage.
1923 | Powercor 16/70 | Powercor | 2016-04-12 | 0.39792 | 34.2989 | 142.2209 |  | 33064221 | RCTS-MBN | 22kV AC | Unknown | - fuse (boric acid) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 12613 | 20161206PWA_04 | Vic fire , Bird hit wires and caused small grass fire CFA on site. CFA had left prior to crew arriving. Upon arrival the crew found that a bird had flashed over between a HV dropper and the line side of a BA fuse unit, the remains of the bird was found on the ground at the base of the pole, a small ground fire resulted approximately 4m radius in area of grass burnt. Some minor damage to HV BA fuse unit was evident due to flashover and was changed as a result. The HV dropper was in good condition upon closer inspection using the EPV therefore was left in service. It is clear that the incinerated bird commenced the ground fire at the base of the pole. There were no reported injuries or 3rd party damage. Protection operated ( N/A ).
1924 | Powercor 16/71 | Powercor | 2016-05-12 | 0.22917 | -37.6726 | 143.4514 |  | 33001737 | BAS021 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 12622 | 20161212PWA_02 | A person driving past a pole noticed the cross arm was on fire at the address below. On arrival the work crew found a cross arm had burnt off and the conductor was still alive in the air. There was no ground fire. No third party damage or injury was reported.
1925 | Powercor 16/72 | Powercor | 2016-11-12 | 0.71528 | -36.472277, | 144.3773 |  | 30237533 | EHK024 | 22kV AC | Rural Long | - fuse (boric acid) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 12625 | 20161212PWA_05 | Vic Fire reported a pole fire at 2024 BENDIGO-TENNYSON ROAD, KAMAROOKA. On arrival the crew found one of the two BA fuses was candling and had caused a fire underneath the pole. No shock, No injuries, Small ground fire 10m x 100m. Third party damage to customer canola crop.
1926 | Powercor 16/73 | Powercor | 2016-12-12 | 0.70486 | -35.8592 | 144.1414 |  | 32035769 | CHA006 | 22kV AC | Rural Long | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 12627 | 20161213PWA_01 | Vic Fire reported a pole fire at corner Leitchville-Kerang Rd and Majors Rd. On arrival the crew found a grass fire and blackened pole. HV bridge on centre phase had burnt out. ESV Notified. No shock, No injuries, ground fire (approx. 30m x 200m sq.m). Third party damage to customer fence + hay bale + burnt paddock.
1927 | Powercor 16/74 | Powercor | 2016-12-12 | 0.625 | -36.7973 | 144.343 |  | 30041489 | BGO013 | 22kV AC | Rural Short | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 12623 | 20161212PWA_03 | Vic Fire reported car hit a pole at 767 Strathfieldsaye Rd Strathfieldsaye. They also reported a damaged cross-arm, wires down on road and footpath, burn marks on houses and a small grass fire. On arrival the crew found that the HV cross-arm had broken, HV conductors were dislodged and LV conductors were on the ground. Car had driven off. A small fire had started on the nature strip that was approx. 2m x 10m. There was a ground fire, no injuries and third-party property damage due to HVI.
1928 | Powercor 16/75 | Powercor | 2016-12-12 | 0.45833 | -37.7628 | 144.8339 |  | 30118234 | SSE012 | Low voltage AC (<1kV) | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 12626 | 20161212PWA_06 | The MFB reported that a truck has hit (side swiped) a pole and started a fire at the incident location. On arrival the fault crew found a truck had collided with pole LIS 21762 adjacent 20 Ayton Road (south side of road) corner Nettlefold Avenue, Sunshine North. The collision resulted in the low voltage wooden cross-arm on this pole breaking in half and the cross-arm and tee-off conductors fell onto the low voltage conductor+X106s below. Contact between the low voltage conductors has caused low voltage bus fuses to operate on the pole three poles north of the incident location (6 Nettlefold Road). Operation of the low voltage fuses caused hot debris to fall on the ground near pole LIS 26585 (6 Nettlefold Avenue) resulting in a small grass fire 2*3 meters (6m2). The MFB were on site and the grass fire has been extinguished. The crew have replaced the broken low voltage cross-arm and restored the blown low voltage bus fuses. There was no injury as a result of this incident.
1929 | Powercor 16/76 | Powercor | 18/12/2016 | 0.5625 | -37.5474 | 144.2327 |  | 32166522 | BMH003 | 12.7kV AC (SWER) | Rural Long | - earth / earthing | single wire earth return (SWER) | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 12653 | 20161223PWA_02 | Mick Van Ravenstein, ATL from Ardeer Construction, rang me, as the NAO AH Ardeer, on Monday 19/12/2016 @13:06, to ask if I was aware and had been notified about a pole fire incident the previous day. I had discussed with Mick that I had not received any phone call nor an email from dispatch regarding a pole fire. Please note, on Sunday 18/12/2016 many IT systems including OMS were down. He let me know that the crew who attended the pole fire was, Tony Esposito and he had photos and all information regarding the incident. I spoke to Tony Esposito on Tuesday 20/12/2016 @ 15:30. Tony advised that the SWER earths at P30E LIS-104332, BLAKEVILLE P30E 25kVA SWER Tx, had been unknowingly damaged at the base of the pole, which had caused a fire at the base of the pole to track upwards along the connection of the earth to the pole. The fire was contained to the base of the pole only up to where the earths were connected, the ground was dry back from the pole but there was no ground fire, the fire was isolated to the pole only. No protection operated, there were no reported injuries or ground fire start.
1930 | Powercor 16/77 | Powercor | 20/12/2016 | 0.79444 | -37.7326 | 144.8239 |  | 30110872 | SA002 | Low voltage AC (<1kV) | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 12648 | 20161222PWA_01 | Mr John Condon phoned in to advise of a wire down and a small grass fire at the incident location. Upon arrival the crew had found that an unknown truck had come into contact with the CATV at the intersection of Calverton Road/Driscolls Rd (southern side of No. 2 Valewood Drive, Kealba 3021) and flicked the Foxtel into the LV above which caused sparks to fall to the ground. The resultant sparks from this caused 2 x minor grass fires and scorch marks on the nature strip approx. 1m x 1m total area, at the intersection of Calverton Road/Driscolls Rd (southern side of No. 2 Valewood Drive, Kealba 3021). LV Bus Fuses (north circuit) operated at Calverton-Hadley Pole substation. The MFB were on site and the grass fire has been extinguished. Police were also on site. There was no injury or shocks as a result of this incident.
1931 | Powercor 16/78 | Powercor | 20/12/2016 | 0.77986 | -36.321 | 145.1125 |  | 32188133 | KYM003 | Low voltage AC (<1kV) | Rural Long | - overhead service conductor (residential) | single phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 12646 | 20161221PWA_02 | Customer reported that they had no supply and that the service cable was on the ground. Neighbour had extinguished a small grass fire. A high load vehicle had made contact with multiphase service mains cable from substation pole direct to house damaging the customers facia board and breaking the service mains cable. Crew attended and the Police were onsite as the service cable was across a main road. Vehicle details unknown by Police in attendance. Small grass fire, Property damage to facia board and customers mains, defect issued and left off supply.
1932 | Powercor 16/79 | Powercor | 20/12/2016 | 0.6 | -37.8672 | 143.4618 |  | 32008602 | BAS021 | 12.7kV AC (SWER) | Rural Long | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any other thing forming part of or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 12647 | 20161221PWA_03 | The CFA reported a machine has struck Power lines at the incident location. On arrival the crew found that a farm sprayer unit had contacted the SWER line when lowering the arms of the sprayer resulting in a strand of the conductor to break and a ground fire to occur. The crew repaired the damaged cable using a splice over the broken strand. There was a ground fire of approximately 100 metres x 50 metres in size. No protection operated. No reported shocks or injuries.
1933 | Powercor 16/80 | Powercor | 20/12/2016 | 0.25972 | -37.7539 | 144.8048 |  | 32167390 | SSE031 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 12650 | 20161220PWA_02 | Powercor fault crew attending an outage (SSE031 feeder) found a pole-top fire at the incident location. The crew isolated the faulty section and restored the feeder. No evidence of ground fire found. Protection operated as expected. There was suspected HVI however no damage was found. A person in the street advised our Operator of a fatality inside a house.
1934 | Powercor 16/81 | Powercor | 20/12/2016 | 0.125 | -36.5729 | 142.359 |  | 30077099 | HSM001 | 12.7kV AC (SWER) | Rural Long | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by lightning striking a distribution system or a part of a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 12644 | 20161221PWA_01 | Whilst responding to a fault, a Powercor fault crew reported that lightning had struck a HV SWER line, resulting in a transformer tank rupturing and spraying oil on the ground and on a nearby shed. The lightning strike also damaged the next pole along the line, resulting in a small grassfire of less than 1 square metre in size. There were no injuries, and the protection operated as expected. Note: This fault occurred at approx. 3am in the morning, however was not reported to the BH NAO until almost 4pm, the AH NAO was reluctant to take on the job at 4pm, so the job was held over to today, hence the lateness of the report.
1935 | Powercor 16/82 | Powercor | 22/12/2016 | 0.39792 | -38.373 | 142.4927 |  | 33099041 | WBL002 | Low voltage AC (<1kV) | Rural Short | Public lighting | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 12655 | 20161223PWA_04 | VicFire reported a streetlight pole on fire at the incident location. On arrival the crew found that a streetlight lantern mounted on a steel pole and bracket, had caught fire. There was no ground fire, no reported third party damage or any injuries. The light was isolated in the UG pit for later replacement when traffic control is available.
1936 | Powercor 16/83 | Powercor | 23/12/2016 | 0.87847 | -37.7445 | 144.778 |  | 33071133 | SA004 | Low voltage AC (<1kV) | Urban | Other | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 12726 | 20170117PWA_05 | Mr Charles reported a meter fire at the incident location and base of meter is melted. No sparking or smoking now but loss of supply. On arrival the Powercor crew found melted meter burnt out switch board and meter panel. The fault crew isolated supply, removed the damaged meter panel and issued a defect notice for the customer to engage a REC to undertake the necessary repairs. There was no ground fire. There were no reported injuries or third party property damages.
1937 | Powercor 16/84 | Powercor | 24/12/2016 | 0.72639 | -36.2563 | 144.7266 |  | 31026711 | ECA012 | 22kV AC | Rural Long | - transformer (pole mounted) | three phase | Started by lightning striking a distribution system or a part of a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 12659 | 20161229PWA_02 | VicFire reported a pole fire at the incident location. On arrival the crew found that a transformer has failed rupturing the tank and the ejected oil had ignited, resulting in fire damage to the pole and commencing a ground fire. It is believed that the transformer had suffered damage due to lightning earlier that morning when the spur was affected by an lightning related outage that the crew attended and replaced a section fuse at P1 Quinn spur. A ground fire of approximately 50m x 60m resulted, some fencing was slightly burnt as the fire passed through it. There were no reported injuries.
1938 | Powercor 16/85 | Powercor | 24/12/2016 | 0.63264 | -36.6664 | 143.9149 |  | 32039847 | BET001 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 12660 | 20161229PWA_03 | VicFire reported wire down and ground fire at the incident location. On arrival the crew found that large tree branch had come away from a tree outside the clearance space and fallen onto 1 phase of the 3 phase 22kV line, breaking the conductor and commencing a ground fire. A ground fire of approximately 120Ha resulted, an estimated 300>600M of fencing was burnt to varying degrees and 2 farm sheds also damaged by the fire, at least 12 CFA tankers attended and clean up was still occurring at 8pm as the fire had got into vegetated areas along the river side. There were no reported injuries. Protection operated, 1 fuse at SW/P 10032 operated, and Marong ACR on the BET001 feeder tripped to lockout for the incident.
1939 | Powercor 16/86 | Powercor | 24/12/2016 | 0.49931 | -35.8124 | 144.2144 |  | 32038108 | CHA003 | 22kV AC | Rural Short | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 12658 | 20161229PWA_01 | Powercor fault crew reported ground fire(s) associated with lightning strike to 22kV overhead conductors at the incident location. On arrival the crew found that lightning had struck overhead conductors between SW/P 46534 & SW/P 10220, both air-break switches flashed over to the switch frame, small ground fires resulted at the base of both these structures, approximately 4M X 4M in area of grass burnt in total. There were no reported injuries or 3rd party damage. Protection operated ( CHA3 & CHA6 feeder CB’s reclosed ).
1940 | Powercor 16/87 | Powercor | 24/12/2016 | 0.49931 | -35.8122 | 144.213 |  | 30028343 | CHA006 | 22kV AC | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 12657 | 20161229PWA_01 | Powercor fault crew reported ground fire(s) associated with lightning strike to 22kV overhead conductors at the incident location. On arrival the crew found that lightning had struck overhead conductors between SW/P 46534 & SW/P 10220, both air-break switches flashed over to the switch frame, small ground fires resulted at the base of both these structures, approximately 4M X 4M in area of grass burnt in total. There were no reported injuries or 3rd party damage. Protection operated ( CHA3 & CHA6 feeder CB’s reclosed ).
1941 | Powercor 16/88 | Powercor | 25/12/2016 | 0.65694 | -38.1659 | 144.3135 |  | 32083825 | WPD013 | Low voltage AC (<1kV) | Rural Short | - overhead service conductor (residential) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 12665 | 20161229PWA_08 | VicFire advised of a wire down with Arcing and sparking. Attending crew found service cable had parted in span and supply end had been brushing against cable guard on pole, and had ignited a small ground fire. There was no injuries or third property damage. Fire area 1 sqm. Crew replaced service.
1942 | Powercor 16/89 | Powercor | 25/12/2016 | 0.53472 | -37.5921 | 143.8656 |  | 32010016 | BAS013 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very High | 1 | 4.6 | 12663 | 20161229PWA_06 | A Powercor employee reported a pole fire at the incident location. On arrival the crew found that a three phase 22kV wooden cross arm had previously burnt through at a cross arm strap position and the cross arm was now broken. The pole is located in the road reserve and there was no ground fire. There were no injuries.
1943 | Powercor 16/90 | Powercor | 28/12/2016 | 0.55208 | -37.5639 | 143.8361 |  | 30014532 | BAS014 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 12666 | 20161229PWA_09 | VicFire reported a pole fire at the incident location. On arrival the crew found that a tree branch had broken in the windy weather conditions and had fallen across high voltage and low voltage conductors which resulted in the branch burning through. There was no ground fire. There were no injuries.
1944 | Powercor 16/91 | Powercor | 28/12/2016 | 0.35764 | -35.1664 | 141.7415 |  | 32139791 | OYN001 | 22kV AC | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | Very High | 1 | 1 | 12661 | 20161229PWA_04 | VicFire reported wire down and ground fire at the incident location. On arrival the crew found that a tree had fallen over in high winds from outside the clearance space onto 1 phase of the 3 phase 22kV line, breaking the insulator, dislodging the conductor which fell to the ground and commenced a ground fire. A ground fire of approximately 150M x 15M in area, roadside grass burnt. There were no reported injuries or 3rd party damage. Protection operated, Underbool P428 ACR tripped to lockout for the incident.
1945 | Powercor 16/92 | Powercor | 28/12/2016 | 0.27917 | -36.4022 | 141.6422 |  | 32122737 | NHL015 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very High | 1 | 1 | 12664 | 20161229PWA_07 | VicFire reported a pole fire at the incident location. On arrival the crew found that a three phase 22kV wooden cross arm had burnt through at the king bolt position and the cross arm with brown fog type insulators was broken in half. The pole is located in a fallow paddock and there was no ground fire. There were no injuries
1946 | Powercor 16/93 | Powercor | 29/12/2016 | 0.58125 | : -38.334039 | 144.3245 |  | 30292613 | WPD024 | Low voltage AC (<1kV) | Rural Short | Other | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 12704 | 20170111PWA_04 | customer reported a meter board fire at the incident location. Upon arrival, the Powercor crew found that an overheated meterboard fuse caught fire and melted. There were no injuries or ground fire.
1947 | Powercor 16/94 | Powercor | 29/12/2016 | 0.54931 | -36.5147 | 145.2038 |  | 32191788 | MNA021 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 12673 | 20161230PWA_05 | The customer at the incident location reported that a tree had fallen over the overhead line. It had started a small grass fire which self-extinguished. On arrival the crew found that at the incident location a tree had fallen across the conductors near P1 Dickenson Spur and bought them close to ground. A small ground fire was observed (Less than 1sq metre). No injury and only minor third party damage was reported.
1948 | Powercor 16/95 | Powercor | 30/12/2016 | 0.73819 | 38.2111 | 143.0397 |  | 30042574 | CDN006 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 12675 | 20170103PWA_01 | VicFire reported a junction box on building at dairy on fire at the incident location. On arrival the crew found a customer switchboard had caught fire above the meterboard and a ground fire at the pole servicing the property via an underground cable. The fuse at the pole had overheated and fallen from the box. The pole was located in the road reserve and there were scorch marks on the fence posts but no structural damage. Area of fire approx. 20m x 7m (140m²).
1949 | Powercor 16/96 | Powercor | 2017-01-01 | 0.70833 | -38.2903 | 144.3096 |  | 33042148 | WPD022 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 12676 | 20170103PWA_02 | Customer reported all supply fail at the incident location. On arrival the crew found an overheated fuse had melted through the box and fallen to the ground burning a small patch of grass. No injury or third party property damage.
1950 | Powercor 16/97 | Powercor | 2017-02-01 | 0.30139 | -37.5395 | 143.8266 |  | 30014161 | BAN001 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 12677 | 20170103PWA_03 | A call was received from the CFA that a pole was on fire outside 1253 Howitt Street Wendouree. On arrival the crew found that a Pole Fire had occurred on Lake Nth Howitt Pole 20. Leakage on the HV switch pole had caused damage to the pole where the LV X-arm attaches and burnt through the LV X-arm. The HV switch mounted on the pole was not earthed and it is assumed that leakage current from the HV tracked to the LV neutral conductor and then to earth. The crew isolated supply to the area and the pole and x-arm was replaced. The was no ground fire, third party damage or injury. Police and FCA attended the scene.
1951 | Powercor 16/98 | Powercor | 2017-04-01 | 0.90694 | -37.6883 | 144.4362 |  | 33075192 | BMH004 | Low voltage AC (<1kV) | Rural Short | Public lighting | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 12715 | 20170112PWA_06 | A passer-by reported that a street light lantern (150W HPS on an outreach bracket) at pole LIS-105857 (12.5m concrete pole) had caught fire resulting in the lantern cover melting and coming down to ground through the tree beneath the pole. The fault crew did not advise of the possible cause of the fire/damage to the lantern. The fault crew isolated supply to the light, and repairs will be undertaken by Powercor’s lighting contractor as a fault follow up. The MFB were in attendance, however they advised that any fire that may have started self-extinguished prior to their arrival on site. There was no ground fire, injuries or third party damage to report.
1952 | Powercor 16/99 | Powercor | 2017-05-01 | 0.70833 | -36.0899 | 144.6633 |  | 33104974 | ECA010 | 22kV AC | Rural Short | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 12714 | 20170112PWA_05 | Nearby resident reported that pole sparking and flaming. CFA was leaving as line crew arrived. Upon arrival crew found that an EDO fuse had candled on sub pole (LIS-924576) P1 DYBALL SPURLINE. There had been high levels of lightning on Christmas eve. There was no ground fire, injuries or third party property damage
1953 | Powercor 16/100 | Powercor | 2017-05-01 | 0.55486 | -36.3917 | 142.3915 |  | 32106745 | HSM005 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 12685 | 20170106PWA_02 | Customer reports of “no supply” were received beyond the incident location. On arrival the crew found that a farmer driving a tractor and towing a grain chaser bin with an auger which was not stowed had contacted an overhead high voltage line. There was a ground fire in private property covering an area of approximately 150 hectares. There is a burn mark on the auger and no other apparent damage to the grain chaser bin. There were no reported injuries.
1954 | Powercor 16/101 | Powercor | 2017-05-01 | 0.50139 | -35.9715 | 145.623 |  | 33085558 | CME015 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 12684 | 20170106PWA_01 | The CFA reported a pole had caused a grass fire at the incident location. On arrival the crew found that at the incident location a pole box had faulted resulting in approximately 4 acres of grassland being burnt. No injury and or other third party damage was reported. The pole box was replaced and supply returned to normal. The crew were concerned that this fuse assembly had already been replaced at this location and load may have been a factor in it faulting.
1955 | Powercor 16/102 | Powercor | 2017-07-01 | 0.81042 | -37.6747 | 144.5702 |  | 30103772 | MLN014 | Low voltage AC (<1kV) | Urban | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 12688 | 20170109PWA_02 | Angelique from Vic fire reported sparks fell from a pole at the incident location and started a small fire on nature strip, the fire extinguished by itself and she advised that Vic fire was enroute. Few customers reported no power on their properties. A Powercor crew attended and discovered that at pole LIS 110961 a LV conductor line bridge had burnt at a substation LV bus fuse termination. This caused the sparks and probably hot debris that fell to the ground starting a small ground fire on a couple of spots on the nature strip (approx.1m square), the fire extinguished by itself. The crew replaced the LV bridge conductor between the LV bus and the fuse termination. There were no reported injuries or third party damage. LV Bus Fuses operated (COBURNS RD P22 Pole substation).
1956 | Powercor 16/103 | Powercor | 2017-07-01 | 0.52708 | -38.0271 | 144.4229 |  | 33040304 | FNS012 | Low voltage AC (<1kV) | Rural Short | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 12696 | 20170110PWA_01 | The customer at the incident location reported that a conductor had faulted and fallen to ground. On arrival the crew found at the incident location, an LV conductor had faulted and showed signs of burning in small patches on the ground. No injury and no third party damage was reported. The Cause appears to be an overheated IPC connector at the ABC t/off
1957 | Powercor 16/104 | Powercor | 2017-07-01 | 0.52222 | -36.3245 | 144.9779 |  | 33092311 | KYM-ECA1 | 66kV AC | Unknown | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 12692 | 20170109PWA_06 | Control room noted a reclose on KYM-ECA No..1 66kV line. Control Room contacted Chris Tobias on call ZSO to perform patrol of KYM-ECA 1 66kV line. Chris advised that there had been a centre phase to earth flashover the cause of which seemed to be a bird (crow) as there were burnt feathers at the base of the pole. CFA had attended. The area affected was approximately 1100m² of burnt grass reserve. There were no reported injuries.
1958 | Powercor 16/105 | Powercor | 2017-10-01 | 0.78125 | -36.756 | 144.2606 |  | 33021007 | BET002 | 22kV AC | Rural Short | - dropper / bridge | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 12716 | 20170116PWA_01 | VICFIRE reported a grassfire at the incident location. Dispatch contacted NAO at 17:41hrs. Upon arrival the crew noted the CFA leaving the scene after extinguishing a small grass fire which burnt an area of approximately 150m² behind Clark Rubber and Spotlight in Ironbark. The area was both private property and road reserve. Police were also in attendance. Crew noted splash marks across one phase, D and dropper which may have resulted in a phase to earth fault on the line. FFU has been arranged by crew to replace damaged dropper. A suspected object being thrown over 22kV overhead conductors at the incident location was the cause of the fire. There were no reported injuries or 3rd party damage.
1959 | Powercor 16/106 | Powercor | 13/01/2017 | 0.62292 | -36.3111 | 143.974 |  | 33017867 | CHA006 | Low voltage AC (<1kV) | Rural Long | - overhead service conductor (other) | single phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 12717 | 20170116PWA_02 | Customer reported cables clashing and a small grass fire started at 6223 Loddon Valley Highway BEARS LAGOON. Crew attended and found small grass fire of approximately 10m X 5m was extinguished. Grey PVC Service cable leads insulation had failed had shorted out causing grass fire. Crew replaced leads and conducted testing and restored supply. No injuries or property damage reported.
1960 | Powercor 16/107 | Powercor | 15/01/2017 | 0.45556 | -38.2637 | 143.5561 |  | 30054319 | CLC003 | Low voltage AC (<1kV) | Rural Long | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 12722 | 20170117PWA_02 | A farmer reported that a small grassfire had started on his property. He stated that a nearby pole had been sparking, smoking and glowing orange. The farmer believed this pole was the likely cause of the fire. A crew was dispatched to investigate the incident. The attending crew found evidence of a small grass fire totalling approximately 2m² which had been extinguished by the farmer. An inspection of the transformer pole 3 (LIS-1605) identified a hot connection on a LV isolator. The line worker suggested that this may have caused the sparks and possible hot debris that fell to the ground. The customer’s supply was isolated and the site made safe until appropriate repairs were later completed. There was no third party damage or injuries reported.
1961 | Powercor 16/108 | Powercor | 15/01/2017 | 0.31181 | -37.9535 | 144.0935 |  | 31012957 | GL015 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 12721 | 20170117PWA_01 | System Controller reported that Lethbridge P179 ACR had operated with a nearby grassfire being attended to by CFA shortly after (identified on Vic Emergency website). A crew and operator was dispatched to investigate the cause. Attending crew found steel conductor had broken between P7 (LIS-45724) and P8 (LIS-45726) resulting in a small ground fire. The fire was approximately 10m² on road reserve. There was no third party damage or injuries reported.
1962 | Powercor 16/109 | Powercor | 16/01/2017 | 0.88472 | -38.0742 | 144.3952 |  | 30073835 | FNS032 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 12727 | 20170118PWA_01 | Attending crew found centre phase 19/3.25 AAC HV conductor had hit the ground between P52 (LIS-60484) and P53 (LIS- 44188), conductor had broken off at strain termination fitting. The broken termination was on the load side which meant the conductor on the ground was fed through the windings of the down-stream transformer/s, causing small spot fires/burns to the grass. The CFA and police were onsite. The burns total approximately 30m long and 100mm wide. After a closer look by the crew, it was identified by the crew that the PG clamp had become over heated, causing the conductor to melt and break. The site was made safe and appropriate repairs were made. There was no third party damage or injuries reported.
1963 | Powercor 16/110 | Powercor | 16/01/2017 | 0.55694 | -37.6164 | 143.8353 |  | 30001216 | BAS022 | Low voltage AC (<1kV) | Rural Long | - overhead service conductor (residential) | single phase | Started by any other thing forming part of or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 12723 | 20170117PWA_03 | Vic fire reported a grass fire at the base of a pole at the incident location. On arrival the crew found that an unknown vehicle had contacted the LV overhead service, causing it to scrape on a metal saddle and drop debris to the ground, resulting in a small grassfire of approx. 10m x 20m = 200m2 on the road reserve. There was no reported third party damage or any injuries. After restoration the service measured 7.0m above the road.
1964 | Powercor 16/111 | Powercor | 16/01/2017 | 0.325 | -36.9747 | 143.9596 |  | 33014297 | BETS-MRO | 66kV AC | Unknown | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very High | 1 | 4.6 | 12720 | 20170116PWA_06 | CFA reported a pole fire at the incident location. Upon arrival the crew found that a bird flashover on 66kV line and fell on to the ground resulting approx. 500 Sqm ground fire. The protection operated (line auto reclosed). There were no reported injuries or property damage.
1965 | Powercor 16/112 | Powercor | 19/01/2017 | 0.96319 | -38.3364 | 141.5164 |  | 32134228 | PLD006 | 12.7kV AC (SWER) | Rural Short | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by lightning striking a distribution system or a part of a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 12740 | 20170123PWA_03 | Customers reported a loss of supply and a wire down following a lightning strike at the incident location. A crew attended that night and found the SWER 3/2.75SC had broken and was on the ground between P8 and P10 Logan S/L. The HV fuse at Logan P1 had blown. The line was left off supply until the following morning. In daylight hours the crew found P9 had been struck by lightning. There was also a 2m/sq. patch of grass burnt at the base of P9. A burnt area of approx. 30m in length occurred between P8A and P9 where the SWER conductor had broken and fallen to ground. CFA attended and extinguished the fire. An insulator was replaced at P8 and P9 was replaced. At P10, the pole mounted TX had failed, dropping oil at the base of the pole. There was no run off of oil from site. The TX was replaced. The Environmental group to arrange a contractor to clean up oil spill from site. No shocks, injuries or third party damage. NOTE: Fire start and oil leak reported by crew directly to A/H NAO on 20.01.2017. A/H NAO passed details on to B/H NAO 20.01.2017 after returning to work from being on stand down.
1966 | Powercor 16/113 | Powercor | 19/01/2017 | 0.93125 | -38.2512 | 144.2482 |  | 32079759 | WPD014 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 12741 | 20170123PWA_04 | A customer reported a grass fire at the base of a pole at the incident location. On arrival the crew found that an LV fuse box overheated, causing it to drop debris to the ground, resulting in a small grassfire of approx. 15m x 3m = 45m2 on the road reserve and part private property. There was no reported third party damage or any injuries.
1967 | Powercor 16/114 | Powercor | 19/01/2017 | 0.73194 | • -36.403547 | 142.557 |  | 32109005 | HSM005 | 12.7kV AC (SWER) | Rural Long | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any other thing forming part of or coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 12735 | 20170120PWA_01 | A customer reported that a farm worker on his property had driven a tipper truck into overhead power lines and bought them down. On arrival the crew found that a tip truck had contacted the SWER conductor near Nullan-Owen Pole 18 and the SWER conductor between Pole 14 and Pole 20 Nullan-Owen Spur had been pulled down. The SWER ACR protecting the line operated for the fault. The truck sustained damage to its tyres as a result of the contact. A ground fire started as a result of the contact. Approx. 5-6 hectares of wheat stubble was burnt. CFA attended and extinguished the fire. There was no other damage, no injury and no shock. The line was isolated and the conductor was repaired.
1968 | Powercor 16/115 | Powercor | 19/01/2017 | 0.23194 | -37.5108 | 143.9456 |  | 30016329 | BAN008 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 12770 | 20170131PWA_03 | A customer reported no supply at the incident location. On arrival the crew found that an LV FOLCB overheated and caught fire on the substation pole out front of this address. There was no ground fire, no reported third party damage or any injuries. Note: As NAO I was informed of this incident after restoration, hence the lack of some information.
1969 | Powercor 16/116 | Powercor | 21/01/2017 | 0.10764 | -38.3724 | 141.5859 |  | 30240396 | PLD006 | 22kV AC | Rural Short | - fuse (any other type) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 12771 | 20170131PWA_04 | Fire Comms reported a pole fire at the incident location. On arrival the crew found that a HV fuse barrel had failed to operate correctly and had candled. There was no ground fire, no reported third party damage or any injuries.
1970 | Powercor 16/117 | Powercor | 22/01/2017 | 0.89236 | -36.4601 | 145.4082 |  | 32191546 | STN021 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 12778 | 20170201PWA_07 | Customer reported a fire on a pole at the incident location. On arrival the crew found that a LV FSD had failed due to suspected poor connection and caught on fire, molten plastic fell to the ground but no ground fire resulted. There were no reported injuries, no third party damage.
1971 | Powercor 16/118 | Powercor | 22/01/2017 | 0.070139 | -38.3985 | 143.8529 |  | 32065952 | WIN011 | 22kV AC | Rural Long | - fuse (any other type) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 12776 | 20170201PWA_05 | Fire Comms reported a pole fire at the incident location. On arrival the crew found that a HV fuse barrel had failed to operate correctly and had candled. There was no ground fire, no reported third party damage or any injuries.
1972 | Powercor 16/119 | Powercor | 23/01/2017 | 0.84722 | -36.7475 | 144.2563 |  | 30019838 | BET001 | Low voltage AC (<1kV) | Rural Long | - overhead service conductor (residential) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 12755 | 20170125PWA_03 | Customer reported a tree had brought down an LV service and had commenced a ground fire at the incident location. On arrival the crew found that a LV neutral screened service cable was brought down by a customer tree, resulting in the service breaking and igniting a small ground fire, 0.3m square in total burnt. The service remained alive on the ground until the Powercor fault crew arrived & isolated it. There were no reported injuries, no 3rd party damage, no protection operated. Local SES ( per Craig Guymer, PAL employee ) removed a branch from the same service some 2 weeks earlier, customer was previously advised to cut their tree as it is in poor health.
1973 | Powercor 16/120 | Powercor | 23/01/2017 | 0.74306 | -37.8793 | 144.6759 |  | 33071396 | WBE021 | Low voltage AC (<1kV) | Urban | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 12751 | 20170124PWA_04 | The MFB rang and advised they had extinguished a ground fire under our assets at the above address; also, there did not appear to be anything wrong with our assets. A neighbour subsequently rang to advise their security camera detected something “dripping” from our assets which caused the fire. On arrival fault crews found a low voltage copper to aluminium dee on the white phase had failed resulting in the ground fire and third party damage to a small bush. There was no loss of supply. No protection operated. There was no injury as a result of this incident.
1974 | Powercor 16/121 | Powercor | 23/01/2017 | 0.64028 | -38.1475 | 144.6044 |  | 30065422 | DDL021 | Low voltage AC (<1kV) | Rural Short | - overhead service conductor (other) | single phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 12786 | 20170127PWA_03 | CFA fire investigator requested assistance to determine cause of grass fire. No fault / outage reports had been received for a small grass fire that had occurred several days previously. Attending crew lowered service cable to private pole to assist fire investigation. Crew identified overheated connection in customers API box on private pole and remnants of cable tie where CFA had identified the location of grass fire ignition. Crew replaced service, reconnected and restored supply. There was no injuries or third property damage.
1975 | Powercor 16/122 | Powercor | 23/01/2017 | 0.62153 | -37.68 | 144.3797 |  | 30102859 | BMH003 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 12795 | 20170207PWA_01 | Pole Fire - crossarm broken resulting in 40 SQ m ground fire. Details unknown - NAO not notified
1976 | Powercor 16/123 | Powercor | 23/01/2017 | 0.55903 | -37.6531 | 144.315 |  | 30116684 | BMH003 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 12754 | 20170125PWA_02 | CFA reported a pole fire at the above location. A crew attended and found both the HV earths on the wooden SWER S/S pole had been removed. The resulting current leakage cause a pole fire. The embers from the pole fire started a grass fire at the base of the pole. CFA attended and extinguished a fire of approx. 100m x 50m in private paddock and road reserve. After the fire was extinguished, the crew replaced the missing HV earths and restored supply. The crew listed a FFU to have the pole inspected. Police have been notified and a safety link report submitted. No shocks, injuries or third party damage.
1977 | Powercor 16/124 | Powercor | 25/01/2017 | 0.78056 | -37.9409 | 144.0958 |  | 30249584 | GL015 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 12783 | 20170127PWA_01 | Powercor received of a wire down and possible ground fire. On arrival the crew found both phases of the HV overhead line had broken and fallen to ground. A grass fire of some 150 x 300m occurred on roadside and private farm land. No fencing or other 3rd party property damage was reported damaged. Initially the crews were unsure as to the cause for the broken conductor. After the fire was extinguished, further investigation found evidence of a swan carcass in the area. This was attributed as being the cause of the initial outage and damage to the HV conductors. There was no injuries or other third party property damage reported.
1978 | Powercor 16/125 | Powercor | 26/01/2017 | 0.73194 | -36.756 | 144.2606 |  | 33021007 | BET002 | 22kV AC | Rural Short | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 12785 | 20170116PWA_01 | CFA reported a grass fire caused by Powercor assets at the incident location. Fault crew had just attended bird flashover @ Wood street when this report was received, after investigation crew found evidence of arcing on a PG clamp at P46 Happy Valley believed to have a high impedance connection which arced when it was subjected to fault current associated with the wood street event, this location being on the same feeder between the terminal station and the fault location. It is believed molten material from the PG fell to the ground igniting an area of grass at the base of the pole, approximately 50M square was burnt. There were no reported injuries, no 3rd party damage, BET002 feeder successfully reclosed.
1979 | Powercor 16/126 | Powercor | 26/01/2017 | 0.71944 | -36.7398 | 144.2665 |  | 30031270 | BET002 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 12784 | 20170127PWA_02 | CFA reported a grass fire caused by Powercor assets at the incident location. On arrival the crew found that a bird had made contact with the surge diverter on HV cable head structure. The bird apparently fell to the ground and ignited a small area of grass at the base of the pole, approximately 1M square was burnt. The resulting fault current appears to have ruptured a connection in Susan street Ironbark leading to a second fire of some 50 sq. metres. There were no reported injuries or 3rd party damage.
1980 | Powercor 16/127 | Powercor | 26/01/2017 | 0.45486 | -34.7798 | 142.6405 |  | 32141451 | WMN013 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 12787 | 20170202PWA_02 | Customer reported a low wire at the incident location. On arrival the crew found that a wood cross-arm had burnt through at the insulator pin causing the conductor to come adrift and hang approximately 4.0M above ground at the lowest point. There was no ground fire, no reported injuries, no 3rd party damage, no protection operated.
1981 | Powercor 16/128 | Powercor | 27/01/2017 | 0.94375 | -35.4842 | 143.661 |  | 31021765 | SHL005 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 12762 | 20170130PWA_02 | CFA reported a grass fire caused by Powercor assets at the incident location. On arrival the crew found that a swan had struck HV 3 phase steel conductors between pole 21 & pole 22 of the Tresco spur line, the swan fell to the ground and ignited an area of grass, approximately 50M x 40M was burnt. There were no reported injuries, no 3rd party damage, 1 x 40A fuse operated @ Tresco P2.
1982 | Powercor 16/129 | Powercor | 27/01/2017 | 0.58472 | -36.8204 | 144.2441 |  | 30235097 | BET004 | 22kV AC | Rural Short | - pole (wood) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 12765 | 20170130PWA_04 | A Bobcat operator reported that his machine has hit a pole and smoke coming from the pole at the incident location. Upon arrival, the Powercor crew found that the Bobcat made contact with CHP and the impact cause to damage the steel cable protection, UG cable and fire damage to the pole. The protection operated. There were no injuries or ground fire. The protection operated.
1983 | Powercor 16/130 | Powercor | 27/01/2017 | 0.26875 | -36.5079 | 145.3106 |  | 33095056 | MNA034 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 12798 | 20170210PWA_01 | CFA reported a pole fire at the above location. A crew attended and found a LV U/G pole box had overheated and melted. Crew advise they had found a birds nest in the box. CFA attended. There was no ground fire start. Crew isolated supply and replaced LV U/G pole box. No shocks, injuries, ground fire start or third party damage.
1984 | Powercor 16/131 | Powercor | 28/01/2017 | 0.60764 | -37.6745 | 143.5252 |  | 33005605 | BAS021 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 12767 | 20170130PWA_05 | VicFire reported a fire at the incident location. On arrival the crew found that an EDO fuse had operated, however the barrel of the EDO fuse stayed in position without dropping down. The barrel then caught fire resulting in a ground fire (approx. 50 square metres) on the road reserve an private property. There was also minor damage caused to fencing and a private motor car parked on the property. Tere were no injuries.
1985 | Powercor 16/132 | Powercor | 29/01/2017 | 0.49792 | -38.2691 | 141.6738 |  | 30148494 | PLD001 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very High | 1 | 1 | 12763 | 20170130PWA_03 | At 11:57am the PLD001, TYRENDARRA P493R ACR tripped to lockout, interrupting supply to 521 accounts. Shortly after, Powercor received a call from Vic Fire advising of a fire at the base of a pole in Snapper Point Rd. When LSA crews arrived they found a failed conductor (3/12 steel) at HVCHP P6, Snapper Point Rd and CFA crews in attendance. The fire burnt an area of approx. 100m x 10m along the road reserve and entered into an adjoining Abalone Farm – causing minor damage to a shade cloth structure and possibly perimeter fencing before being extinguished by the CFA. Attending linesman Ben Cumming advised it appeared the conductor had failed due to corrosion. The incident location is within 200m of the coastline. No injuries were reported.
1986 | Powercor 16/133 | Powercor | 31/01/2017 | 0.575 | -36.3331 | 141.644 |  | 30077836 | NHL016 | Low voltage AC (<1kV) | Rural Long | - underground service cable (residential) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 12772 | 20170201PWA_02 | Vic Fire reported a service down and a ground fire at the incident location. On arrival the crew found that an LV neutral screen service had broken away from the roller at the POA, falling to the ground alive. The sparking service ignited some straw mulch in a garden bed resulting in a ground fire of approx. 10m x 2m = 20m2 on private property. There was no other reported third party damage or any injuries.
1987 | Powercor 16/134 | Powercor | 2017-03-02 | 0.83889 | -37.3039 | 142.7668 |  | 32090686 | ART033 | 22kV AC | Rural Long | - underground service cable (residential) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 12791 | 20170201PWA_02 | The CFA reported a pole fire at the incident location. On arrival the crew found that the HV dropper connected to the HV bushing had failed which caused arching at the joint resulting with sparks falling to the ground causing a small ground fire. The crew put parallels in place to isolate the faulty transformer and have marked the transformer to be replaced. There was a ground fire of approximately 15 metres x 5 metres in size. No protection operated. No reported shocks or injuries.
1988 | Powercor 16/135 | Powercor | 2017-04-02 | 0.46736 | -36.5327 | 144.6654 |  | 33079146 | KYM001 | 12.7kV AC (SWER) | Rural Long | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any other thing forming part of or coming into contact with a distribution system | HBRA only | 1 | Very High | 1 | 1 | 12794 | 20170206PWA_06 | Susan Jordan VIC Fire reported pole down Nhill Road near the corner of McKenzies Road RUNNYMEDE. Crew attended and speaking with attending Police were informed that a local farming contractor was shifting large hay bales and made contact with the HV conductor between pole # 1 Nhill Spur and pole # 2 Nhill Spur causing the cable to fail. As result of the shock load tee off pole # 14 Runnymede Spur failed at ground level [limited life pole]. A stubble fire started and burnt an estimated 10 acres [150m wide by 550-600 metres long]. Tee off pole # 14 Runnymede required replacement and approximately 250 metres of cable replaced from pole # 1 Nhill Spur. Ground fire attended by CFA. No property damage reported no shock or personal injury reported.
1989 | Powercor 16/136 | Powercor | 2017-05-02 | 0.48611 | -37.7945 | 144.8251 |  | 32178417 | SSE014 | Low voltage AC (<1kV) | Urban | - overhead service conductor (residential) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 12789 | 20170206PWA_01 | Ms Jillian Powell reported a service down and a ground fire at the incident location. On arrival the crew found the service cable had broken at he house end roller clamp, falling to the ground alive. The sparking service ignited some grass area in the garden resulting in a ground fire of approx. 1m x 1m on private property. There was no other reported third party damage or any injuries. Crew replaced service cable.
1990 | Powercor 16/137 | Powercor | 2017-06-02 | 0.30139 | -35.5205 | 143.0072 |  | 32156368 | CTN003 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 12972 | 20170405PWA_01 | Burnt pole top boigbeat east pole 39 recut poletop and new insulator fitted.
1991 | Powercor 16/138 | Powercor | 2017-11-02 | 0.41806 | -38.5326 | 142.7747 |  | 30136052 | WBL012 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 12800 | 20170213PWA_01 | Customer reported small ground fire at the incident location. On arrival the crew found a fuse box had caught fire and melted which started a ground fire burning a small patch of grass in road reserve. Extinguished by customer (volunteer firefighter). Area of fire approx. 4m². There was no injuries or third party property damage.
1992 | Powercor 16/139 | Powercor | 16/02/2017 | 0.83264 | -37.576 | 144.1845 |  | 30104525 | BAN011 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 12844 | 20170228PWA_01 | CFA reported a pole fire at the above address. A crew attended and found that a possum had bridged out between the top of an EDO fuse unit and the steel Xarm on the pole. The resulting current flow caused the pole to burn at the Xarm king bolt. The crew removed the possum and isolated the EDO fuses. The CFA were in attendance and extinguished the pole fire. The pole was replaced and supply restored. There were no shocks, injuries, ground fire start or third party damage.
1993 | Powercor 16/140 | Powercor | 16/02/2017 | 0.074306 | -37.9322 | 142.4948 |  | 30042625 | TRG002 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 12973 | 20170405PWA_02 | Pole fire reported at Pole 261 Penshurst spur Line. Crossarm burnt through at insulator.
1994 | Powercor 16/141 | Powercor | 17/02/2017 | 0.64167 | 37.8273 | 144.7788 |  | 33074084 | LVN024 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 12827 | 20170221PWA_01 | During feeder patrol following a truck collision reported in incident 12826 a grass fire occurred at the base of a hv switch at the incident location. The contacts of the switch appear to be welded shut. There were no injuries reported.
1995 | Powercor 16/142 | Powercor | 17/02/2017 | 0.64167 | -37.8273 | 144.7788 |  | 33074084 | LVN024 | 22kV AC | Urban | - switch (disconnector/isolator) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 12826 | 20170221PWA_02 | The MFB reported that a truck had hit wires at corner of Australis drive and Robinsons road and started a fire at the incident location. Truck and grass on fire. MFB was on site. On arrival the fault crew found a truck had collided with a 66KV/22KV INT pole LIS 839192 at 354a Robinsons Road (west side of road) near intersection with Australis drive, Derrimut. The wood pole broke nearly at ground level and fell on the ground causing a grass fire approximately 200m x 50m. Crossarm assemblies on both adjacent poles were damaged. The crew said that when they arrive MFB and police were on site. The fire brigade had extinguished the fire and that the truck was being towed away. The crew said that the 66KVO/H line was not in service at that time. Protection operated, LVN24 22kv feeder CB opened to lockout.
1996 | Powercor 16/143 | Powercor | 22/02/2017 | 0.54444 | -37.8487 | 141.8367 |  | 32127314 | HTN002 | 12.7kV AC (SWER) | Rural Long | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Severe | 2 | 9.2 | 12832 | 20170223PWA_03 | VicFire reported a wire down and fire start at the incident location. The Portland Rd P2 SWER ACR tripped to lock out at the same time. A crew attended and found a pine tree adjacent to P16 Portland Rd S/L had fallen and contacted the line. The tie at P16 broke and the conductor came to ground. The conductor did not break. This resulted in a ground fire start of approx. 10m x 150m in the plantation easement. No plantation trees were damaged. The CFA attended and extinguished the fire. The crew replaced the PTA and tie on P16 and retied the conductor at P15 Portland S/L. There were no shocks, injuries or third party damage.
1997 | Powercor 16/144 | Powercor | 27/02/2017 | 0.84167 | -37.8449 | 144.7278 |  | 30238362 | LV002 | 22kV AC | Rural Short | - surge diverter | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 12893 | 20170320PWA_02 | Customer reported a loud bang in his street and what looked like a burnt insulator at the base of a pole. Powercor fault crew leader Terry Burton was directed to check the incident as part of a line patrol for a feeder outage on a separate feeder. (LV 003 feeder trip at 20:10hrs on 27.2.17). The Powercor crew attended the site and noted a damaged surge diverter and a small burnt patch on the nature strip beneath a HV cable head outside No 89 Marquands Rd, Truganina. The burnt patch measured approx. 400mm x 400mm. The surge diverter damage is suspected to have occurred as a secondary incident pursuant to reclose events after the original LV 003 feeder trip. The Powercor crew made the site safe by replacing the cable head surge diverter. There were no reported injuries. There were no other reports of ground fire.
1998 | Powercor 16/145 | Powercor | 28/02/2017 | 0.875 | -35.8091 | 143.2529 |  | 33015899 | CTN003 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 12894 | 20170320PWA_03 | VicFire reported a fire on a pole at the incident location. On arrival the crew found that a LV FOLCB had failed due to suspected poor connection and caught on fire, molten plastic fell to the ground but no ground fire resulted. Fire self extinguished prior to CFA arriving. There were no reported injuries, no third party damage, no protection operated.
1999 | Powercor 16/146 | Powercor | 28/02/2017 | 0.85694 | -38.3549 | 141.6141 |  | 32135103 | PLD005 | 22kV AC | Urban | - overhead conductor (bare; copper) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 12848 | 20170302PWA_02 | A call was made to Powercor advising of a crane making contact with overhead High Voltage wires at the incident location. No contact details were provided. No injuries were reported. When crews arrived on site they found that an ISO Marshalling timber transporting crane had hit the 3 phase 22kV line between Pole 12 (LIS-997381) and Pole 13 (LIS-905402). The incident caused 2 phases of conductor to break and fall to the ground, and a flashover and small ground fire to occur. It appeared that the crane operator may have driven underneath the line with the boom still in the air. The crew reported that the excavator operator did not appear to be injured or receive any shock, however he appeared to be a bit shaken by the ordeal. He then left the incident site with ISO Marshalling colleagues. The attending crew replaced the 2 spans of the damaged 2 wires (7/.104Cu) with approximately 300m of 7/2.75Cu. As provided by the lineworker (Ben Cumming): “At approx. 2045 Tuesday 28 February an ISO Marshalling crane operator drove his vehicle into 3 phase 22kv conductors between pole 12 and pole 13 Cliff St spur on PLD005. The collision caused a flashover and two of the conductors to break and fall to the ground. There was no damage to any Powercor assets or to the surrounds of the incident. The conductors were repaired and sagged to a height of 10m at road crossing. (Same height as originally). The crane operator was uninjured and the machine did not sustain any damage.” I made a follow-up call to the Port of Portland (03 5525 0900) to confirm that the crane operator was OK. During the call, Terry Baily from the Port of Portland advised that they want to have the overhead line relocated to underground, I advised how to get this request moving. No injuries have been reported. Protection systems operated as expected.
2000 | Powercor 16/147 | Powercor | 2017-02-03 | 0.026389 | -38.3089 | 144.2674 |  | 32084185 | WPD014 | 22kV AC | Rural Short | - fuse (powder filled) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very High | 1 | 4.6 | 12853 | 20170302PWA_06 | Mike from CFA reported that a small grassfire had started around the base of a pole. He stated that a fuse had dropped down and started the fire. The CFA were onsite at the time of the report. Mike from CFA reported that a small grassfire had started around the base of a pole. He stated that a fuse had dropped down and started the fire. The CFA were onsite at the time of the report. The attending crew found evidence of a small grass fire around switch pole 3 (LIS-35392) SW21816. The fire, totalling approximately 40m²- 45m², had been extinguished by the CFA. The CFA had left the site when the attending crew arrived. The lineworker (David Pickering) found that 1 of the 3 powder filled fuses was most likely the cause of the fire. He suggested that the fuse had failed to operate correctly and had candled with hot debris falling to the ground. There was minor damage to a private boundary fence (420 Coombes Rd), however the fence appeared to remain intact (secure). Definitive cause is unknown, however with the high humidity (95%) and foggy conditions, the weather could have played a part in the incident. appropriate repairs were completed and the red phase fuse replaced. The site was deemed safe. There were no reported injuries. There were no reported injurie
2001 | Powercor 16/148 | Powercor | 2017-03-03 | 0.53681 | -37.5801 | 143.8771 |  | 32009382 | BAS013 | Low voltage AC (<1kV) | Rural Short | - overhead service conductor (other) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 12857 | 20170306PWA_04 | Customer called to advise wire down in driveway at the above location. A crew attended and found a N/S service cable to house had burnt off at roller clamp at house end resulting is the service cable breaking and falling to the ground. An area of approx. 1m/sq. was burnt on the lawn in the front yard. This was extinguished by the property owner. The crew isolated the broken service, replaced it with a new T.S.C and reconnected supply. There were no shocks, injuries or third party damage.
2002 | Powercor 16/149 | Powercor | 2017-03-03 | 0.36389 | -38.2143 | 141.7138 |  | 32135590 | PLD001 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 12854 | 20170303PWA_01 | VicFire reported a fire start at the incident location. A crew attended and found a pole fire had occurred at P16 Translator S/L. A fire had starts at the head of the pole, burning thru the pole at the king bolt. The cross arm released from the pole and the conductor came to ground. The conductor did not break. Protection operated. This resulted in a ground fire start of approx. 5m x 5m on private property. There was no third party damage. The CFA attended and extinguished the fire. The crew replaced the pole and supply was restored. There were no shocks, injuries or third party damage. Note: The original Wood HV cross arm, had been replaced in August 2013 with a Steel cross arm as a P2 maintenance item but all original brown insulators and disc where refitted.
2003 | Powercor 16/150 | Powercor | 2017-04-03 | 0.90903 | -36.0351 | 145.4042 |  | 33087082 | NKA006 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 12859 | 20170307PWA_02 | CFA reported grass fire at the above location. A crew attended and the operation of an EDO fuse had caused a grass fire approx. 200m x 30m in both road reserve and on customer grazing land. Crew isolated supply and replaced fuse. CFA were in attendance prior to crew arrival and extinguished fire. CFA had to cut customer’s fence to gain access to property. Customer’s fence-line was reported to be concrete posts and therefore no further damage was reported as having been sustained. No shock, no third party damage, no injuries were sustained.
2004 | Powercor 16/151 | Powercor | 2017-05-03 | 0.44097 | -38.2568 | 142.4412 |  | 32198619 | KRT012 | 22kV AC | Rural Long | - dropper / bridge | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 12895 | 20170320PWA_04 | The CFA reported a pole fire at the incident location. On arrival the crew found that the pole had burnt through under the king bolt, attached to the crossarm for the HV fuses. The pole was severely damaged and almost burnt through. This could have caused the pole top to come to ground, if it had burnt through. The pole fire was initially discovered by some horse riders. Fortunately the CFA were in the vicinity undertaking an exercise. No third party damage or injury was reported. The crew made the site safe, and replaced the pole.
2005 | Powercor 16/152 | Powercor | 2017-06-03 | 0.49306 | -36.6214 | 145.2194 |  | 32192135 | MNA034 | Low voltage AC (<1kV) | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 12968 | 20170323PWA_01 | Crew advised of a small fire resulting from clashing of Low voltage conductors during works. The white phase overhead conductor burnt through fell to the ground and a fire of less than 1 square metre was initiated. The crew extinguished the fire. Supply isolated for installation to complete repairs. There was no injuries
2006 | Powercor 16/153 | Powercor | 2017-07-03 | 0.87917 | -37.4523 | 142.969 |  | 33048290 | ART033 | 12.7kV AC (SWER) | Rural Long | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any other thing forming part of or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 12878 | 20170308PWA_08 | A farmer reported that a B-Double tip truck working on his property had hit the overhead power lines and bought them down. On arrival the crew found that a B-Double tip truck had contacted the SWER conductor between king Pole 35 and King Pole 36 and pulled the SWER conductor low. The SWER ACR protecting the line operated for the fault. The truck sustained damage to its tyres as a result of the contact. A ground fire started as a result of the contact. Approx. 200 (20x10) sq. metres of grass was burnt. There was no other damage, no injury and no shock. The line was isolated and the conductor was repaired.
2007 | Powercor 16/154 | Powercor | 2017-07-03 | 0.53333 | -37.5033 | 142.817 |  | 30151626 | ART033 | 12.7kV AC (SWER) | Rural Long | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any other thing forming part of or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 12879 | 20170308PWA_07 | CFA called to advise of a wire down and a fire start at the above location. On arrival the crew found a farmer had been building a large hay stack under a SWER O/H line. During construction of the stack, the loader contacted the SWER line resulting in the line breaking and falling onto the stack, starting a fire. Protection operated at P1 Gleeson S/L when a fuse blew. The CFA attended and extinguished the surrounding ground fire. Approx. 1000m/sq. of private grass land was burnt. Due to the location of the smouldering stack, the broken SWER line could not be re strung and 1 customer past the location will remain off supply until the CFA can arrange an excavator onsite today to disperse and extinguish the stack. The crew will then be able to re string the SWER conductor and restore supply to the last customer. CFA to notify Powercor when the stack has been extinguished. Work cover and ESV have been notified of the incident. There were no shocks, injuries or third party damage.
2008 | Powercor 16/155 | Powercor | 2017-08-03 | 0.54375 | -37.6578 | 143.9722 |  | 32002591 | BAS023 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 12880 | 20170309PWA_03 | CFA called to advise a tree had pulled down a wire and started a grass fire at the above location. On arrival the crew found a tree had contacted 1 phase of a single phase 22kV line and broke the conductor, resulting in the conductor falling to the ground and starting a grass fire on public property. The CFA attended and extinguished the ground fire. Approx. 500m/sq. of road reserve was burnt. Protection operated at Eureka P97A ACR. The crew removed the tree and repaired the conductor, restoring supply. There were no shocks, injuries or third party damage.
2009 | Powercor 16/156 | Powercor | 2017-08-03 | 0.0083333 | 38.3627 | 141.618 |  | 32139117 | PLD006 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 12917 | 20170321PWA_02 | The CFA reported a pole fire at the incident location. On arrival the crew found that the crossarm had caught fire at one of the outside HV insulators. No conductors came to ground hence, no protection activated for this incident. There was no ground fire. No third party damage or injury was reported. The crew made the site safe and replaced the crossarm.
2010 | Powercor 16/157 | Powercor | 2017-09-03 | 0.94861 | -37.8708 | 144.7009 |  | 30111186 | LV004 | Low voltage AC (<1kV) | Urban | - overhead service conductor (other) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 12882 | 20170314PWA_02 | VicFire phoned in to advise of a wire down at the premises, pole to house and a small grass fire at the incident location. Upon arrival the crew had found that the 2/C Twisted Grey PVC service cable from LV Pole LIS-209218-7728 to POA House No. 6 Sheahan Crescent, Hoppers Crossing 3029, had failed and snapped at the house end which caused the Live LV Service Cable to come to ground in the front yard. The resultant sparks from this caused a minor grass fire in the front yard of No. 6 Sheahan Crescent, Hoppers Crossing 3029, approx. 5m x 4m total area. The CFA were on site and the grass fire was extinguished. There was no reported injury or shocks as a result of this incident. The LV Service Cable was replaced.
2011 | Powercor 16/158 | Powercor | 2017-10-03 | 0.78958 | -34.6136 | 142.7503 |  | 33064684 | RVL004 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 12886 | 20170314PWA_06 | Report from REC that there was a cable down on the road verge and no supply in the area, cable reported to be broken between pole 11 and pole 12. Crew attended and found HV 3/2.75 Steel Cable had failed at cable sleeve with no apparent reason. A burn area on the ground of 3 Metres by 3 Metres was evident, No property damage and No injuries reported.
2012 | Powercor 16/159 | Powercor | 2017-12-03 | 0.34028 | -37.7731 | 144.8217 |  | 30113183 | SSE014 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 12884 | 20170314PWA_04 | A number of residents/customers in the Sunshine & St Albans Area phoned in to advise that they had no power. Upon arrival the PCA HV Operator, Ashley Magnus, had discovered that a HV X-arm Fire had occurred on HV Strain Pole LIS-25393-7728, St Albans Rd corner Gilmour Rd. The resultant HV X-arm fire had caused the outer BL side phase conductor and strain/bridging insulator’s to come away from the HV X-arm and fall onto the LV conductor’s below. Protection on 22kV Feeder SSE011 did not operate as it was supposed, this subsequently resulted in the loss of Bus No.1 at SSE Zone Sub, resulting in an outage to approximately 11,000 customers supplied from SSE011, SSE012, SSE013 & SSE014 22kV Feeders. Initial reports from the field crew suggested possible HVI, this was later confirmed by the LEI, Terry Long, who attended. The following damage occurred due to the HVI to a VicTrack Hut at the corner of St Albans Rd Gilmour Rd, (approx. 100m south of LIS-25393). Customer:- BAYSIDE TRAINS COROPORATION, ID 34024473 - Damaged LV Fused Mains Box, Damaged Customers Unmetered Mains Cable from LV Fused Mains Box to PCA Smart Meter, Damaged PCA Smart Meter. PCA Crew & LEI returned the following day to assist customers REC with repairs. There was no reported ground fire, injury or shocks as a result of this incident.
2013 | Powercor 16/160 | Powercor | 2017-12-03 | 0.19236 | -37.677 | 144.4322 |  | 31033069 | BMH004 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 12921 | 20170321PWA_03 | CFA called in to advise of a pole on fire cnr Clarinda St & Turner St, Bacchus Marsh, LIS-965846. Upon arrival the crew, had discovered that a HV X-arm had caught fire and burnt through at the HV X-arm Strap. Please Note:- The HV Conductors remained in place and connected to the HV Wood Strain X-arm/HV Insulators. There was no reported ground fire, third party damage, injury or shocks as a result of this incident. The crew made the site safe and replaced the HV X-arm.
2014 | Powercor 16/161 | Powercor | 14/03/2017 | 0.52639 | -38.3525 | 143.3519 |  | 32065090 | CLC006 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 12922 | 20170321PWA_04 | A customer reported that the pole out front of their house was on fire at the incident location. On arrival the crew found that a fuse box on the substation pole had overheated, resulting in the box catching fire and dropping melted plastic and debris to the ground. The debris landed on short green grass and there was no ground fire, no reported third party damage or any injuries.
2015 | Powercor 16/162 | Powercor | 14/03/2017 | 0.43264 | -36.0242 | 146.0006 |  | 30239162 | CME014 | Low voltage AC (<1kV) | Rural Short | - switch (disconnector/isolator) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 12923 | 20170321PWA_05 | The Police reported a pole fire at the incident location. On arrival the crew found that a tree had fallen across the line and the blue and white phase conductors had clashed. The clashing caused a flashover at the FSD, this in turn caused a small fire in the area of the FSD. The crew said there was no ground fire. No third party damage or injury was reported.
2016 | Powercor 16/163 | Powercor | 15/03/2017 | 0.58889 | -38.0149 | 143.2515 |  | 32055045 | CDN004 | 22kV AC | Rural Long | - pole (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very High | 1 | 4.6 | 12888 | 20170316PWA_02 | Vic Fire reported a ground fire at the incident location. On arrival the crew found that a large grassfire of approx. 8ha in size had ignited near Cable Head Pole 210 of the Lismore Line. There was a reclose of the P113 Lismore Line ACR at 2:01pm. Inspections of the CHP at P210 Lismore by the attending crew failed to identify a cause for the grassfire. The area burnt was a mixture of road reserve and private land, with damage caused to fences and approx. 15 hay bales.
2017 | Powercor 16/164 | Powercor | 2017-12-03 |  | -37.0495 | 144.1474 |  | 32044587 | CMN004 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by lightning striking a distribution system or a part of a distribution system | within electric line construction area | 19.8 | Very High | 1 | 19.8 | 12887 | 20170315PWA_01 | CFA reported cable on the ground grass smouldering corner of Castlemaine - Maldon and Muckleford - Walmer Roads. Crew attended and found HV conductor 3/2.75 Galvanised Steel Conductor had failed believed to be caused by lightning strike. An area of 8 Metres by 2 Metres was burnt on the road verge. HV fuse had operated and suspected back feed was the cause of the small fire. Crew Isolated supply and restored cable. No property damage and No injuries reported
2018 | Powercor 16/165 | Powercor | 16/03/2017 | 0.45903 | -34.3302 | 141.735 |  | 32144890 | RCT023 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started by any other thing forming part of or coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 12889 | 20170317PWA_01 | Vic Fire reported a tractor hit a pole and caused a ground fire. The crew attended and confirmed that a tractor (Driven by Anthony Rowe) had hit a pole and bought it and the conductors to ground. This caused a ground fire of approximately 5 meters X 40 meters. The site the was made safe. P6 was also considered to be in poor condition following the incident, so both P5 and P6 were changed, before restoring supply.
2019 | Powercor 16/166 | Powercor | 19/03/2017 | 0.68472 | -34.2705 | 142.172 |  | 32148440 | RCT021 | 22kV AC | Rural Short | Other | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 12925 | 20170321PWA_06 | Customer reported pole on fire at base of pole. On arrival, crew found 2 separate spot fires (5-10 square meters) at bottom of 2 pole substations within 200m of each other. Customer had extinguished the fire, no CFA attendance. One section fuse operated, there was no evidence of failed assets at either pole. There were no reported injuries, minor property damage.
2020 | Powercor 16/167 | Powercor | 20/03/2017 | 0.79931 | -36.7496 | 144.3211 |  | 31037843 | EHK021 | 22kV AC | Urban | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 12926 | 20170321PWA_01 | Vic Fire reported a pole exploded and started ground fire at corner Piper Lane and Piper Rd East Bendigo. On arrival the crew found one of the HV cable head joint terminations had failed and a fire occurred at the base of the pole approx. 25 sq. meters in area. The fire had gone through a mesh fence but no property damage evident. Crew performed switching and logged fault follow up to occur morning of 21/03/2017. ESV notified. No shock or injuries. VicFire reported a pole exploded and started ground fire at corner Piper Lane and Piper Rd East Bendigo. Vic Fire reported a pole exploded and started ground fire at corner Piper Lane and Piper Rd East Bendigo. On arrival the crew found one of the HV cable head joint terminations had failed and a fire occurred at the base of the pole approx. 25 sq. meters in area. The fire had gone through a mesh fence but no property damage evident. Crew performed switching and logged fault follow up to occur morning of 21/03/2017. ESV notified. No shock or injuries.
2021 | Powercor 16/168 | Powercor | 21/03/2017 | 0.64861 | -35.2004 | 141.2853 |  | 32152227 | OYN001 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started by lightning striking a distribution system or a part of a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 12927 | 20170322PWA_13 | CFA reported a pole fire at the incident location. Upon arrival, the fault crew found that a HV SWER pole was struck by lightning. This resulted in a ground fire of some 35 acres in salt bush. No injuries were reported. There were no reported injuries.
2022 | Powercor 16/169 | Powercor | 22/03/2017 | 0.034722 | -34.7859 | 142.6269 |  | 32139293 | WMN013 | 22kV AC | Rural Short | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 12967 | 20170403PWA_03 | CFA reported pole fire at 3493 Hattah-Robinvale Rd Liparoo. On arrival, crew found cross-arm had fire on the footpath side of it. Crew were unsure if the storm activity or asset failure had caused it although they suspected tracking likely to have occurred. Crew advised disc insulator had pulled through and re-drilled 100mm from the affected area. No injuries, no ground fire, no third party damage.
2023 | Powercor 16/170 | Powercor | 27/03/2017 | 0.45 | -38.4287 | 143.5789 |  | 33039891 | CLC006 | 22kV AC | Rural Long | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 12933 | 20170328PWA_06 | Vic Fire reported a ground fire at the incident location. On arrival the crew found that a grassfire of approx. 1,000m2 in size had ignited beneath the 22kV conductors near Pole 115 of the Gellibrand Line. There was a reclose of the CLC006 feeder CB recorded at approx. 10:42am. Inspections of the HV conductor in the area by the attending crew failed to identify a cause for the grassfire, however it was noted that strong winds were present, and several pieces of bark were scattered on the ground in the area. The area burnt was a mixture of road reserve and private land, with minor damage caused to fences and private trees. The crew were told by the CFA crews onsite that a CFA investigator was to attend the site. There was no other reported third party damage or any injuries.
2024 | Powercor 16/171 | Powercor | 27/03/2017 | 0.44653 | -36.7594 | 144.2665 |  | 32034497 | BET002 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 12971 | 20170404PWA_03 | Employee report of pole fire. HV xarm burnt off HV insulator sitting on LV crossarm. NO report of ground fire or injuries
2025 | Powercor 16/172 | Powercor | 30/03/2017 | 0.77639 | -35.5975 | 143.5422 |  | 32155539 | SHL005 | 12.7kV AC (SWER) | Rural Long | - crossarm (wood) | single wire earth return (SWER) | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 12960 | 20170331PWA_01 | Customer reported a grass fire caused by Powercor assets ( pole fallen over ) at the incident location. On arrival the crew found that a pole had failed and the SWER conductor made contact with the ground in an adjacent span, a ground fire ignited resulting in approximately 50m x 100m of stubble paddock being burnt. CFA attended & extinguished the fire. There were no reported injuries, no 3rd party damage, BA fuse at “Beauchamp West ISO” operated for the incident.
2026 | Powercor 16/173 | Powercor | 30/03/2017 | 0.041667 | -36.592 | 143.922 |  | 30017992 | EHK024 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 12965 | 20170403PWA_01 | VicFire advised a fire at the above address. Fire had been extinguished upon crew arrival. Upon arrival noted burning to the pole and 2 small patches of grass at the base of the pole. . Pole is limited life. Follow up has been raised with Bendigo CPL for replacement. There were no injuries, loss or damage to third party property.
2027 | Powercor 16/174 | Powercor | 2017-02-04 | 0.96319 | -37.846 | 144.6852 |  | PA0129419 | LV001 | 22kV AC | Rural Short | - transformer (kiosk mounted) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 12969 | 20170404PWA_01 | Observations from site attendances: 1) A 315kVA, Etel kiosk in a residential subdivision appears to have sustained a major fault. 2) A grass fire was initiated in reserve landscaping surrounding the Kiosk location. 3) The forces of the electrical fault have caused the kiosk to: a. Disturb the soil adjoining the Kiosk’s concrete plinth. b. Rupture and deform the transformer tank, tank lid, welds, tank bracing. c. Discharge oil from the transformer tank d. Deform and force open the Kiosk roof, doors, steel shell cross members e. Snap a HV fuse holder and project Bayonet HV fuses over the road and into residential property 4) There is indication of discolouration of HV insulation on the inner set, C phase, HV Pin bushing. 5) Per suggestion by Underground repair personnel attending during daylight hours on 3/4/17, this may be the fourth ETEL Kiosk substation to have faulted in a similar manner in recent times. 6) There appears to be no indication that customer numbers, and loading type have contributed to a substation overload issue prior to the incident. There were no reported injuries. There was no other reported damage.
2028 | Powercor 16/175 | Powercor | 2017-03-04 | 0.55764 | -37.7768 | 141.8724 |  | 30090621 | HTN002 | 22kV AC | Rural Long | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 12970 | 20170404PWA_02 | CFA called to report a tree down, wires sparking and a grass fire start. A crew attended and found that a tree had fallen onto a HV conductor between P130 and P131 Branxholme line resulting is a ground fire start. The tree burnt thru the conductor before the crew could isolate the line and the conductor came to ground. The ACR at Branxholme P30 then tripped to lock out. The attended CFA crews extinguished the ground fire start and once it was confirmed supply was isolated, also extinguished the burning tree. Once the fire was extinguished, the crew repaired the broken conductor and restored supply. The ground fire was approx. 10m x 30M in area on the road reserve. There were no shocks, injuries or 3rd party damage.
2029 | Powercor 16/176 | Powercor | 2017-03-04 | 0.49306 | -37.1774 | 141.5068 |  | 32101722 | CHM011 | 12.7kV AC (SWER) | Rural Long | - dropper / bridge | single wire earth return (SWER) | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 12994 | 20170411PWA_01 | A customer called to report the top of a pole at their premises was sparking and on fire. A crew attended and found the live line flex had broken off at the top EDO connection at SWER substation pole Thornlea 7, resulting is arcing and the top EDO cap melting/burning. The crew isolated supply and replace the burnt EDO cap and broken flex. CFA did not attended. There was no ground fire start. There were no shocks, injuries or fire start.
2030 | Powercor 16/177 | Powercor | 2017-05-04 | 0.068056 | -38.1811 | 144.5135 |  | 32076029 | DDL014 | 66kV AC | Rural Short | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 12981 | 20170406PWA_03 | Customers reported an outage and also a car impacting into a pole at Corryule Rd Curlewis. Upon arrival the crew found that the car hit the 22/66kV intermediate pole. The driver was taken to hospital with non-life threatening injuries. The broken pole was on the ground and also one end on the roof of car. High voltage injection occurred involving 66Kv, 22kV an aerial earth (connected to LV neutrals remote from site). A number of surge diverters, 22Kv fuses and transformers were damaged in other parts of the 22kV feeders and a small ground fire of some 10M square occurred during restoration.
2031 | Powercor 16/178 | Powercor | 2017-08-04 | 0.60694 | -37.1854 | 143.3913 |  | 33013577 | MRO008 | 22kV AC | Rural Long | - guy wire | three phase | Started by lightning striking a distribution system or a part of a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 13005 | 20170413PWA_03 | Customer reported a lightning strike and small grass fire around stay which was extinguished by heavy rain at the incident location. On arrival the crew found no asset or property damage, a ground fire had ignited resulting in approximately 1m x 1m of grass being burnt. There were no reported injuries, no 3rd party damage, no protection operated for the incident.
2032 | Powercor 16/179 | Powercor | 2017-08-04 | 0.56944 | -38.0957 | 143.6879 |  | 32062880 | CLC003 | 22kV AC | Rural Long | - fuse (any other type) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 13007 | 20170413PWA_04 | Customer reported Transformer appears to have flames coming out of top of it. On arrival crew crew found that HV fuse had candled. There was no evidence of ground fire, no reported injuries or third party property damage.
2033 | Powercor 16/180 | Powercor | 2017-09-04 | 0.93125 | -38.4023 | 144.1858 |  | 30065718 | WPD014 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13000 | 20170412PWA_05 | On Sunday evening, WPD014 tripped at the CB at the WBD Zone Substation. The Powercor control room notified the A/H Operator to investigate the cause. The operator patrolled and conducted some switching to isolated the problem, but could not locate the exact location/cause. A crew was dispatched to investigate early the following morning, a customer reported a leaning pole near the Anglesea River which lead the crew to the incident location. Upon arrival, the crew identified a 21/12 wood pole leaning approx. 45°. This was causing a span of 22kV conductor to be sagging into the Anglesea River. It was identified that the stay rod had rusted through and gave way. The site is now safe and all repairs have been made. A tree top was burnt where the conductor had made contact. There were no reported injuries or third party damage.
2034 | Powercor 16/181 | Powercor | 2017-09-04 | 0.82986 | -35.6281 | 143.7805 |  | 30235186 | KGT004 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very High | 1 | 1 | 13012 | 20170418PWA_02 | Customer reported wires down and pole fire at the incident location. On arrival the crew found a pole fire had caused a small ground fire resulting in approximately 2m x 3m of grass being burnt. There were no reported injuries, no 3rd party damage, for the incident.
2035 | Powercor 16/182 | Powercor | 2017-09-04 | 0.33194 | -35.1109 | 141.1987 |  | 32149124 | OYN001 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very High | 1 | 1 | 13013 | 20170418PWA_03 | Crew found the customer outage was the result of a burnt HV strain arm at the incident location. There were no reported injuries, no 3rd party damage or grass fire for the incident.
2036 | Powercor 16/183 | Powercor | 2017-10-04 | 0.28125 | -38.539 | 143.9741 |  | 30064045 | CLC005 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 12997 | 20170412PWA_02 | The Crew were dispatched to investigate a wires down and possible HVI incident in Grove Rd, Lorne. Attending crew found that a tree had fallen onto a span of 3-7/2.5 AAC HV conductor between Pole 488 (LIS-30400) and Pole 1 (LIS-29595). The HV then hit the ground and left small burn marks on the grass. The burns total approximately 2m long and 50mm wide. It is suspected that there was also a HVI with the HV making contact with the bare LV. The site was made safe and appropriate repairs were made. The LEI, Allan Garrett, tested all customer connections and confirmed no damage to customer property. Allan advised one customer was unable to be reconnected due to possible faulty CB, and believed this was not related to incident. There was no third party damage or injuries reported.
2037 | Powercor 16/184 | Powercor | 2017-11-04 | 0.26667 | -36.3777 | 145.4249 |  | 33089832 | STN024 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13021 | 20170418PWA_08 | Vic Fire reported a Pole Fire at the incident location. On arrival the crew found the FSD unit to be overloaded and burnt out. There were no reported injuries, no 3rd party damage, no ground fire for the incident.
2038 | Powercor 16/185 | Powercor | 2017-12-04 | 0.92986 | -36.333 | 145.4318 |  | 30305074 | STN024 | 22kV AC | Rural Long | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13014 | 20170418PWA_04 | CFA reported a grass fire at the incident location. The crew found a faulty HV bridge caused a small fire 10m x 1m along the drain at the incident location. There were no reported injuries, no 3rd party damage for the incident.
2039 | Powercor 16/186 | Powercor | 2017-12-04 | 0.64931 | -36.1899 | 144.7483 |  | 32184201 | ECA012 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 13011 | 20170418PWA_01 | CFA reported wires down and they were controlling a small grass fire at the incident location. The crew found a broken HV termination Xarm which caused a 150m x 100m grass fire in a re-vegetation area at the incident location. There were no reported injuries, no 3rd party damage for the incident.
2040 | Powercor 16/187 | Powercor | 2017-12-04 | 0.1 | -38.4048 | 144.1989 |  | 33042041 | WPD021 | 22kV AC | Rural Short | - transformer (pole mounted) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 13001 | 20170413PWA_01 | On Wednesday morning, the crew were conducting some switching for operations. When they closed Switch 20175 (Angsew Spur), the crew noticed an explosion in the distance. They drove to investigate. Upon arrival, the crew found that transformer, Treatment Works 14, had exploded and was on fire. The CFA extinguished the fire. The crew advised that oil had hit the ground and small ground fires had occurred. The property is a Barwon Water treatment plant and a representative was called to attend site at the time of the incident. The Powercor Environmental Group was made aware of the situation. Soil samples were taken and sent off for testing. Veolia was arranged to dispose of the contaminated soil. Barwon Water assets remained on supply during the repairs via a generator. Representatives were onsite throughout the day. The site is now safe and all repairs have been made. ESV was notified of the incident. There were no reported injuries or third party damage.
2041 | Powercor 16/188 | Powercor | 14/04/2017 | 0.52917 | -35.2241 | 143.4672 |  | 30276890 | SHL004 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13029 | 20170420PWA_03 | CFA reported that there had been a pole fire at the above-mentioned location. Upon arrival, the crew found that the fuse box had burnt at the 4m mark on the pole. Cause unknown. Crew removed old fuse box and replaced it with a new unit. The site is now safe and all repairs have been made. There were no reported injuries or third party damage.
2042 | Powercor 16/189 | Powercor | 15/04/2017 | 0.94444 | -38.3313 | 144.3209 |  | 30319569 | WPD032 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13022 | 20170419PWA_01 | The CFA reported a pole fire at the incident location. On arrival the crew found that a Low Voltage three phase pole box had faulted and caught fire. Talking to the crew there was no ground fire. No third party damage or injury was reported. The crew made the site safe, the pole box was replaced and supply was restored.
2043 | Powercor 16/190 | Powercor | 18/04/2017 | 0.675 | 37.8321 | 144.7995 |  | 31038884 | LVN022 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13024 | 20170419PWA_03 | During Transport an excavator has contacted the HV conductors at 25 Cyanamid st Laverton North. The conductors were slightly damaged and there were flashover marks on the boom. There were burnt HV connections and HV conductors on the ground outside 85 Cherry Lane. At 73 Cherry lane there was evidence of HVI and a ground fire of 3.5 square metres. There were a number of street lights damaged along Cherry Lane. The Protection operated as expected. There were no reported injuries.
2044 | Powercor 16/191 | Powercor | 18/04/2017 | 0.29236 | -37.8058 | 144.8317 |  | 33105773 | SSE033 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13018 | 20170418PWA_06 | A customer reported a pole fire at the incident location. Upon arrival, the Powercor crew found that an overheated termination ignited the Krone box on concrete pole. There were no injuries, third party damages or ground fire. The repairs arranged.
2045 | Powercor 16/192 | Powercor | 19/04/2017 | 0.30486 | -38.3707 | 142.4633 |  | 30137969 | WBL006 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 13033 | 20170420PWA_04 | VicFire reported a pole smouldering and a wire hanging low. A crew attended and found that a wooden Tee off cross arm on P44 Warrnambool West S/L had burnt thru at the bridging insulator and was hanging from the bridging conductor. The crew isolated the 22kV conductors and replaced Tee off cross arm and all insulators with new units. There was no ground fire start. Local CFA was in attendance. There were no shocks, injuries or 3rd party damage.
2046 | Powercor 16/193 | Powercor | 20/04/2017 | 0.77222 | -35.5996 | 143.9347 |  | 32030269 | KGT003 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 13046 | 20170427PWA_03 | CFA reported Pole Fire APPROX 600-700 metres SOUTH of intersection of Kerang - Murrabit Road and Guilmartin Road Capels Crossing. Crew attended and assessed the partially burnt HV intermediate crossarm where the insulator pin had fallen through, crew assessed the integrity of the crossarm and reported as a fault follow-up. No ground fire, no property damage, no reported injuries.
2047 | Powercor 16/194 | Powercor | 20/04/2017 | 0.77153 | -37.6898 | 144.4421 |  | 30115961 | BMH006 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 13048 | 20170427PWA_05 | VicFire called in to advise of a wire on fire & brigade en-route. A resident Mrs Kerry Fay also called in to advise of a small box on pole outside property has caught fire, CFA have attended and fire now out, customer has no supply. On arrival the crew had discovered that a Single-Phase FOLCB and approximately 1m of 16mm LV UG Service Cable running down the pole had overheated and burnt out at LV Inter Pole LIS-103032. There was an outage to 3 x LV customers as a result of the Blue-Phase LV Fused Isolator at the Sub Pole Nordic 7 operating. There was no reported ground fire, third party damage, injury or shocks as a result of this incident. The crew made the site safe and replaced the FOLCB and the affected 16mm LV UG Service Cable.
2048 | Powercor 16/195 | Powercor | 20/04/2017 | 0.74861 | -35.9131 | 143.2266 |  | 32024287 | CTN003 | 22kV AC | Rural Long | - crossarm (wood) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 13042 | 20170426PWA_04 | CFA reported Pole Fire on the Calder Highway between the towns of Demosa and Nullawil. Crew attended and opened off ACR for isolation and replaced HV intermediate crossarm. No ground fire, no property damage, no reported injuries.
2049 | Powercor 16/196 | Powercor | 20/04/2017 | 0.57153 | -34.1991 | 142.1652 |  | 32150522 | MDA031 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13041 | 20170426PWA_03 | A passer-by informed that a loud bang, sparking and smoking at the incident location. On arrival the crew found that a Pole Fire had occurred on 12 X ETIW-SMATEO 1 (LIS 10044 strain pole). The crew made the place safe and repairs done. There was no ground fire or injury. CFA attended. Note: At the time of the incident no HVI found. After power restoration, a customer informed some damages to his installation. An inspector attended but no HVI found at the time. He will inspect the customer’s installation again.
2050 | Powercor 16/197 | Powercor | 21/04/2017 | 0.50556 | -36.2625 | 142.3932 |  | 32097104 | HSM005 | Low voltage AC (<1kV) | Rural Long | - overhead service conductor (residential) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13039 | 20170421PWA_03 | A customer reported a wire to the house had broken and burn marks on ground where it landed. A crew attended and found a NS service to the premises had burnt off at the roller clamp at the house end and the service had fallen to the ground, resulting is a ground fire start of approx. 100mm/sq. No CFA attended. The crew replaced the broken service with a new service. There were no shocks, injuries or 3rd party damage.
2051 | Powercor 16/198 | Powercor | 21/04/2017 | 0.42778 | -38.69673949, | 143.4246 |  | 33039339 | CLC006 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 13049 | 20170427PWA_06 | Customer reported a transformer on fire at the incident location. On arrival the crew found that a HV EDO fuse had operated on a transformer pole, however the barrel of the EDO fuse stayed in position without dropping down. The barrel then caught fire. There was no injuries, ground fire or third party property damage reported. The fault caused the CLC006 - Hordern Vale P5 ACR to also trip to Lock Out at 10:16 PM, interrupting supply to 137 accounts. The faulty transformer was disconnected and left off supply overnight. Replacement to be arranged the following day. All other interrupted supply accounts were restored. The previous day the same transformer had been struck by Lighting - refer OMS 984970. Attending crews feel the incidents are related.
2052 | Powercor 16/199 | Powercor | 21/04/2017 | 0.34306 | -37.6686 | 144.4451 |  | 30112526 | BMH005 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 13047 | 20170427PWA_04 | Vic fire reported a pole fire at the incident location. On arrival the fault crew found that a junction box had overheated and caught fire at the incident location. The crew replaced the burnt out connection box. There was no ground fire and no injury as a result of this incident.
2053 | Powercor 16/200 | Powercor | 2017-03-05 | 0.29931 | -38.255 | 143.6122 |  | 32061990 | CLC003 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 13068 | 20170504PWA_01 | REC reports a line had fallen and resulted in a fire start. CFA in attendance. A crew attended and found 1ph on a 3ph HV line had broken and fallen on to a tree below, causing the tree to smoulder. There was no ground fire start. The crew isolated the line and repaired the conductor before supply was restored. There were no shocks, injuries, third party damage or ground fire start. Note: There is a project to re conductor this line this year after 4 breakages of the HV conductors on this line in last 18mths.
2054 | Powercor 16/201 | Powercor | 2017-07-05 | 0.79931 | -37.52496632, | 143.7415 |  | 30004238 | BAS011 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 13084 | 20170509PWA_01 | VicFire reported a sparking pole top at the incident location. On arrival the crew found a 22kV candled EDO fuse on the footpath side of the high voltage switch on ARWHITE P1. There was no ground fire. There were no injuries.
2055 | Powercor 16/202 | Powercor | 2017-07-05 | 0.83194 | -36.4567 | 145.4978 |  | 30329181 | STN011 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 13137 | 20170605PWA_01 | Customers advised fuses down and dim lights. On arrival the crew found a bird clashed the conductors, one conductor on ground and second frayed right in middle of bay, grass fire limited to small spots where conductor was laying on ground, made safe, repaired. There were no reported injuries, no property damage for the incident.
2056 | Powercor 16/203 | Powercor | 2017-10-05 | 0.98472 | -34.2034 | 142.1409 |  | 32141697 | MDA033 | Low voltage AC (<1kV) | Urban | - fuse (any other type) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 13135 | 20170601PWA_06 | CFA reported switch board fire, at the incident location. On arrival the crew found meter board had been fire damaged as the result of a fuse base failure, made safe, repaired. There were no reported injuries and no protection operated for the incident.
2057 | Powercor 16/204 | Powercor | 2017-12-05 | 0.28264 | -38.3137 | 141.5297 |  | 32128364 | PLD003 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 13104 | 20170515PWA_01 | At 06:47hrs today, the customer reports no supply to premises. The smart meter shows a power outage at 01:25hrs this morning. A crew attended and found the fuse box on the substation pole had overheat and started a pole fire. The box, LV leads and LV earth on the pole were damaged. The pole is still serviceable. The crew replaced the damaged items and restored supply. There were no reported shocks, injuries, third party damage or ground fire start.
2058 | Powercor 16/205 | Powercor | 23/05/2017 | 0.49861 | -37.5948 | 144.4634 |  | 32167656 | BMH006 | 22kV AC | Rural Long | - overhead conductor (bare; steel) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 13111 | 20170524PWA_01 | Emergency Services reported a cable on the ground and sparking at the incident location. Upon arrival, the crew found that a HV conductor down and the live cable caused a small ground fire. The crew believed a vehicle brought down the cable but no vehicle details or witnesses available. There were no reported injuries.
2059 | Powercor 16/206 | Powercor | 2017-01-06 | 0.375 | -38.3962 | 142.6917 |  | 32194437 | WBL002 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 13131 | 20170601PWA_01 | CFA reports a transformer fire at the above address. A crew attended and found a fuse box on a service pole had overheated and melted. The resulting falling debris started a grass fire at the base of the pole of approx. 1m/Sq. CFA attended and extinguished fire. The crew replaced the melted fuse box and restores supply. The box feeds a local shire works depot and a church. There were no reported shocks, injuries or third party damage.
2060 | Powercor 16/207 | Powercor | 2017-02-06 | 0.35694 | -38.5846 | 143.1667 |  | 33035862 | COB011 | Low voltage AC (<1kV) | Rural Long | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 13136 | 20170602PWA_01 | Customer reports fire at junction box on pole. A crew attended and found a fuse box on a substation pole had overheated and caught fire. The resulting falling debris started a grass fire at the base of the pole of approx. 5m/Sq. Customer extinguished grass fire. The crew replaced the melted fuse box and restores supply. There were no reported shocks, injuries or third party damage.
2061 | Powercor 16/208 | Powercor | 2017-04-06 | 0.34722 | -37.0844 | 144.3138 |  | 33026659 | CMN001 | 22kV AC | Rural Long | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 13173 | 20170621PWA_01 | Customer reported all supply fail. On arrival, crew found evidence of candled fuse. Crew advised EDO was held up and had appeared to have candled. Only thing left was the bottom of the unit. Crew isolated and repaired. They advised that there was no fire or smouldering on ground (heavy frost). No injuries, no ground fire, no third party damage.
2062 | Powercor 16/209 | Powercor | 2017-05-06 | 0.50208 | -36.1858 | 141.7931 |  | 32104727 | NHL015 | 12.7kV AC (SWER) | Rural Long | - pole (wood) | single wire earth return (SWER) | Started by any other thing forming part of or coming into contact with a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 13172 | 20170606PWA_01 | A customer reported no supply at the incident location. On arrival the crew found that a tractor had struck a SWER intermediate pole in a paddock while plowing, knocking the pole over. The SWER conductor contacted the ground resulting in a grassfire of approx. 15m x 20m= 300m2 in a stubble paddock. Protection operated. There was no other reported third party damage or injuries. Crew attended and replaced pole
2063 | Powercor 16/210 | Powercor | 17/06/2017 | 0.72708 | -38.4281 | 144.1734 |  | 32079086 | WPD021 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 13184 | 20170627PWA_04 | CFA reported that a pole mounted fuse box was on fire at the incident location. On arrival the crew found that the fuse box had been on fire and insulation melted away. Melted plastic and debris fell to the ground but did not start a fire due to moisture, no reported third party damage or any injuries.
2064 | Powercor 16/211 | Powercor | 20/06/2017 | 0.37639 | -36.7732 | 144.2486 |  | 31004007 | BET002 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 13221 | 20170713PWA_06 | The CFA reported a pole fire at the incident location. On arrival the crew found that a Low Voltage three phase pole box had faulted and caught fire. Talking to the crew there was no ground fire. No third party damage or injury was reported. The crew made the site safe, the pole box was replaced and supply was restored.
2065 | Jamena 16/17 | Jamena | 19/08/2016 | 0.17361 | -37.8152 | 144.8329 |  | A089155 | TH22 | 22kV AC | Urban | - pole (wood) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 137123 | 20160819JEM_02 | Airborne debris caused the pole to catch fire. Pole subsequently replaced.
2066 | Jamena 16/18 | Jamena | 23/08/2016 | 0.89028 | -37.7401 | 145.0443 |  | A107676 | NH5 | Low voltage AC (<1kV) | Urban | - fuse (any other type) | single phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 137293 | 20160824JEM_01 | Investigations found that the incoming service active conductor had over heated and caught fire causing localised damage to the customer's two point connection box and weather boards. The fire appeared to be the result of a loose connection in the mains box on the incoming service active.
2067 | Jamena 16/19 | Jamena | 26/10/2016 | 0.56597 | -37.7045 | 144.9401 |  | A045338 | PV23 | 11kV AC | Urban | - insulator tie wires / connections | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 140444 | 20170406JEM_03 | Broken HV tie caused the HV conductor coming off and contacting the street light. The molten parts of the street light also started a small grass fire at the base of the pole.
2068 | Jamena 16/20 | Jamena | 2016-01-11 | 0.3375 | -37.8249 | 144.8729 |  | A029455 | FE5 | Low voltage AC (<1kV) | Urban | - overhead service conductor (residential) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 140627 | 20170124JEM_01 | Deteriorated service insulation caused a service fire.
2069 | Jamena 16/21 | Jamena | 26/11/2016 | 0.53264 | -37.787 | 144.8871 |  | A036948 | BY12 | 22kV AC | Urban | - transformer (ground outdoor mounted) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 142339 | 20161126JEM_01 | Tree lopper caused a tree branch to fall on the bushing of a ground type transformer. This resulted in a fire to the tree branch. One high voltage bushing required replacement post this event.
2070 | Jamena 16/22 | Jamena | 2016-08-12 | 0.71875 | -37.8083 | 144.8417 |  | A020459 | TH22 | 22kV AC | Urban | - crossarm (wood) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 142787 | 20170124JEM_03 | Pole top fire due to tracking. New steel crossarm installed.
2071 | Jamena 16/23 | Jamena | 20/12/2016 | 0.67153 | -37.7487 | 144.955 |  | A146791 | CS5 | 22kV AC | Urban | - pole (wood) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 143274 | 20161221JEM_01 | Pole top fire due to tracking. New steel crossarm installed.
2072 | Jamena 16/24 | Jamena | 25/12/2016 | 0.72917 | -37.7053 | 144.8798 |  | A127943 | AW11 | Low voltage AC (<1kV) | Urban | - dropper / bridge | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 143417 | 20161226JEM_01 | The red phase LV connector lead between the substation LV isolators and LV mains failed. Sparking from failure caused a small grass fire to a vacant lot.
2073 | Jamena 16/25 | Jamena | 28/12/2016 | 0.83958 | -37.691 | 144.9754 |  | A035962 | CN6 | 22kV AC | Urban | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 143506 | 20161229JEM_02 | HV conductor fell down on the ground due to animal strike and started a grass fire.
2074 | Jamena 16/26 | Jamena | 30/12/2016 | 0.26597 | -37.6622 | 144.9684 |  | A126129 | BD8 | 22kV AC | Urban | - pole (wood) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 143603 | 20161230JEM_02 | Vandal threw jumper cables over HV overhead. Contact between conductor and HV arm caused fire which was confined to the pole top. Pole replaced on the day.
2075 | Jamena 16/27 | Jamena | 2017-10-01 | 0.59167 | -37.8197 | 144.8937 |  | A051445 | YVE25 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 143985 | 20170116JEM_03 | Tree branch contacted HV conductor and caught fire.
2076 | Jamena 16/28 | Jamena | 18/01/2017 | 0.28403 | -37.7064 | 144.879 |  | A046419 | AW12 | 22kV AC | Urban | - crossarm (wood) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 144286 | 20170118JEM_01 | Pole top fire due to tracking. New steel crossarm installed.
2077 | Jamena 16/29 | Jamena | 2017-05-02 | 0.83264 | -37.7958 | 144.9035 |  | A018179 | FE6 | 22kV AC | Urban | - crossarm (wood) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 145006 | 20170205JEM_01 | Pole top fire due to tracking. New steel crossarm installed.
2078 | Jamena 16/30 | Jamena | 22/02/2017 | 0.59167 | -37.6026 | 144.9152 |  | LONG ISLAND-ROYAL TROON | ST32 | Low voltage AC (<1kV) | Urban | - switch (any other type) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 145932 | 20170223JEM_01 | LV pillar was struck by a vehicle resulting in the LV circuit fuse at kiosk (LONG ISLAND-ROYAL TROON) to not operate causing leaves and bark inside the kiosk enclosure to smoulder. LV cabling and fuse equipment replaced after the event.
2079 | Jamena 16/31 | Jamena | 2017-01-03 | 0.47917 | -37.6699 | 144.9379 |  | A085074 | BD11 | Low voltage AC (<1kV) | Urban | - connector / termination | single phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 146152 | 20170406JEM_01 | Neutral screen service fell down to the ground and started a grass fire.
2080 | Jamena 16/32 | Jamena | 16/03/2017 | 0.63611 | -37.7362 | 144.8844 |  | A062446 | AW6 | Low voltage AC (<1kV) | Urban | Public lighting | single phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 146755 | 20170317JEM_01 | Public lighting fire. Lantern replaced on the day.
2081 | Jamena 16/33 | Jamena | 22/03/2017 | 0.17431 | -37.8146 | 144.8577 |  | A030074 | FW5 | 22kV AC | Urban | - crossarm (wood) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 146951 | 20170322JEM_01 | Pole top fire due to tracking. New steel crossarm installed.
2082 | Jamena 16/34 | Jamena | 19/05/2017 | 0.56458 | -37.6961 | 144.8856 |  | A045824 | AW14 | 22kV AC | Urban | - crossarm (wood) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 149283 | 20170519JEM_01 | Pole top fire due to tracking. New steel crossarm installed.
2083 | Jamena 16/35 | Jamena | 20/06/2017 | 0.98472 | -37.704 | 145.025 |  | A007393 | TT3 | 22kV AC | Urban | - crossarm (wood) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 150444 | 20170621JEM_01 | LV crossarm broke causing the HV dropper to contact the pole and burn through the LV arm. New LV crossarm installed.
2084 | Jamena 16/36 | Jamena | 25/06/2017 | 0.8 | -37.737 | 144.9932 |  | A071096 | CN8 | Low voltage AC (<1kV) | Urban | Public lighting | single phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 150619 | 20170629JEM_01 | Public lighting fire. Lantern replaced on the day.
2085 | CitiPower 16/17 | CitiPower | 18/08/2016 | 0.57917 | -37.8387 | 144.9931 |  | 30302043 | TK024 | Low voltage AC (<1kV) | Urban | - fuse (any other type) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 12356 | 20160826PWA_03 | A customer requested urgent attendance to isolate supply due to fire in MSB room at the incident location. Upon arrival, crew found that an overheated LV fuse board caught fire. MFB attended. Protection operated. The supply isolated and the place made safe. There were no injuries or ground fire.
2086 | CitiPower 16/18 | CitiPower | 20/08/2016 | 0.75417 | -37.8628 | 145.0196 |  | 30198370 | AR007 | Low voltage AC (<1kV) | Urban | - luminaries (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 12360 | 20160830PWA_01 | Trams control room reported a light fitting on Tramway Pole was on fire at the above incident location. On arrival, the crew found that a light fitting cap on a PTC Tramway Pole (located on the Tramway medium strip) had caught on fire, which melted the cap and burnt the light electrical components. There was no ground fire nor third party damaged. There were no reported injuries.
2087 | CitiPower 16/19 | CitiPower | 19/10/2016 | 0.49097 | -37.8329 | 144.9562 |  | 30170659 | AP011 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 12501 | 20161019PWA_02 | CitiPower report room received advise from the MFB about a fire at the incident location. On arrival the fault crew found that a krone box had overheated and caught fire, resulting in molten plastic falling onto a car below it, causing damage to the cars paint. The MFB extinguished the fire. CitiPower fault crew replaced the krone box and re-terminated connections to it. Supply was restored. There was no injury or ground fire as a result of this incident
2088 | CitiPower 16/20 | CitiPower | 28/10/2016 | 0.76042 | -37.8028 | 144.9457 |  | 30198811 | VM014 | Low voltage AC (<1kV) | CBD | - luminaries (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 12541 | 20161108PWA_05 | MSY Technology Pty Ltd staff reported a light fitting on Public Lighting Pole was on fire at the above incident location. On arrival, the crew found that a light fitting cap on a Public Lighting Pole had caught on fire, which melted the cap and burnt the light electrical components. There was no ground fire nor third party damaged. There were no reported injuries.
2089 | CitiPower 16/21 | CitiPower | 15/11/2016 | 0.41667 | -37.7607 | 144.9978 |  | 30186544 | NC014 | 11kV AC | Urban | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 12577 | 20161125PWA_02 | A passer-by called to advise pole on the corner of Stott & Woolton Avenue is sparking and making an arcing noise the MFB are in attendance at the incident location. On arrival the fault crew found that the a GFB switch was candling of the arc chute on roadside phase (HVSW #1008) was on fire at the incident location. The GFB was opened and the fire then extinguished. There was no ground fire and no injury as a result of this incident.
2090 | CitiPower 16/22 | CitiPower | 24/12/2016 | 0.6875 | -37.8086 | 145.0762 |  | 30175325 | L004 | Low voltage AC (<1kV) | Urban | - overhead conductor (bare; copper) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 12667 | 20161229PWA_10 | A customer reported that an insulator exploded and a fire occurred outside 125 Gordon St Balwyn at 16:30 24/12/16. CitiPower fault was dispatched at 16:37 to investigate. On arrival the crew found the bimetal crimp on the blue phase of the LV conductor, overheated and as a result melted the aluminium connecting cable. This caused melted aluminium to drop down to the below grass creating a ground fire on the road reserve. The dimension of the ground fire was 250mmx250mm. Crew reported that the fire was located on the road reserve next to pole LIS 18339 outside 127 Gordon St Balwyn. Crew made the site safe, installed parallels to put the customers back on supply and organised another crew to replace damaged assets. There were no reported injuries or 3rd party damage.
2091 | CitiPower 16/23 | CitiPower | 29/12/2016 | 0.79514 | -37.7598 | 144.9934 |  | 30197792 | NC013 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 12724 | 20170117PWA_04 | MFB reported a fire at the pole outside 316 St Georges Rd. On arrival the crew found that a krone box had burnt and required replacement. The krone box was open at the time of the fault & the cause of the fire was attributed to a loose connection. There were no reported injuries, ground fire or property damage.
2092 | CitiPower 16/24 | CitiPower | 18/01/2017 | 0.32431 | -37.7984 | 144.9953 |  | 30170685 | CW009 | 11kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 12753 | 20170125PWA_01 | Vic Fire informed that a pole on fire at the incident location and also a customer reported a transformer on fire. On arrival the crew found that an 11kV top cross arm had burnt through but the insulator and conductor intact on LULIE ABBOTT P07S (LIS 20676). The crew made the place safe and repairs have been arranged. There was no ground fire, third party damage or injury. MFB attended the scene.
2093 | CitiPower 16/25 | CitiPower | 19/03/2017 | 0.58403 | -37.8682 | 145.0145 |  | 30219414 | EL011 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 12964 | 20170331PWA_04 | Customer phoned in to advise that the a pole mounted box has caught fire and dropped to the ground, still smoking, and a possible wire down. Upon arrival the CitiPower faults crew found that the LV FOLCB supplying 590 & 590A Inkerman Rd, Caulfield North had caught fire and melted to the ground. The FOLCB also came into contact with the CATV on the pole which was found hanging from Pole LIS-30749. The crew made temporary repairs to the CATV to make it safe and made repairs to the LV underground service. There was no ground fire, injuries or third party damage.
2094 | CitiPower 16/26 | CitiPower | 19/05/2017 | 0.71458 | -37.8402 | 145.0724 |  | 30177504 | RD009 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 13133 | 20170601PWA_03 | MFB reported a pole fire opposite Wilson Park at 8 Culliton Rd Camberwell at approximate 17:09 19/05/2017. CitiPower linesmen were dispatched to investigate. On arrival the Linesmen determined that an FOLCB on Pole LIS 10497 overheated causing it to be damaged. The Linesmen on further investigation found burn marks on the pole and concluded that there was a small fire on the pole.
2095 | CitiPower 16/27 | CitiPower | 28/05/2017 | 0.94861 | -37.825 | 144.998 |  | 30221370 | NR006 | Low voltage AC (<1kV) | Urban | - luminaries (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 13132 | 20170601PWA_02 | MFB reported a pole fire at the above incident location. On arrival, the crew found that a Public Lighting Photo Electric Cell had faulted and caught on fire. There was no ground fire nor third party damaged. There were no reported injuries.
2096 | CitiPower 16/28 | CitiPower | 30/06/2017 | 0.52917 | -37.8306 | 145.0529 |  | 30202208 | CL023 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 13222 | 20170713PWA_07 | MFB reported a pole fire at the incident location. Upon arrival, the Powercor crew found that an overheated termination ignited the junction box on the pole. There were no injuries, third party damages or ground fire.
2097 | Ausnet 16/17 | Ausnet | 2016-01-07 | 42552.3528 | -38.0332 | 145.4819 |  | 501136 | OFR23 | Low voltage AC (<1kV) | RURAL LONG | - crossarm (wood) | single phase | Otherwise started by a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 222754 | 20160704SPN_02 | LV crossarm burnt in half on Substation pole.
2098 | Ausnet 16/18 | Ausnet | 2016-06-07 | 42557.9882 | -37.8109 | 145.2544 |  | 1221996 | RWT32 | Low voltage AC (<1kV) | URBAN | - lamps (major road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 222834 | 20160707SPN_01 | Reported street light fire at LIS 1221996. Isolated s/l. 150 Watt HPS; Crew isolated the S/L.
2099 | Ausnet 16/19 | Ausnet | 16/07/2016 | 42567.7208 | -38.1804 | 146.5619 |  | 2607388 | TGN11 | 22kV AC | RURAL SHORT | - switch (disconnector/isolator) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 222995 | 20160725SPN_02 | Burnt grass area at base of switch TN212 in road reserve. Removed wire from the top of the switch which it seemed birds had used to make a nest.
2100 | Ausnet 16/20 | Ausnet | 21/07/2016 | 42572.5785 | -37.4804 | 145.0118 |  | 931594 | KLO14 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 223145 | 20160725SPN_03 | Candled WØ EDO Fuse. NCF Conc pole LIS # 931594.
2101 | Ausnet 16/21 | Ausnet | 2016-02-08 | 42584.8388 | -37.6656 | 145.0178 |  | 911897 | EPG31 | 22kV AC | URBAN | - crossarm (wood) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 223367 | 20160805SPN_01 | Replaced HV X-arm which burnt due to tracking of conductor to X-arm. Fire restricted to end insulator and X-arm. No other damage.
2102 | Ausnet 16/22 | Ausnet | 2016-05-08 | 42587.3132 | -37.046 | 145.2985 |  | 4705147 | SMR5 | 12.7kV AC (SWER) | RURAL LONG | - fuse (EDO fuse) | single wire earth return (SWER) | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 223470 | 20160805SPN_02 | Fault crew found candled fuse Boric acid on SE273, replaced fuse and supply was restored.
2103 | Ausnet 16/23 | Ausnet | 2016-07-08 | 42589.5 | -38.0789 | 145.2838 |  | 523879 | CRE23 | Low voltage AC (<1kV) | URBAN | - lamps (minor road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 223502 | 20160808SPN_02 | Street light head burnt out. Concrete street light column with pit at base of pole.
2104 | Ausnet 16/24 | Ausnet | 2016-11-08 | 42593.4056 | -38.2116 | 145.7534 |  | 2718897 | WGL13 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 223599 | 20160812SPN_01 | HV fuse had candled/burnt
2105 | Ausnet 16/25 | Ausnet | 17/08/2016 | 42599.2772 | -38.0795 | 145.2743 |  | 505476 | CRE23 | 22kV AC | URBAN | - fuse (EDO fuse) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 223700 | 20160817SPN_01 | 3 blown fuses found at Sth Gipp Thompson S/S. Transformer found unserviceable with large oil leak. The substation had exploded. There had been a previous fault when a tree had fallen through the conductors causing a jolt on the transformer which may have caused transformer failure.
2106 | Ausnet 16/26 | Ausnet | 18/08/2016 | 42600.8479 | -37.875 | 148.005 |  | 1902429 | BDL41 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 223771 | 20160819SPN_01 | Field crew reports on arrival @ LIS #1902429 fuse tube burnt in half. Suspect candled. no ground fire.
2107 | Ausnet 16/27 | Ausnet | 22/08/2016 | 42604.7292 | -38.1903 | 147.2719 |  | 5744973 | SLE31 | Low voltage AC (<1kV) | RURAL LONG | - connection box | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 223842 | 20160823SPN_01 | Ground fire reported at base of pole.Fire area of 1 sq. metre. Found burnt out Krone Box.
2108 | Ausnet 16/28 | Ausnet | 25/08/2016 | 42607.627 | -37.7556 | 145.6848 |  | 1407925 | WYK23 | 22kV AC | RURAL SHORT | - overhead conductor (ABC) | three phase | Otherwise started by a distribution system | within electric line construction area | 19.8 | No forecast | 0.1 | 1.98 | 223925 | 20160829SPN_01 | HVABC joint failed in Alpine St, Warburton. Report received of fire on the ground. DAO advised. Failure occurred during REFCL testing.
2109 | Ausnet 16/29 | Ausnet | 27/08/2016 | 42609.5549 | -37.8603 | 148.08 |  | 1902844 | NLA34 | Low voltage AC (<1kV) | RURAL SHORT | - connection box | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 223960 | 20160829SPN_02 | Per CFA Pole Fire. 3 phase mains pole box caught fire and melted on pole scorching the pole. Melting plastic fell to the ground, no fire started on the ground.
2110 | Ausnet 16/30 | Ausnet | 29/08/2016 | 42611.7143 | -38.1844 | 146.5619 |  | 2604178 | TGN-MFA | 66kV AC | UNCLASSIFIED | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 223979 | 20160830SPN_01 | Fault crew called to fire at base of concrete HV pole 2604178 on the Traralgon Maffra Road, Traralgon. Grass fire area burnt was approximately 25 x 15 metres in size. 66kV feeder had 1 reclose, on supply when the crew arrived. 2 burnt crows found at base of pole. Bird flashover.
2111 | Ausnet 16/31 | Ausnet | 2016-02-09 | 42615.184 | -38.2463 | 145.5667 |  | 513602 | LLG11 | Low voltage AC (<1kV) | RURAL SHORT | - connection box | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 224049 | 20160906SPN_01 | Emergency Authorities reported an alleged pole fire. When AusNet Services' fault crew arrived the CFA were on site. Allegedly only the LV leads and 3 phase fuse box (FOLCB) was burnt. The pole was a HV/LV wood substation pole.
2112 | Ausnet 16/32 | Ausnet | 2016-05-09 | 42618.4965 | -36.1011 | 146.8266 |  | 5217235 | WO13 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 224089 | 20160906SPN_02 | Crew found a HV fuse hung up and candled PF fuse tube. The fuse and fuse tube were replaced. lis 5217235.
2113 | Ausnet 16/33 | Ausnet | 14/09/2016 | 42627.1248 | -36.2961 | 146.2655 |  | 5696900 | WN2 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 224271 | 20160914SPN_01 | On patrolling the line to locate a fault the crew found a HV fuse had hung up and candled.
2114 | Ausnet 16/34 | Ausnet | 15/09/2016 | 42628.4917 | -36.1241 | 146.8916 |  | 5808844 | WO32 | Low voltage AC (<1kV) | URBAN | - LV pillar | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 224298 | 20160922SPN_02 | Fault Crew attended a reported pillar on fire in Ethel St Wodonga. A small area of grass was burnt surrounding the pillar due to the flames/arc coming out of the base of the pillar. A 200 Amp switch failed, believed to have been caused by moisture ingress.
2115 | Ausnet 16/35 | Ausnet | 24/09/2016 | 42637.8932 | -37.8967 | 145.2344 |  | 1309556 | BRA21 | Low voltage AC (<1kV) | URBAN | - lamps (minor road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 224480 | 20160926SPN_01 | Street light head South side burnt out. VicRoads advised a street light head on fire 200 metres east of Stud Road in Ferntree Gully Road Scoresby. Lis number 1309623. No fire on pole or ground.
2116 | Ausnet 16/36 | Ausnet | 29/09/2016 | 42642.7674 | -36.4566 | 146.4609 |  | 5740818 | WN5 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 224584 | 20161003SPN_01 | Fault crew attended reports of dim lights by customers. found a candling HV BA 6V fuse on the transformer, pole 5740818. No fire evident
2117 | Ausnet 16/37 | Ausnet | 2016-02-10 | 42645.6472 | -37.8831 | 145.506 |  | 408364 | BGE22 | 12.7kV AC (SWER) | RURAL SHORT | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 224591 | 20161003SPN_03 | Storm winds and rains caused an approx. 25 metre tall skinny stringy bark tree to fall on onto 3/12 steel 12.7 kV S.W.E.R overhead conductor to break and fault current suspected to have caused sparks and hot molten metal to ignite and start a small grass fire. ACR tripped to lockout.
2118 | Ausnet 16/38 | Ausnet | 2016-09-10 | 42652.6211 | -37.7261 | 145.1472 |  | 921845 | ELM34 | 22kV AC | URBAN | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 224666 | 20161010SPN_04 | Large tree located on Parkland opposite 674 Main Rd, Eltham fell over onto open bare 22kV and 415V conductors. This caused the Feeder to trip. Tree fell due to high wind gusts at the time and the ground being very wet from recent rain. A FOLCB caught fire at LIS 921845 but it was extinguished and no ground fire occurred.
2119 | Ausnet 16/39 | Ausnet | 2016-09-10 | 42652.6924 | -38.0443 | 145.4964 |  | 503441 | PHM33 | 22kV AC | RURAL SHORT | - fuse (boric acid) | single phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 224711 | 20161014SPN_01 | Large Tree approx. 15m away from powerline was >20m tall and fell across HV Wires. Fire and burn damage to tree in immediate area, but no significant damage to the ground or any property or livestock.
2120 | Ausnet 16/40 | Ausnet | 2016-12-10 | 42655.1424 | -37.7462 | 145.6536 |  | 1407535 | WYK23 | Low voltage AC (<1kV) | RURAL SHORT | - connection box | three phase | Otherwise started by a distribution system | within electric line construction area | 19.8 | No forecast | 0.1 | 1.98 | 224695 | 20161012SPN_01 | Small fire in vicinity at base of pole, LV Krone fuse box melted on substation pole caused by a loose LV connection on LV leads to Krone fuse box.
2121 | Ausnet 16/41 | Ausnet | 2016-12-10 | 42655.6583 | -36.4604 | 146.5048 |  | 5110573 | WN5 | 22kV AC | RURAL LONG | - fuse (boric acid) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 224710 | 20161014SPN_02 | Cust reports crackling/buzzing sound from transformer in front of property. A 6 Amp Boric Acid fuse on the roadside was hung-up and candled.
2122 | Ausnet 16/42 | Ausnet | 16/10/2016 | 42659.7549 | -38.0299 | 145.3151 |  | 504819 | NRN14 | 22kV AC | URBAN | - crossarm (wood) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 224761 | 20161017SPN_02 | CEOT received a report from the CFA of a fire on LV crossarm @ LIS #504819. The HV crossarm was found broken and the HV overhead conductor fell into LV conductor. HV fuse operated, BW3356. No ground fire occurred. No HVI damage occurred to customers' properties.
2123 | Ausnet 16/43 | Ausnet | 16/10/2016 | 42659.9416 | -37.7673 | 145.4711 |  | 1014014 | WYK12 | 22kV AC | RURAL SHORT | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 224759 | 20161017SPN_01 | An AusNet Services' fault crew attended an incident and advised CEOT that a small ground fire was observed around AusNet Services' assets ex HV Switch LD463. The fire size was less than 10m x 1m in size. A tall gum tree fell onto the HV overhead line and caused a HV conductor to break and fall to the ground.
2124 | Ausnet 16/44 | Ausnet | 21/10/2016 | 42664.241 | -38.4533 | 145.2616 |  | 2805771 | PHI13 | 22kV AC | URBAN | - fuse (boric acid) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 224867 | 20161024SPN_02 | HV fuse at substation has hung-up/candled. The substation fuse was a 6A Boric Acid fuse that had candled, no fire, but well on the way to burning out.
2125 | Ausnet 16/45 | Ausnet | 30/10/2016 | 42673.3993 | -38.0782 | 147.1014 |  | 2502968 | SLE32 | Low voltage AC (<1kV) | RURAL SHORT | - connection box | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 224998 | 20161102SPN_01 | On arrival the fault truck noticed a 100 amp fused mains box that was fed from the line side of the transformer isolators was melting/burning and proceeded to isolate it.
2126 | Ausnet 16/46 | Ausnet | 2016-02-11 | 42676.7479 | -38.0611 | 145.3218 |  | 5639730 | HPK14 | Low voltage AC (<1kV) | URBAN | - LV pillar | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 225023 | 20161104SPN_02 | VicPol reported that a car had run into an electrical pillar. The driver lost control of his Holden Commodore ute and hit the LV paralleling pillar 5664082 and the car caught fire as a result. The car caught fire because one of the phases came in contact with the metal frame of the car.
2127 | Ausnet 16/47 | Ausnet | 2016-04-11 | 42678.7123 | -37.6308 | 145.0966 |  | 917429 | DRN11 | 22kV AC | RURAL SHORT | - overhead conductor (ABC) | three phase | Otherwise started by a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 225045 | 20161107SPN_01 | Between Lis 917428 and 917429 - HV ABC failed/blown midspan - small grass fire reported underneath. Fire damage 30cm/30cm to wood chip garden bed underneath HV ABC.
2128 | Ausnet 16/48 | Ausnet | 2016-06-11 | 42680.9581 | -38.1508 | 146.7824 |  | 5643747 | TGN41 | Low voltage AC (<1kV) | RURAL LONG | - lamps (major road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 225046 | 20161107SPN_02 | Streetlight head was reported on fire out the front of 93 Princes st Rosedale. Exact cause uncertain but it is common for such older street lights to fail due to either faulty ignitors with repetitive striking or failed plastic clad capacitors.
2129 | Ausnet 16/49 | Ausnet | 2016-07-11 | 42681.4599 | -38.1005 | 145.7424 |  | 2709203 | WGL12 | 22kV AC | RURAL LONG | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 225057 | 20161108SPN_01 | CFA reported trees on power lines and grass fire in area. Tree fell into overhead HV conductors causing the conductors to clash. The tree was between pole asset numbers 2709203 and 2709206 and was located in the road reserve.
2130 | Ausnet 16/50 | Ausnet | 2016-10-11 | 42684.5535 | -37.0592 | 145.1086 |  | 578208 | SMR1 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | within electric line construction area | 19.8 | Low-moderate | 0.2 | 3.96 | 225159 | 20161110SPN_01 | Crew found hung up EDO fuse that had possibly candled & cause a spark to hit the ground. Customer extinguished the fire of approx. size 86m2.
2131 | Ausnet 16/51 | Ausnet | 15/11/2016 | 42689.0514 | -37.8256 | 147.6361 |  | 1614740 | BDL43 | Low voltage AC (<1kV) | RURAL SHORT | - lamps (major road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 225215 | 20161115SPN_02 | A street light caught fire per cfa. The street light had a black plastic cover on the back of the light and there was a fault in the wiring that caused this plastic to combust, melting the plastic and causing smoke.
2132 | Ausnet 16/52 | Ausnet | 21/11/2016 | 42695.4167 | -37.6903 | 145.0426 |  | 5792621 | WT12 | Extra low voltage DC (<120V ripple free) | URBAN | Other | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 225384 | 20161220SPN_02 | Report on burnt CB Trip Coil at AAGS for Q102 HV CB Monday 21st Nov, 2016 No persons were hurt or in immediate danger due to this incident.
2133 | Ausnet 16/53 | Ausnet | 21/11/2016 | 42695.4292 | -38.4822 | 145.2052 |  | 2807007 | PHI12 | 22kV AC | RURAL SHORT | - overhead conductor (bare; copper) | single phase | Otherwise started by a distribution system | HBRA only | 1 | Very high | 1 | 1 | 225339 | 20161121SPN_01 | HV overhead conductor broke and fell to the ground. A 5m x 10m shrub fire occurred. The CFA was called to extinguish the fire. HV fuse operated.
2134 | Ausnet 16/54 | Ausnet | 23/11/2016 | 42697.7257 | -37.1251 | 145.0274 |  | 4701254 | SMR4 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 225404 | 20161124SPN_02 | On arrival to SMR BFD 205 substation, one HV fuse had candled and there was a tail hanging on the lightning arrestor but unable to determine if this had caused the fault. There were no deceased bird life or animals in vicinity.
2135 | Ausnet 16/55 | Ausnet | 28/11/2016 | 42702.1597 | -38.4997 | 145.4449 |  | 2803741 | WGI23 | 22kV AC | RURAL SHORT | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 225484 | 20161128SPN_01 | Operator advised upon arriving @ INCD-21401-s that he found a candled & hung-up Boric Acid fuse. It was a 6A Boric Acid fuse and there was a light drizzle and mist at the time. The area is a high salt area which may have been a contributing factor for this incident.
2136 | Ausnet 16/56 | Ausnet | 2016-02-12 | 42706.0917 | -37.9873 | 145.3147 |  | 519671 | LYD13 | Low voltage AC (<1kV) | URBAN | - lamps (minor road) | single phase | Otherwise started by a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 225575 | 20161205SPN_02 | Street light hit - fire - disconnected.
2137 | Ausnet 16/57 | Ausnet | 2016-04-12 | 42708.6729 | -37.7728 | 145.2757 |  | 1216269 | CPK11 | 22kV AC | RURAL SHORT | - overhead conductor (ABC) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 225589 | 20161205SPN_04 | HV ABC cable had been found burnt between poles 1216269 and 1216271 after protection had tripped off. No evidence of any fire damage was found, only the HV ABC appeared to be damaged. DAO attended site and found burnt HV ABC still in the air.
2138 | Ausnet 16/58 | Ausnet | 2016-09-12 | 42713.4076 | -38.5108 | 145.3342 |  | 2800945 | WGI31 | 22kV AC | RURAL SHORT | - guy wire | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 225705 | 20161216SPN_01 | Corroded stay wire helical termination failed at ground level on HV anchor pole (with single phase transformer) and flicked into HV droppers of transformer becoming alive on ground where small fire occurred.
2139 | Ausnet 16/59 | Ausnet | 2016-12-12 | 42716.0479 | -37.8579 | 145.2324 |  | 1031645 | BRA21 | Low voltage AC (<1kV) | URBAN | - LV pillar | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 225845 | 20170116SPN_02 | Crew were callled to replace 300kva kiosk s/s as well as LV straight joints to pillar which had failed due to the cabiling being old lead sheath U/G cable. The LV paralleling pillar was burnt out. The fire was contained within the pillar. There was no ground /grass fire.
2140 | Ausnet 16/60 | Ausnet | 2016-12-12 | 42716.1944 | -36.1654 | 146.7646 |  | 597646 | BWA22 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 225722 | 20170117SPN_04 | Rural customer called up fault and reported arcing on transformer pole with sparks and lights dimming. Customer is fed via MARTINDALE 16, single phase 10kVA S/S, wood pole. Crew attended and found one of the two EDO fuses tubes burnt in half, no evidence of fire on ground.
2141 | Ausnet 16/61 | Ausnet | 14/12/2016 | 42718.474 | -38.6367 | 145.7106 |  | 2810182 | WGI34 | 22kV AC | RURAL SHORT | - overhead conductor (bare; all aluminium conductor) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 225792 | 20170117SPN_06 | HV centre phase conductor failed at bridge where it has signs of corrosion at pole 2810182 Toorak Rd Spur P8 falling to ground where small fire was noticed. Fire attended by CFA and extinguished. Very small grass fire in vicinity. Fire size 1m x 200mm in LBRA location. Feeder CB tripped to lockout.
2142 | Ausnet 16/62 | Ausnet | 17/12/2016 | 42721.6624 | -37.9015 | 147.2116 |  | 2512255 | MFA21 | 12.7kV AC (SWER) | RURAL LONG | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 225833 | 20161219SPN_01 | A tree fell into a SWER conductor bringing the conductor to the ground and allegedly starting a grass fire. ACR reclosed a number of times then went to lockout. The fire had burnt an area of approximately 25m x 5m. A tree branch was on the ground underneath where the conductor had been dislodged.
2143 | Ausnet 16/63 | Ausnet | 17/12/2016 | 42721.8995 | -38.1835 | 145.7807 |  | 2702476 | WGL13 | Low voltage AC (<1kV) | RURAL SHORT | - connection box | three phase | Otherwise started by a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 225834 | 20161219SPN_02 | Hot metal from a loose LV connection on the pole for underground conductors appeared to have fallen to the ground. A 8m x 7m ground fire was observed in the vicinity. No other damage.
2144 | Ausnet 16/64 | Ausnet | 19/12/2016 | 42723.7479 | -38.5219 | 145.3875 |  | 2812439 | WGI31 | 22kV AC | RURAL SHORT | - connector / termination | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very high | 1 | 4.6 | 225855 | 20161220SPN_01 | AusNet Services' fault crew attended the site and discovered a small 6m x 4m fire had burnt out in relatively short green grass at the base of the concrete pole. The White Phase Ampact connector had failed at the top of the ACR line side isolator.No damage to property.
2145 | Ausnet 16/65 | Ausnet | 21/12/2016 | 42725.2889 | -37.8234 | 147.6593 |  | 1610888 | BDL4 | Low voltage AC (<1kV) | RURAL SHORT | - connection box | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 225879 | 20170201SPN_01 | Upon investigation found melted Krone box. Two small grass fires at base of pole, one was approx 6 x 4 metres the other was approx. 3 x 1 metres.
2146 | Ausnet 16/66 | Ausnet | 22/12/2016 | 42726.7083 | -38.5771 | 145.6837 |  | 2804984 | WGI14 | Low voltage AC (<1kV) | RURAL SHORT | - switch (disconnector/isolator) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 225901 | 20170206SPN_07 | Small fire in waist high dry grass 4x6m size. A loose connection on LV isolator was the cause of the fault. Crew repaired damaged LV isolator.
2147 | Ausnet 16/67 | Ausnet | 24/12/2016 | 42728.3861 | -37.319 | 145.0683 |  | 4701417 | SMR3 | 12.7kV AC (SWER) | RURAL LONG | - fuse (boric acid) | single wire earth return (SWER) | Otherwise started by a distribution system | within electric line construction area | 19.8 | High | 0.5 | 9.9 | 225923 | 20170202SPN_02 | Crew were sent to all supply fault, found the boric acid fuse had hung up, also found blown transformer and damage to lightning arrestor
2148 | Ausnet 16/68 | Ausnet | 26/12/2016 | 42730.4282 | -36.2074 | 146.9741 |  | 5201337 | WOTS11 | 22kV AC | RURAL LONG | - insulators | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very high | 1 | 4.6 | 225927 | 20170103SPN_03 | Magpie across insulator @ LIS 5201337. 5 Shed insulator damaged. Grass fire reported by CFA. WOTS11 reclose was at 0701hrs.
2149 | Ausnet 16/69 | Ausnet | 28/12/2016 | 42732.5242 | -37.4822 | 145.2908 |  | 1401497 | KLK1 | 22kV AC | RURAL SHORT | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very high | 1 | 4.6 | 225932 | 20170103SPN_04 | Large pine tree broke off near base and fell 22m across hv/lv line just south of pole 1400108. Small grass fire was started mid span between poles 5765123 and 1401497
2150 | Ausnet 16/70 | Ausnet | 29/12/2016 | 42733.3371 | -37.7135 | 145.1054 |  | 901742 | WT7 | Low voltage AC (<1kV) | URBAN | - connection box | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 225934 | 20170206SPN_04 | Crew attended and found that service junction box allegedly caught fire above LV x arm on concrete pole, LIS 901742.
2151 | Ausnet 16/71 | Ausnet | 2017-06-01 | 42741.7213 | -37.5111 | 145.0258 |  | 914158 | KLO14 | 22kV AC | RURAL LONG | - switch (disconnector/isolator) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 225981 | 20170109SPN_01 | A loose conductor connection on a pole mounted HV isolator failed resulting in hot particles falling to the ground resulting in a medium size grass fire.
2152 | Ausnet 16/72 | Ausnet | 2017-07-01 | 42742.5304 | -37.6167 | 145.5216 |  | 1409917 | WYK24 | 22kV AC | RURAL SHORT | - overhead conductor (ABC) | three phase | Otherwise started by a distribution system | within electric line construction area | 19.8 | Very high | 1 | 19.8 | 225984 | 20170109SPN_02 | HV non-metallic screened (NMS) ABC cable insulation failure with fault current traversing the steel cable catenary and concrete pole earthing causing hot melted particles to fall to the ground resulting in a small grass fire.
2153 | Ausnet 16/73 | Ausnet | 2017-07-01 | 42742.641 | -37.7967 | 147.8581 |  | 1900002 | BDL41 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 225985 | 20170116SPN_01 | Candled/burnt EDO fuse tube. EDO fuse failed to operate correctly resulting in a small grass fire at base of pole.
2154 | Ausnet 16/74 | Ausnet | 2017-08-01 | 42743.2913 | -37.8096 | 145.2387 |  | 1212124 | RWT14 | Low voltage AC (<1kV) | URBAN | - connector / termination | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 225987 | 20170109SPN_03 | IPC connector on 4x150 sq.mm LV ABC mains conductor failed with hot molten plastic from the connector igniting a small grass fire at base of pole.
2155 | Ausnet 16/75 | Ausnet | 2017-08-01 | 42743.5104 | -37.8468 | 147.0095 |  | 2513880 | MFA21 | Low voltage AC (<1kV) | RURAL LONG | - connector / termination | three phase | Otherwise started by a distribution system | HBRA only | 1 | Very high | 1 | 1 | 225988 | 20170109SPN_04 | Loose LV connection on pole mounted Blue phase LV fuse isolator.
2156 | Ausnet 16/76 | Ausnet | 2017-10-01 | 42745.5042 | -38.0214 | 146.6344 |  | 2602874 | TGN31 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 226003 | 20170220SPN_03 | Candled/burnt EDO fuse tube. EDO fuse failed to operate correctly.
2157 | Ausnet 16/77 | Ausnet | 2017-10-01 | 42745.7521 | -38.4606 | 146.2471 |  | 2721123 | MWT14 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 226011 | 20170220SPN_02 | Candled/burnt EDO fuse tube. EDO fuse failed to operate correctly.
2158 | Ausnet 16/78 | Ausnet | 2017-12-01 | 42747.5319 | -38.1231 | 147.0804 |  | 2503205 | MWTS-SLE | 66kV AC | UNCLASSIFIED | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 226009 | 20170111SPN_01 | A very large bird (an Eagle) landed on a concrete pole with steel crossarms (dual circuit 66kV lines and a single circuit 22 kV line angle type structure) and made contact with a 66kV conductor (and believed to the steel crossarm) resulting in electrocution and burning of the bird which fell to the ground starting a medium size grass fire.
2159 | Ausnet 16/79 | Ausnet | 16/01/2017 | 42751.7743 | -38.6524 | 146.3258 |  | 2014374 | FTR12 | Low voltage AC (<1kV) | RURAL LONG | - overhead service conductor (residential) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 226065 | 20170117SPN_01 | A tractor with a mowing unit attached contacted a 3-wire overhead service cable which broke and fell to the ground causing sparks resulting in a small grass fire.
2160 | Ausnet 16/80 | Ausnet | 17/01/2017 | 42752.4465 | -37.2954 | 144.9823 |  | 4717283 | SMR-KMS | 66kV AC | UNCLASSIFIED | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Severe | 2 | 9.2 | 226071 | 20170117SPN_02 | A large bird caused a flashover between a 66kV conductor to the bottom of the 66kV insulator to the concrete pole resulting in a small fire.
2161 | Ausnet 16/81 | Ausnet | 17/01/2017 | 42752.4785 | -37.9631 | 146.9858 |  | 2514867 | MFA31 | Low voltage AC (<1kV) | RURAL SHORT | - overhead service conductor (residential) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 226088 | 20170118SPN_01 | A neutral screen service cable termination clamp failed at the pole end causing the cable to burn and fall to the ground resulting in a small grass fire.
2162 | Ausnet 16/82 | Ausnet | 17/01/2017 | 42752.7653 | -37.8947 | 145.249 |  | 1311306 | BRA13 | Low voltage AC (<1kV) | URBAN | - connection box | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 226090 | 20170222SPN_01 | A Fused Switch Disconnector (FSD) (Krone box) caught fire causing the box to melt. Typical causes are high impedance connections or electrical overload.
2163 | Ausnet 16/83 | Ausnet | 25/01/2017 | 42760.7569 | -37.8302 | 145.3347 |  | 1208865 | BWR13 | 22kV AC | URBAN | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within electric line construction area | 19.8 | High | 0.5 | 9.9 | 226200 | 20170301SPN_02 | Candled/burnt EDO fuse tube. EDO fuse failed to operate correctly.
2164 | Ausnet 16/84 | Ausnet | 25/01/2017 | 42760.7625 | -36.1553 | 146.0553 |  | 5131906 | WN2 | 12.7kV AC (SWER) | RURAL LONG | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any other thing forming part of or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very high | 1 | 4.6 | 226201 | 20170130SPN_01 | A tip truck delivering mulch contacted an overhead SWER conductor resulting in a small grass fire.
2165 | Ausnet 16/85 | Ausnet | 26/01/2017 | 42761.4146 | -38.6299 | 146.503 |  | 2609024 | FTR12 | Low voltage AC (<1kV) | RURAL LONG | - connection box | single wire earth return (SWER) | Otherwise started by a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 226205 | 20170215SPN_01 | A Fused Overhead Line Connector Box (FOLCB) caught fire causing the box to melt resulting in a small grass fire. Typical causes are high impedance connections or electrical overload.
2166 | Ausnet 16/86 | Ausnet | 31/01/2017 | 42766.7403 | -36.551 | 145.9832 |  | 3900143 | BN4 | Low voltage AC (<1kV) | URBAN | - connection box | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 226246 | 20170301SPN_03 | A 100 Amp pole junction box supplying an underground service cable caught fire caused by electrical overload. This also resulted in fire damage to overhead service cables on the pole.
2167 | Ausnet 16/87 | Ausnet | 2017-05-02 | 42771.7438 | -38.249 | 146.4971 |  | 2623408 | TGN23 | 22kV AC | RURAL SHORT | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 226292 | 20170206SPN_01 | A large bird caused a flashover between a HV conductor and steel crossarm on a concrete pole resulting in electrocution and burning of the bird which fell to the ground starting a large grass fire.
2168 | Ausnet 16/88 | Ausnet | 2017-05-02 | 42771.7875 | -37.7703 | 145.2038 |  | 1205491 | RWN26 | Low voltage AC (<1kV) | RURAL SHORT | - overhead service conductor (residential) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Low-moderate | 0.2 | 0.92 | 226466 | 20170206SPN_02 | Strong wind conditions caused a neutral screen service cable connection to come away at the POA end causing the cable to fall to the ground resulting in sparking and a small grass fire.
2169 | Ausnet 16/89 | Ausnet | 2017-08-02 | 42774.6103 | -36.378 | 146.3562 |  | 5110868 | WN5 | 22kV AC | RURAL LONG | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 226337 | 20170215SPN_02 | A large decayed mature river red gum tree fell onto 22kV conductors which resulted in a medium size grass fire.
2170 | Ausnet 16/90 | Ausnet | 2017-08-02 | 42774.9924 | -37.8219 | 145.2432 |  | 1216447 | RWT32 | Low voltage AC (<1kV) | URBAN | - services pit | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 226336 | 20170209SPN_01 | An LV IPC connection caught fire and hot molten plastic fell to the ground resulting in several small burn marks on the grass.
2171 | Ausnet 16/91 | Ausnet | 2017-09-02 | 42775.7854 | -36.5305 | 145.9173 |  | 597128 | BN3 | 22kV AC | RURAL SHORT | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 226356 | 20170213SPN_01 | Candled/burnt EDO fuse tube. EDO fuse failed to operate correctly resulting in a medium size grass fire and the burning of 300 hay bales.
2172 | Ausnet 16/92 | Ausnet | 2017-11-02 | 42777 | -37.8541 | 145.5429 |  | 1316030 | LDL13 | 12.7kV AC (SWER) | RURAL SHORT | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 226393 | 20170213SPN_03 | Windy conditions caused a large tree branch to fall into a SWER line bringing the conductor to the ground starting a small grass fire.
2173 | Ausnet 16/93 | Ausnet | 2017-12-02 | 42778.1181 | -36.1566 | 147.2631 |  | 5212292 | WOTS24 | 12.7kV AC (SWER) | RURAL LONG | - fuse (boric acid) | single wire earth return (SWER) | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 226394 | 20170213SPN_04 | A Boric Acid tube fuse hung-up and candled caused by lightning.
2174 | Ausnet 16/94 | Ausnet | 13/02/2017 | 42779.4224 | -38.4696 | 145.2972 |  | 2805593 | PHI11 | 22kV AC | RURAL SHORT | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 226406 | 20170214SPN_02 | Possum on substation pole caused a flashover, shorted between phases, which resulted in the pole top being burnt through at the king bolt causing the HV conductors to fall into LV conductors.
2175 | Ausnet 16/95 | Ausnet | 13/02/2017 | 42779.5861 | -38.2143 | 145.3189 |  | 517359 | CRE33 | 22kV AC | RURAL SHORT | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 226409 | 20170214SPN_03 | Possum on 3 phase anchor pole caused a flashover, shorted between phases which resulted in a pole fire.
2176 | Ausnet 16/96 | Ausnet | 14/02/2017 | 42780.6337 | -36.0083 | 146.3938 |  | 5207130 | WN3 | Low voltage AC (<1kV) | RURAL LONG | - switch (disconnector/isolator) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 226441 | 20170216SPN_02 | An LV fused isolator on a substation pole overheated where the copper lead is attached to the isolator. Hot material falling from the isolator may have still been alight when it hit the ground resulting in a small grass fire.
2177 | Ausnet 16/97 | Ausnet | 15/02/2017 | 42781.5021 | -37.7986 | 145.4079 |  | 1010839 | LDL13 | Low voltage AC (<1kV) | RURAL SHORT | - overhead conductor (ABC) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very high | 1 | 4.6 | 226450 | 20170216SPN_03 | Burnt out active conductors at LV ABC IPC connections at pole top caused sparks and molten plastic to fall to the ground resulting in a very small grass fire.
2178 | Ausnet 16/98 | Ausnet | 15/02/2017 | 42781.8299 | -38.5098 | 145.2277 |  | 2806401 | PHI12 | 22kV AC | RURAL SHORT | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | HBRA only | 1 | Very high | 1 | 1 | 226461 | 20170216SPN_04 | Plastic silage pieces for hay bales was blown onto the nearby HV conductors causing the plastic silage to catch fire and fall to the ground starting a medium size grass fire.
2179 | Ausnet 16/99 | Ausnet | 16/02/2017 | 42782.2083 | -37.8358 | 145.2389 |  | 1204917 | RWT15 | 66kV AC | URBAN | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 226488 | 20170217SPN_01 | A possum caused a flashover between a 66kV conductor and the concrete pole/steel crossarm and into the neutral via an Optus earth resulting in a gas meter fire.
2180 | Ausnet 16/100 | Ausnet | 17/02/2017 | 42783.7245 | -36.285 | 147.1187 |  | 5217958 | WOTS13 | 22kV AC | RURAL LONG | - fuse (boric acid) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 226507 | 20170220SPN_01 | A Boric Acid tube fuse hung-up and was arcing between the top and bottom sections of the fuse tube causing molten material to fall to the ground resulting in a medium size grass fire.
2181 | Ausnet 16/101 | Ausnet | 22/02/2017 | 42788.6597 | -37.3762 | 145.0333 |  | 912281 | KLO14 | 22kV AC | RURAL LONG | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Severe | 2 | 9.2 | 226575 | 20170222SPN_02 | During strong wind conditions a partly rotted tall gum tree on private property broke and fell into a 22kV conductor causing it to contact an LV conductor resulting in sparks and hot molten material to fall to the ground igniting a medium size grass fire.
2182 | Ausnet 16/102 | Ausnet | 23/02/2017 | 42789.6278 | -36.1174 | 147.0031 |  | 5235747 | WOTS-HPS | 66kV AC | UNCLASSIFIED | - crossarm (wood) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very high | 1 | 4.6 | 226579 | 20170223SPN_01 | A broken crossarm on a parallel vertical 66kV circuit caused the middle and lower conductors to clash resulting in a large grass fire. Active termites were found in the broken crossarm and in the pole.
2183 | Ausnet 16/103 | Ausnet | 28/02/2017 | 42794.6153 | -37.8133 | 145.287 |  | 1206763 | CYN11 | 22kV AC | URBAN | - switch (disconnector/isolator) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 226658 | 20170228SPN_01 | A bird shorted out between the 22kV leads and the lever of a HV gas switch resulting in a small grass fire.
2184 | Ausnet 16/104 | Ausnet | 2017-01-03 | 42795.2792 | -36.8438 | 145.463 |  | 3901723 | BN1 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 226773 | 20170301SPN_01 | A Boric Acid fuse tube hung-up and candled causing molten material to fall to the ground resulting in a medium size grass fire. Boric Acid fuse failed to operate correctly.
2185 | Ausnet 16/105 | Ausnet | 2017-03-03 | 42797.4701 | -36.2386 | 146.272 |  | 5103424 | WN3 | Low voltage AC (<1kV) | RURAL LONG | - connection box | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | Very high | 1 | 4.6 | 226737 | 20170306SPN_01 | A Fused Switch Disconnector (FSD) (Krone box) caught fire causing the box to melt resulting in a small grass fire. Typical causes are high impedance connections or electrical overload.
2186 | Ausnet 16/106 | Ausnet | 2017-03-03 | 42797.9429 | -37.2217 | 145.6514 |  | 4712442 | RUBA12 | 12.7kV AC (SWER) | RURAL LONG | - overhead conductor (bare; steel) | single wire earth return (SWER) | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 226756 | 20170306SPN_02 | Strong windy conditions caused a large tree branch to fall into a SWER line bringing the conductor to the ground starting a medium size grass fire. The tree branch showed signs of rot and the tree was outside the vegetation clearance space.
2187 | Ausnet 16/107 | Ausnet | 2017-08-03 | 42802.5986 | -38.0926 | 145.5022 |  | 524590 | PHM12 | 22kV AC | RURAL SHORT | - transformer (pole mounted) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 226815 | 20170309SPN_01 | A large bird caused a flashover between a HV termination and earth of a transformer on a concrete substation pole resulting in electrocution and burning of the bird which fell to the ground starting a medium size grass fire.
2188 | Ausnet 16/108 | Ausnet | 2017-10-03 | 42804.7278 | -38.4562 | 145.2422 |  | 2803645 | PHI13 | Low voltage AC (<1kV) | URBAN | - connection box | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 226862 | 20170406SPN_01 | A Fused Switch Disconnector (FSD) (Krone box) caught fire causing the box to melt. Typical causes are high impedance connections or electrical overload.
2189 | Ausnet 16/109 | Ausnet | 13/03/2017 | 42807.4326 | -38.1201 | 146.2694 |  | 2201134 | MOE21 | Low voltage AC (<1kV) | RURAL SHORT | - connection box | single phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | High | 0.5 | 2.3 | 226876 | 20170508SPN_01 | A pole junction box failed causing it to catch on fire. A small patch of grass was burnt at base of the pole. Typical causes are high impedance connections or electrical overload.
2190 | Ausnet 16/110 | Ausnet | 15/03/2017 | 42809.1222 | -37.7073 | 145.1617 |  | 918947 | ELM13 | 22kV AC | URBAN | - switch (disconnector/isolator) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Very high | 1 | 0.2 | 226903 | 20170316SPN_02 | A possum caused a flashover between phases at a manually operated HV Gas Switch mounted on a wood pole resulting in hot particles falling to the ground starting a very small patch of grass to catch fire.
2191 | Ausnet 16/111 | Ausnet | 15/03/2017 | 42809.2861 | -38.5863 | 146.5596 |  | 2622133 | FTR12 | 22kV AC | RURAL LONG | - fuse (boric acid) | single phase | Otherwise started by a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 226904 | 20170510SPN_02 | Candled/burnt Boric Acid fuse tube. Boric Acid fuse failed to operate correctly.
2192 | Ausnet 16/112 | Ausnet | 18/03/2017 | 42812.0547 | -38.0707 | 145.5725 |  | 517611 | PHM14 | 22kV AC | RURAL LONG | - switch (disconnector/isolator) | three phase | Otherwise started by a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 226971 | 20170319SPN_01 | Burnt out line side of a HV blade isolator mounted on a steel crossarm on a concrete pole resulting in hot particles falling to the ground starting a very small grass fire at base of the pole. Mechanical failure of switch – the isolator had been sparking and appeared not to be aligned straight.
2193 | Ausnet 16/113 | Ausnet | 27/03/2017 | 42821.4729 | -38.5582 | 145.8813 |  | 2010501 | LGA23 | Low voltage AC (<1kV) | RURAL LONG | - connection box | single phase | Otherwise started by a distribution system | HBRA only | 1 | Very high | 1 | 1 | 227122 | 20170329SPN_02 | A molten LV fuse carrier from a pole mounted FOLCB fell to the ground starting a small grass fire. Cause unknown but likely high impedance connection of the inserted fuse carrier.
2194 | Ausnet 16/114 | Ausnet | 2017-02-04 | 42827.3264 | -38.3985 | 146.1587 |  | 2021888 | LGA11 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 227320 | 20170403SPN_01 | Candled/burnt EDO fuse tube. EDO fuse failed to operate correctly.
2195 | Ausnet 16/115 | Ausnet | 2017-11-04 | 42836.5694 | -37.9279 | 145.9502 |  | 2700395 | WGL24 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 227473 | 20170420SPN_01 | Candled/burnt EDO fuse tube. EDO fuse failed to operate correctly.
2196 | Ausnet 16/116 | Ausnet | 24/04/2017 | 42849.1042 | -37.851 | 145.2602 |  | 1219519 | BWR34 | Low voltage AC (<1kV) | URBAN | - lamps (minor road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 227611 | 20170426SPN_01 | Street light lantern caught fire. Internal fault in street light lantern.
2197 | Ausnet 16/117 | Ausnet | 2017-09-05 | 42864.9681 | -38.031 | 145.342 |  | 5765423 | BWN13 | Low voltage AC (<1kV) | URBAN | - lamps (major road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 227798 | 20170529SPN_01 | Street light lantern caught fire. Internal fault in street light lantern.
2198 | Ausnet 16/118 | Ausnet | 17/05/2017 | 42872.7951 | -37.8765 | 148.0051 |  | 1902475 | BDL41 | Low voltage AC (<1kV) | RURAL LONG | - lamps (major road) | single phase | Otherwise started by a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 228117 | 20170601SPN_01 | Street light lantern caught fire. Internal fault in street light lantern.
2199 | Ausnet 16/119 | Ausnet | 24/05/2017 | 42879.2451 | -38.1281 | 145.7544 |  | 2716082 | WGL12 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 228037 | 20170531SPN_02 | Candled/burnt EDO fuse tube. EDO fuse failed to operate correctly.
2200 | Ausnet 16/120 | Ausnet | 31/05/2017 | 42886.8819 | -37.8714 | 148.008 |  | 1902525 | BDL41 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 228272 | 20170614SPN_01 | Candled/burnt EDO fuse tube. EDO fuse failed to operate correctly.
2201 | Ausnet 16/121 | Ausnet | 2017-10-06 | 42896.9694 | -37.8962 | 147.8553 |  | 1911158 | BDL6 | Low voltage AC (<1kV) | RURAL SHORT | - connection box | three phase | Otherwise started by a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 228484 | 20170704SPN_01 | Overheated connection caused LV fuse box to combust
2202 | Ausnet 16/122 | Ausnet | 15/06/2017 | 42901.75 | -37.8989 | 145.3327 |  | 1314427 | UWY1 | Low voltage AC (<1kV) | RURAL SHORT | - overhead conductor (insulated) | three phase | Otherwise started by a distribution system | within electric line construction area | 19.8 | No forecast | 0.1 | 1.98 | 228541 | 20170817SPN-01 | LV leads burnt out
2203 | Ausnet 16/123 | Ausnet | 20/06/2017 | 42906.2928 | -37.2185 | 145.7338 |  | 4711213 | RUBA12 | 22kV AC | RURAL LONG | - fuse (boric acid) | three phase | Otherwise started by a distribution system | within area delineated on plan LEGL./16-354 | 4.6 | No forecast | 0.1 | 0.46 | 228617 | 20170707SPN_01 | Candled/burnt BA fuse tube
2204 | Ausnet 16/124 | Ausnet | 25/06/2017 | 42911.75 | -38.0318 | 146.9864 |  | 2508411 | MFA23 | 22kV AC | RURAL SHORT | - overhead conductor (bare; steel) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 228743 | 20170627SPN_01 | Conductor down. Observed a burnt area.
2205 | Ausnet 16/125 | Ausnet | 28/06/2017 | 42914.3882 | -38.3841 | 146.115 |  | 2002648 | LGA11 | 22kV AC | RURAL LONG | - fuse (EDO fuse) | single phase | Otherwise started by a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 228816 | 20170817SPN_02 | Candled/burnt switch